GENERATION

MODELING

- Duke generators are now modeled at the nominal dependable capacity based on data provided by Duke Generation.  (The associated ecd & gcp files are kept in the Operating ecdi subdirectory, indicating the files represent expected actual system operation.)  This is their expected output during summer peak conditions.  In the past the generators’ output was modeled according to their MNDC.  Modeling the units at their expected capacity will more closely match actual peak operation and ensure that the transmission system is planned to accommodate actual system conditions.  Duke Generation also provided updated data on reactive power capability.

- Future resource additions are consistent with the projections of load, capacity and reserves from Resource Planning.  Future generation locations were selected based on knowledge gained through generation planning and interconnection studies.

- Dynegy (825 MW), Broad River Energy Center (BREC) (previously, SkyGen and Polsky - 875 MW), CP&L-Rowan (945 MW), generating units have been added to the model and dispatch lists.  These generators are presently in commercial operation.  Buck (620 MW) and Cliffside (800 MW) have also been added to the model.  These sites were chosen based on the high probability of development of these sites by Duke or IPP’s,  All these generators are included in the ecdi files in the years they are assumed to be in operation.

- Dynegy went in service in 2000 summer and has five units.  In 2006, Duke Energy purchased these generators and they are a designated network resource.   There remains a concern about loading of the 100 kV lines leaving Sadler Tie.  Opening the ring bus at Ernest places three of the Dynegy units on a radial connection to Belews Creek, forcing flow away from Sadler.

Three units at BREC went in service in 2000 summer with two additional units going in service in 2001 summer.  All 5 units have annual firm transmission reservations for 850 MW and are dispatched to supply CP&L-E and are designated as must run because they are not under Duke's dispatch control.  The units are dispatched at 875 MW’s – 850 MW which meets the transmission reservation and the other 25 MW’s are assumed to meet losses.

CP&L-Rowan placed 3 CT’s in service in 2001 summer and an additional combined cycle plant (3 units) were placed in service in 2004 summer.  The first 3 units operate as independent CT’s with ratings of 154 MW summer and 185 MW winter.  The second 3 units are combined cycle with two 157 MW summer/183 MW winter CT’s and a 169 MW summer/172 MW winter steam turbine.

- Mill Creek is a CT site at Ripp Tie and is named as a Duke network resource for 2004 and beyond.  Units are rated 76 MW summer and 96 MW winter.

- Cliffside is a very likely site for a new Duke fossil plant.  It has been modeled as a 800 MW base load (priority group 4) generator.  Buck has been a potential Duke self build site, as well as for several IPP’s.  The assumption is that combined cycle generation will be placed near Buck.

- For modeling of cross compound units, the high pressure (HP) and low pressure (LP) machines must work together, i.e., either both are on-line or both are off-line.

- Cross compound units, modeled as HP and LP machines, have the naming convention of:
	HP machine ID = unit number
	LP machine ID = L
For example, at Belews Creek, unit 1 is represented at bus 2377, machine 1 (HP) and machine L (LP).

- Machine ID L is reserved for modeling low pressure units Only.

- Two GCAP files have been created.  Hydrooffgcap.xls will be used to create our worst case/base case models to be used for screening.  The gcap will eliminate (QMAX=0) var support from hydro holdback units.  These units are normally only dispatched for generator contingencies or to meet VACAR reserve sharing requirements.  On peak they may not be available, due to drought or maintenance, for var support to the system.  Motoring of the units is also less desirable than having capacitors available to switch on.  With their var support removed, screening results will require the addition of static var support (capacitors) and allow these units to operate closer to unity pf – creating more available dynamic var support for the area.  The Hydroongcap.xls will be used in creation of the LTSG models to create cases that are more representative of expected operating conditions and not worst case.  The Hydroongcap.xls will continue to have the var support stacked to show motoring availability if necessary and full var capability of the all hydro holdback units.

Jocassee and Bad Creek MVAR capability has been revised to reflect their ability to operate in automatic voltage control.  In the past, their MVAR output was a fixed value in the gcap file.  The revision allows their output to adjust to meet voltage schedule.

- Jocassee is scheduled for a turbine runner upgrade on 2 units in 2007 and 2 units in 2010.  The upgrade will increase the continuous capability of each unit to 201 MW.

- Var capability for Cowans Ford units has been modified to better reflect actual capability based on its actual operation.  The MVAR output has been lowered from 50 MVAR to 20 MVAR per unit.  Their AVR is set to regulate at 20 MVAR immediately following startup and is allowed to float with system voltage.

- Var capability for the Keowee units has been modified to better reflect actual capability based on its actual operation.  The MVAR output has been lowered from 42 MVAR to 20 MVAR per unit.  The units can achieve 35 MVAR according to their D curve.  However, their AVR is set to regulate at 20 MVAR immediately following startup and is allowed to float with system voltage.

- Valley ecd files were created to support light load cases.  These ecd files dispatch units as the SOC would under valley conditions.

- Based on review with the OPA and to make dispatch better match actual practice, the following changes have been made:  Only Unit 1 at Cowans Ford is modeled as the swing bus.  Unit 2 has been given the same priority as conventional hydro units.

- Hartwell (SEPA) is now modeled as 5 separate generators.  Units 1 thru 4 are rated 86 MW and Unit 5 is 96 MW.

- Cherokee Cogen is now modeled as 2 separate generators.

- RJR Tobacco is assumed to be retired and is not modeled.

- Yadkin plants, Badin, High Rock & Tuckertown, are operated by Alcoa Power Generation Inc.  Yadkin load has been reduced to 4.0 MW at Badin.  High Rock & Tuckertown are modeled as off-line.

- Hartwell 5 & Badin are the swing buses for their respective control areas.  Their capacity curve data has been revised so that they cannot have an unrealistic state with 0 MW output and be producing vars.  The .gcp files have been edited to prevent this situation.

Dispatch IPLAN Notes

- Suggested peak spinning reserve = 80 MW.  Actual Contingency Reserve (previously Spinning Reserve) Requirement (SRR) is approximately 515 MW (revised annually according to VACAR Reserve Sharing Agreement).

- Suggested valley spinning reserve = 2000 MW
Absolute valley period is assumed to occur on a Spring or Fall weekend night.  The load swing for this type day ( 4000-5000 MW.  With 2700 MW of hydro capability, enough fossil/nuclear need to be on-line for the daily peak period.