DUKE ENERGY CAROLINAS, LLC

TRANSMISSION SYSTEM 
PLANNING SUMMARY

Power Delivery

TABLE OF CONTENTS

I.	SCOPE	1

II.	TRANSMISSION PLANNING OBJECTIVES	1

III.	TRANSMISSION PLANNING ASSUMPTIONS	2

A.	Load Levels Modeled	2

B.	Generation Modeled	2

1.	Dispatch	2

2.	Voltage Schedules	3

3.	Reactive Capability	3

4.	Power Transactions	3

C.	Equipment Ratings	4

D.	Nominal Voltages	4

E.	Common Right-of-Way	4

IV.	STUDY PRACTICES	5

V.	PLANNING GUIDELINES	6

A.	Voltage	8

B.	Thermal	9

C.	Selected Contingencies	9

D.	Miscellaneous	12

1.	Delivery Point Power Factor Standard	12

2.	Spare Transformer Policy	12

3.	Transformer Tertiary Study	13

4.	Optimal Power Flow (OPF) Studies	13

5.	Stability	13

6.	Power Transfer Studies	14

7.	Impact Study	15

8.	Fault Duty	16

9.	Miscellaneous Losses Evaluations	17

10.	Facilities Adequate Evaluations	17

11.	Severe Contingency Studies	17

VI.	REFERENCE DOCUMENTS	18

# SCOPE

This document contains an overview of the fundamental guidelines followed by Duke Energy Carolinas, LLC’s (Duke Carolinas) Power Delivery employees to plan Duke’s 500 kV, 230 kV, 161 kV, 100 kV, 66 kV and 44 kV transmission systems.  FERC Order 890 requires that public utilities document and make available to stakeholders their basic methodology, criteria, and processes in order to ensure that transmission planning is performed on a consistent basis.  The Transmission System Planning Summary contains general information on Duke Carolinas transmission planning practices and provides links to other Duke Carolinas documents that contain additional detail.

The Duke Carolinas transmission system is planned to meet NERC Reliability Standards.  Any reliable transmission network must be capable of moving power throughout the system without exceeding voltage, thermal and stability limits, during both normal and contingency conditions.  These guidelines and referenced documents are designed to aid Power Delivery employees in planning and designing a safe and reliable transmission system.  Duke Carolinas retains the right to amend, modify, or terminate any or all of these guidelines and referenced documents at its option.

# TRANSMISSION PLANNING OBJECTIVES

The guidelines in this document are formulated to meet the following objectives:

- Provide an adequate transmission system to serve the network load in the Duke Energy Carolinas service territory.

- Balance the risks and expenditures required to ensure a reliable transmission system while maintaining the flexibility to accommodate future uncertainties.

- Maintain adequate transmission thermal capacity and reactive power reserves (in the generation and transmission systems) to accommodate scheduled and unscheduled transmission and generation contingencies.

- Achieve compliance with the NERC and SERC Reliability Standards that are in effect.

- Adhere to applicable regulatory requirements.

- Minimize losses where cost effective.

- Provide for the efficient and economic use of all generating resources in accordance with applicable tariffs and regulatory requirements.

- Provide for comparable service under the Duke Energy Joint Open Access Transmission Tariff.

- Satisfy contractual commitments and operating requirements of inter-system agreements.

# TRANSMISSION PLANNING ASSUMPTIONS

A summary spreadsheet of transmission planning assumptions can be found at:

Duke Planning Info Summary.xls

## Load Levels Modeled

- Summer Peak (for current year and next 9 years)

- Winter Peak (for current year and next 9 years)

- Spring Valley (for current year and next 2 years)

- Loads plus losses at the transmission level will be scaled to match the system forecast for each load level.  When conditions warrant, additional cases may be generated to examine the impact of other load levels.

## Generation Modeled

### Dispatch

Generation patterns may have a large impact on thermal loading levels and voltage profiles.  Therefore, varying generation patterns shall be examined as a part of any analysis.  Generators with confirmed, firm transmission reservations or designated as network resources are modeled as being available for dispatch.  Units serving native load are economically dispatched for normal and contingency conditions.  Normal outages for maintenance, forced outages, and combinations of normal and forced outages are modeled.  Generating units are modeled at their expected seasonal continuous capability.

More detailed information can be found in the following document:

Generation Modeling.doc

### Voltage Schedules

An optimal power flow program is used to determine the voltage schedules for major system generating units.  The voltage schedules are tailored to take into account season and load level to meet system reactive power requirements.

More detailed information can be found in the following document:

System Voltage Planning.ppt

### Reactive Capability

Reactive capability data is included in the base power flow models so the impact of reactive power available from generators can be reproduced in the system model.  The generator MW dispatch module within the power flow analysis program applies generator reactive power limits based on the power output levels of each unit.  Reactive power output is evaluated to ensure sufficient reactive capacity exists.

More detailed information can be found in the following documents:

Generation Modeling.doc

Generator Reactive Power Support.doc

### Power Transactions

Long-term firm power transactions between control areas are included in the appropriate power flow base cases and shall be consistent with contractual obligations.  For an emergency transfer analysis, generation is reduced in a manner that will cause stress on the system.

Duke participates in several reliability groups that perform transfer studies on a regular basis: VACAR (Virginia-Carolinas Subregion of SERC), SERC Intra-Regional Long-Term and Near-Term Power Flow Study Groups (VACAR-Southeastern-Central-Delta-Gateway regions), SERC East-RFC (ReliabilityFirst Corporation), North Carolina Transmission Planning Collaborative, CTCA (Carolinas Transmission Coordination Arrangement).

More detailed information can be found in the following documents:

Regional Transmission Assessment Study Processes within SERC.doc

NCTCP Participation Agreement.doc

ERAG MC Handbook.doc

Eastern Interconnection Coordination Agreement.doc

## Equipment Ratings

The methodology used to rate transmission facilities encompasses all components (e.g., transformers, line conductors, breakers, switches, line traps, etc.) from bus to bus.  Wind speed and angle, ambient temperature, acceptable operating temperatures, as well as other factors are used in determining facility ratings.  All facilities are composed of eight ratings reflecting the following capabilities for both summer and winter seasons:

- continuous

- long-term emergency (1 year)

- 12-hour emergency

- 1-hour emergency

More detailed information can be found in the following document:

DEC Electrical Facility Ratings Methodology

## Nominal Voltages

Nominal voltages on the Duke Carolinas system are 500 kV, 230 kV, 161 kV, 100 kV, 66 kV and 44 kV.  Additional nominal voltages of 138 kV and 115 kV are utilized for some of Duke Carolinas’ interconnections with other utilities.

## Common Right-of-Way

Part of the judgment used for any analysis is the definition of line outages on a common right-of-way.  There are situations where multiple lines may leave a station in a similar direction and along a common corridor for some short distance.  While there are no clear cut rules, the length of exposure of a common right-of-way and the criticality of the circuits involved, must be considered when defining which rights-of-way should be studied.

# STUDY PRACTICES

Duke Carolinas conducts a variety of transmission planning studies including, but not limited to:

- Screening of Voltage Guidelines

- Screening of Thermal Guidelines

Grid Voltage Study For Nuclear Loss-Of-Cooling Accident (LOCA) (System Voltage Planning.ppt)

- Spare Transformer Study

- Transformer Tertiary Study

Optimal Power Flow Studies For Generator Voltage Schedules And Capacitor Additions (System Voltage Planning.ppt)

- Angle and Voltage Stability Analyses

- Power Transfer Studies

- System Impact Studies  (Analysis of Transmission Service Requests.doc)

- Generation Interconnection and Affected System Studies (Generator Interconnection Study abstract Rev3.doc, Duke Power Generating Site Interconnection Guidelines.doc)

- Fault Duty Analyses

- Miscellaneous Losses Evaluation

- Facilities Adequate Evaluations

- Severe Contingency Studies

During the course of transmission planning activities, the identification of a System Operating Limit (SOL) or an Interconnected Reliability Operating Limit (IROL) in the planning or operating horizon is possible.  SOL’s and IROL’s are defined as:

SYSTEM OPERATING LIMIT (SOL) - The value (such as MW, MVar, Amperes, Frequency or Volts) that satisfies the most limiting of the prescribed operating criteria for a specified system configuration to ensure operation within acceptable reliability criteria.  System Operating Limits are based upon certain operating criteria.  These include, but are not limited to:

- Facility Ratings (Applicable pre- and post-contingency equipment or facility ratings)

- Transient Stability Ratings (Applicable pre- and post-contingency stability limits)

- Voltage Stability Ratings (Applicable pre- and post-contingency voltage stability)

- System Voltage Limits (Applicable pre- and post-contingency voltage limits)

INTERCONNECTION RELIABILITY OPERATING LIMIT (IROL) - A System Operating Limit that, if violated, could lead to instability, uncontrolled separation, or Cascading Outages that adversely impact the reliability of the Bulk Electric System.

If a transmission planning activity identifies a SOL or IROL may be exceeded in the operating horizon, System Operations Engineering (as DEC’s Transmission Service Provider, Transmission Operator and Reliability Coordinator) should be immediately notified in accordance with FAC-014-2.  The SOL or IROL information shall also be provided to adjacent Planning Authorities and adjacent Transmission Planners.  SOL or IROL limit violations identified in the planning horizon should be corrected and/or mitigated in advance of the operating horizon.

More detailed information can be found in the following document:

DEC FAC-010 System Operating Limits Methodology Compliance.doc

# PLANNING GUIDELINES

Power Delivery is charged with planning the transmission system (500 kV, 230 kV, 161 kV, 100 kV, 66 kV, 44kV) and the system interconnections, as well as consulting in planning the distribution system (34.5 kV and below).  Voltages and thermal loadings that violate the following guidelines will result in further analyses.  Studies of the bulk transmission system (500 kV and 230 kV) give consideration to the effect Duke Carolinas may have on the planning and operation of neighboring utilities as well as the effect they may have on the Duke Carolinas system.

As a part of the NERC Reliability Standards, utilities are charged with planning their system in a manner that avoids uncontrolled cascading beyond predetermined boundaries.  This is to limit adverse system operations from crossing a control area boundary.  To this extent, Duke participates in several regional reliability groups:  VACAR (Virginia-Carolinas Subregion of SERC), SERC Intra-Regional Long-Term and Near-Term Power Flow Study Groups (VACAR-Southeastern-Central-Delta-Gateway regions), SERC East-RFC, North Carolina Transmission Planning Collaborative, Carolinas Transmission Coordination Arrangement.  Each of these reliability groups evaluates the bulk transmission system to ensure:  1) the interconnected system is capable of handling large economy and emergency transactions, 2) planned future transmission improvements do not adversely affect neighboring systems, and 3) the interconnected system’s compliance with selected NERC Reliability Standards.  Additional information on SERC region efforts to coordinate planning activities related to reliability and economic access can be found in the following documents: (Whitepaper on Reliability and Economic Planning.doc, Southeast_Inter-Regional_Participation_Process11302007Final.doc)

Each of these study groups has developed its own set of procedures that must be followed. (MMWG Procedure Manual.doc, SERC LTSG procedural manual.doc)  These study groups do not have as one of their objectives the analysis and planning for any one individual system.  The main objective of these groups is to maintain adequate transmission reliability through coordinated planning of the interconnected bulk transmission systems.

In addition to these regional and inter-regional reliability studies, Duke Carolinas conducts its own assessments of the bulk transmission system.  While these assessments are typically focused on the Duke Carolinas system, they cannot be conducted without consideration of neighboring systems.

NERC Reliability Standards mandate that facility connection requirements for all facilities involved in the generation, transmission, and use of electricity be documented.  All electric industry participants are required to document the facility connection requirements for their system.

Duke Carolinas has a Facility Connection Requirements document that identifies the technical requirements for connecting load deliveries, generation facilities, and control area Interconnections to the Duke Carolinas transmission system.  Duke Energy Carolinas Facility Connection Requirements.doc).

The Facility Connection Requirements document is divided into two major sections:  1) Load Delivery Requirements and 2) Generation and Interconnection Requirements.  Some projects may have both load and generation on site.  Load Delivery Requirements apply to projects having generating capability of less than 25% of minimum load.  These technical requirements are designed to ensure the safe operation, integrity, and reliability of the transmission system.  Transmission planning studies are performed to ensure that these requirements will be met under the applicable operating conditions.  Some of these requirements are summarized below.

The voltage and thermal guidelines for the transmission system under normal and contingency conditions are described infra in Section V.A and Section V.B, respectively.  A description of the contingencies studied as part of any voltage or thermal evaluation is provided in Section V.C.

## Voltage

Bus voltages are screened using the Transmission System Voltage Guidelines set forth below.  The guidelines specify minimum and maximum voltage levels, the percent voltage regulation during both normal and contingency conditions, and the percent voltage drop due to contingencies.

Absolute Voltage Limits are defined as the upper and lower operating limits of each bus on the system.  The absolute voltage limits are expressed as a percent of the nominal voltage.  All voltages should be maintained within the appropriate absolute voltage bounds for all conditions.

Voltage Regulation is defined as the difference between expected maximum voltage and minimum voltage at any particular delivery point.  The voltage regulation limits are expressed as a percent of the nominal voltage and are defined for both normal and contingency conditions.  Voltage regulation for delivery point voltages should not exceed the guidelines.

Contingency Voltage Drop is defined as the maximum decrease in voltage due to any single contingency.

161 kV, 230 kV, & 500 kV Transmission System Voltage Guidelines

| Nominal Voltage (kV) | Absolute Voltage Limits Minimum Maximum | Maximum Allowable Contingency Voltage Drop |
| --- | --- | --- |
| 161 | 95% 105% | 5% |
| 230 | 95% 105% | 5% |
| 500 | 100% 110% | 5% |

44 kV, 66 kV, & 100 kV Transmission System Voltage Guidelines

| Nominal Voltage (kV) | Absolute Voltage Limits Minimum Maximum | Voltage Regulation Normal Contingency |
| --- | --- | --- |
| 44 | 94% 109% | 8.5% 10% |
| 66 | 94% 109% | 8.5% 10% |
| 100 | 95% 107% | 6% 7% |

Autotransformer voltage limits are based on the secondary tap setting.  The minimum voltage is 95% of the tap voltage and the maximum voltage is 105% of the tap voltage under full load and 110% of the tap voltage under no load.  Thus, the voltage limits for transformers vary with both loading and tap setting.  The secondary tap on most of Duke’s 220/100 kV autotransformers is 100 kV.

Nuclear voltage limits are based on the design of electrical auxiliary power systems within the plants and Nuclear Regulatory Commission (NRC) requirements.  There are two sets of these limits:  minimum and maximum generator bus voltage limits and minimum grid voltage limits.

## Thermal

The following guidelines shall be used to ensure acceptable thermal loadings:

- Under normal conditions, no facility should exceed its continuous thermal loading capability.

- With a transmission contingency having an expected duration of less than 12 hours (line outage or single phase transformer outage where spare is available), no facility should exceed its 12-hour emergency loading capability.

- With a capacitor, transformer (three phase or single phase with no spare) or generator contingency having an expected duration of more than 12 hours, no facility should exceed its long-term emergency loading capability.

## Selected Contingencies

The planning studies for the transmission system are performed for normal and contingency conditions in accordance with NERC Reliability Standards (TPL philosophy.doc).  The thermal and voltage guidelines should not be violated for either normal operations or under the loss of:

- A single transmission circuit

- A single transformer

- A single generating unit

- A single reactive power source or sink

- Combination of a single generating unit and a single transmission circuit, capacitor bank, or transformer

- Combination of two generating units

Sample files - longterm.doc, shortterm.doc, monall.doc

Several 230 kV tie stations on the Duke Carolinas system have incomplete double bus or breaker-and-a-half designs.  Thus, abnormal single contingency configurations can result.  To properly screen for violations of the guidelines, the following table indicates the contingencies that should be modeled.

Abnormal Single Contingency Configurations

| Tie Station | Outaged facilities for 230 kV line fault | Outaged facilities for 230/100 kV autotransformer fault | Short term Contingency Tests | Long Term Contingency Tests |
| --- | --- | --- | --- | --- |
| Bush River | The line and transformer | The transformer and a line | Line & Tx, Line only | Tx only |
| Hodges | The line | The transformer and a line | Line & Tx, Line only | Line & Tx, Tx only |
| Lakewood | The line and transformer | The transformer and a line | Line & Tx, | Line & Tx, Tx only |
| McDowell | The line | The transformer and a line* | Line & Tx, Line only | Line & Tx, Tx only |
| Morningstar | The line | The transformer and possibly a line * | Line & Tx, Line only | Line & Tx, Tx only |
| Peacock | The line | The transformer and a line | Line & Tx, Line only | Line & Tx, Tx only |
| Shady Grove | The line | The transformer and tap line | Tap Line & Tx, Line only | Tap Line & Tx, Tx only |
| Tuckasegee** | The line | The transformer and a line | Line & Tx, Line only | Line & Tx, Tx only |
| Woodlawn | The line and transformer | The transformer and possibly a line * | Line & Tx, Line only | Line & Tx, Tx only |

*   Depends on which 230/100 kV transformer experiences the fault.

** 230/161 kV transformer

When appropriate, additional analyses will be conducted to review the impact of a combination of single contingencies, considering the probability of occurrence, the appropriate customer outage costs, and the possible system improvements to determine what, if any, remedial actions need to be taken.

## Miscellaneous

### Delivery Point Power Factor Standard

Duke Carolinas has established a power factor standard for all delivery points.  This standard is:

- 96.5% lagging power factor or better (equivalent to 98% on the low-side of the transformer) during Duke Carolinas peak load conditions (leading power factors are acceptable) and

- 100% (Unity) power factor or below during valley load conditions (leading power factors are not acceptable).

The power factor standard is designed to allow full utilization of transmission system equipment, provide support of system voltage levels during peak loading conditions and contingencies, and to help prevent high system voltage levels during valley load conditions.

### Spare Transformer Policy

This policy is reviewed periodically to account for changes in failure rates, transformer lead times, and outage costs.  Currently, the following number of spares should be available:

Spare Transformer Requirements

| Type of Transformer | # of Spares |
| --- | --- |
| 230/100/xx kV Autotransformer | 4 |
| 30/40/50 MVA 3 phase 100/44 kV | 0 |
| 20/27/33 MVA 3 phase 100/44 kV | 1 |
| 12/16/20 MVA 3 phase 100/44 kV | 1 |

### Transformer Tertiary Study

This study determines the minimum number of tertiaries required in service to operate the system reliably.  Having only the required amount of tertiaries in service reduces failures from detrimental in-service events like faults.

### Optimal Power Flow (OPF) Studies

OPF studies are conducted to determine the seasonal generator voltage schedules and for reactive power planning.  OPF study results are utilized to reduce system losses by adjusting VAR resources and by planning additional resources.

### Stability

#### Angle

Duke Carolinas performs stability analyses on large generating units as major generation or transmission changes occur on the system and as required by the Nuclear Regulatory Commission for the nuclear plants.  In addition, stability analysis will be performed to comply with NERC Reliability Standards.  These studies assess the ability of the interconnected network to maintain angular stability of the generating units under various contingency situations.  Many different contingencies are considered and the selection is dependent on the type of study and location within the transmission system.  The stability of the Duke Carolinas system and neighboring systems must be maintained for the contingencies specified in the applicable sections of the NERC Reliability Standards.

#### Voltage

An important part of preventing cascading outages is ensuring that voltage collapse will not cascade for the applicable contingencies defined in the NERC Reliability Standards.

Voltage stability analyses are performed using both traditional ZIP models and complex load models for all load in and near Duke.  The Duke Carolinas system is studied on system peak applying various single and multiple contingencies to ensure that voltage collapse will not occur for single contingencies and that voltage collapse will not cascade for multiple element and delayed clearing contingencies.

The corrective measures such as faster relaying, transmission upgrades, or unit tripping are determined on an individual basis after considering economics, probability of occurrence, and severity of the disturbance.

### Power Transfer Studies

Power transfer studies may be conducted as a part of a facility addition or upgrade analysis, as a part of a system impact study, as well as with the regional study groups to ensure system reliability.

Long-Term Planning

An 1100 MW first contingency incremental transfer capability (FCITC) level should be maintained for imports into the Duke Carolinas system from VACAR to ensure system reliability.  Duke Carolinas has an agreement with four systems within VACAR (Duke Energy Progress, South Carolina Public Service Authority, South Carolina Electric & Gas, and Virginia Power) to share contingency reserves.  By maintaining the 1100 MW level of FCITC with VACAR, Duke Carolinas has the capability to import the shared reserve requirements from the member systems.

The following first contingency incremental transfer capability levels should be maintained for exports from the Duke Carolinas system to ensure system reliability:

Non-Simultaneous Export Capability

| Importing System | Minimum FCITC (MW) |
| --- | --- |
| CPLE | 600 |
| SCPSA | 600 |
| SCE&G | 600 |
| DVP | 600 |

Duke Carolinas maintains adequate export capability with the four VACAR systems that share operating reserves to deliver Duke Carolinas’ portion of the reserve.

Available Transmission Capability (ATC) is the measure of the transfer capability remaining in the physical transmission network for further transmission service over and above committed use.  At the present time, the guidance for calculating and coordinating ATC is set forth in Attachment C of its open access tariff.  Pursuant to Order 890, changes to this Attachment are expected.  Duke Carolinas is an active participant in industry organizations developing the methodologies and intends to apply applicable NERC, SERC and other industry guidance for calculating ATC.

### Impact Study

Impact studies are performed to identify any problems associated with a requested/proposed system change.  The following analyses are performed if necessary:

  - Power Flow Analysis
A power flow analysis will be performed to determine any violations of the planning guidelines due to the addition of the request.  Projects that will be accelerated by the request will be identified as well as projects that will be needed to correct violations prior to implementation of the request.

  - Transfer Analysis
A transfer analysis will be performed to determine the impact on the bulk power system and to assess the changes that will occur in other areas resulting from the request.

  - Stability Analysis
A stability analysis will be performed to determine any violations to planning guidelines.

  - Fault Analysis
A fault analysis will be performed to determine information necessary for sizing equipment.

  - Other Analysis
Other analyses as required for a particular request.

As required by FERC Order 890, Conditional Firm Service and Planning Redispatch Service will be evaluated as options to allow the customer to have annual firm transmission service with some restrictions.  More detailed information on Duke Carolinas’ process for performing this evaluation can be found at:

CFS & RPS flowchart.xls
CFS and PRS methodology.doc

### Fault Duty

Fault duty studies are performed to determine the available fault current for each transmission system (500, 230, 161, 100, 66, and 44 kV) breaker location.  A Breaker Rating Module (BRM) program that resides within the fault study is used to check if the fault current capacity of the existing breakers is being exceeded.  Fault duty studies are also used to assist in sizing the interrupting capacity of new breakers being installed on the system.  When major system changes or additions are to be implemented, a BRM study is performed for both the existing and future state system configurations to determine the impact on the Transmission System and if any breaker’s capacity will be exceeded.

Network

Faults are evaluated for each breaker location to find the highest available fault current for the following conditions:

- single phase to ground fault

- two phase to ground fault

- three phase to ground fault

- fault resistance assumed to be zero

- location of fault assumed to be at terminals of the breaker in question

- all breakers at a bus in service

- breakers taken out, one at a time

- line mutual impedance included

- all generation units included

- adjacent system fault contributions included

- 5% above nominal operating voltage

The maximum calculated fault current at each breaker location and the associated breaker fault duty capability are compared to determine where violations of the breaker rating exist.

Radial

Fault duty for radial locations not explicitly modeled is calculated using fault duty at the associated network bus and the impedance of the radial elements.

### Miscellaneous Losses Evaluations

Various equipment and system loss evaluations are performed to aid in the selection of equipment, to meet contractual obligations and to compare system configurations.

### Facilities Adequate Evaluations

Facility evaluations are performed when a customer requests a change in contract MW.  The existing equipment, metering and analysis are evaluated for the proposed increase in load and a determination is made concerning any necessary improvements.  More detailed information is available at:

Major Projects - PES FAR Processes for Wholesale.doc

### Severe Contingency Studies

NERC Reliability Standards instruct transmission providers to evaluate contingency events resulting in the loss of two elements and extreme (highly improbable) contingency events resulting in multiple elements removed or cascading out of service.  The SERC Procedure - Transmission System Performance outlines SERC’s expectations of members with regard to the NERC Standards.  The procedure can be found at:

Transmission System Performance SERC Procedure

All double contingency simulations are analyzed and verify that unacceptable cascading does not occur.  All severe contingency simulations are analyzed and unacceptable cascading is identified and mitigated where possible.

The following double contingencies are modeled to ensure compliance with the standards to avoid cascading outages:

- Breaker (failure or internal fault)

- Delayed clearing of a single-phase fault on the system due to failure of a breaker to open or relaying to operate.

- Common Tower Contingencies with a single phase fault.

- Loss of a single element followed by system adjustments and then followed by a three phase fault resulting in the loss of another element.

The following extreme contingencies are modeled to ensure compliance with the standards to identify cascading outages:

- Loss of all circuits on a common right-of-way

- Loss of a substation (one voltage level plus transformers)

- Loss of all generation at a station

- Delayed clearing of a three-phase fault on the system due to failure of a breaker to open or relaying to operate.

# REFERENCE DOCUMENTS

- Some documents undergo frequent revision or are draft versions.  Please contact Duke Energy Carolinas Transmission Planning for information regarding the most current version of a reference document.