2010 ICT Reliability Assessment Scope

# Objective

The objective of the Reliability Assessment is to assess the ability of the Entergy transmission system to perform according to the Planning Criteria in both near-term and long-term horizons.

# Models

- Base Case 2008-Series Update1.

- Summer and Winter Peak 2010 and 2014 for near-term.

- Summer Peak 2018 for longer-term.

# Model Preparation

The Base Case Model will be updated to reflect:

- The latest confirmed transmission service reservations.

- Updated topology: equipment which has been newly placed in-service.

- Committed and Proposed Construction Plan Projects in the season in which the facilities are expected to be complete and for all seasons thereafter.

# Software

- PSSE v31

- MUST 8

# Contingency Scan

## Category A

- The Base Case Model will be evaluated under normal, system-intact conditions.

- Monitored elements must remain within the thermal and voltage limits specified in Entergy’s Transmission Local Planning Criteria for Category A, currently flows less than 100% of RATEA; voltages between 0.95 and 1.05 per unit.

- Identify all elements that do not meet the Category A limits.

## Category B

- An N-1 contingency scan will be run on the Base Case Models.

- Monitored elements must remain within the thermal and voltage limits specified in Entergy’s Transmission Local Planning Criteria for Category B, currently flows less than 100% of RATEA; voltages between 0.92 and 1.05 per unit.

- For each monitored element that does not remain within these limits, the breaker-to-breaker circuit for the contingency will be identified and an analysis will be done with the entire circuit out of service, if the breaker-to-breaker outage differs from the simulated outage.

- The amount of load shed by breaker operation, Consequential Load, will be recorded and reported for constrained elements.

## Monitored Elements

- Entergy Internal:

- Transmission elements within Entergy’s footprint (including embedded Areas) with nominal voltage 69 kV and higher.

- Ties to outside Areas at 69 kV and higher.

- CLECO & LUS: Transmission elements with nominal voltage 69 kV and higher.

- All other first-tier Areas (AECI, SOCO, TVA, SMEPA, SWPA, AEPW, OKGE, EMDE): Transmission elements with nominal voltage 345 kV and higher.

## Contingencies

- Same as Monitored Elements