## System Intact
System Intact Conditions
Thermal Overlads [%Overload, MVA Flow]
| From Bus |  |  | To Bus |  |  | Circuit | Draft Projects Included? | 2010S |  | 2010W |  | 2014S |  | 2014W |  | 2018S
| No. | Name | kV | No. | Name | kV |  |  | %Overload | Flow | %Overload | Flow | %Overload | Flow | %Overload | Flow | %Overload | Flow
| 335094 | 2MOSSVL | 69 | 335102 | 2CANAL-LA | 69 | 1 | No | [6 empty] | 101.9 | 38 | 102 | 38
[8 empty] | Yes | [6 empty] | 101.9 | 38 | 101.9 | 38
| 335346 | 2SCOTT | 69 | 503304 | RAYNE 2 | 69 | 1 | No | [8 empty] | 105.3 | 21
Yes
| 335411 | 2HOLIDAY | 69 | 335412 | 2LAFAYET | 69 | 1 | No | 103.5 | 40 |  |  | 107.9 | 41 |  |  | 117.1 | 45
Yes
| 335781 | 2ZAC REA | 69 | 335782 | 2PTHUDSONA | 69 | 1 | No |  |  |  |  | 101.3 | 91 |  |  | 114 | 101
[8 empty] | Yes |  |  |  |  | 101.2 | 91 |  |  | 113.9 | 101
| 335844 | 8BOGCHTA | 500 | 335845 | 6BOGCHTA | 230 | 1 | No
[8 empty] | Yes |  |  |  |  | 126.3 | 1144.9 | 131.5 | 1188.9 | 130 | 1170.4
| 338131 | 5MELBRN | 161 | 338132 | 5SAGE * | 161 | 1 | No |  |  | 103.3 | 158 |  |  | 104.6 | 159
Yes
Voltages [pu]
|  |  |  | Bus |  |  | Draft Projects Included? | 2010S | 2010W | 2014S | 2014W | 2018S
|  |  |  | No. | Name | kV |  | Voltage | Voltage | Voltage | Voltage | Voltage
|  |  |  | 334000 | 2CALVERT | 69 | No |  |  | 0.9493 |  | 0.9429
[7 empty] | Yes |  |  | 0.9442 |  | 0.9338
|  |  |  | 334020 | 4BRYAN | 138 | No
[7 empty] | Yes | 1.0604
|  |  |  | 334021 | 4COLSTTA | 138 | No
[7 empty] | Yes | 1.0536
|  |  |  | 335276 | 2KLONDKE | 69 | No |  |  | 0.9491 |  | 0.9436
|  |  |  | 335276 | 2KLONDKE | 69 | Yes |  |  |  |  | 0.9477
|  |  |  | 335275 | 2LKARTHR | 69 | No |  |  | 0.946 |  | 0.9404
|  |  |  | 335275 | 2LKARTHR | 69 | Yes |  |  |  |  | 0.9446
|  |  |  | 334681 | 3NECHESO | 69 | No | 0.9445 | 0.9438 | 0.94 | 0.9375 | 0.9362
|  |  |  | 334681 | 3NECHESO | 69 | Yes | 0.9446 | 0.9427 | 0.9399 | 0.9371 | 0.9363
|  |  |  | 335386 | 4ABBVIL | 138 | No | 0.9429 |  | 0.9242 |  | 0.939
|  |  |  | 335386 | 4ABBVIL | 138 | Yes
|  |  |  | 335391 | 4CECELIA | 138 | No | 0.941 |  | 0.9297 | 0.9481 | 0.9389
|  |  |  | 335391 | 4CECELIA | 138 | Yes
|  |  |  | 335387 | 4DELCAMB | 138 | No |  |  | 0.9338 |  | 0.9421
|  |  |  | 335387 | 4DELCAMB | 138 | Yes
|  |  |  | 335385 | 4LEROY | 138 | No | 0.9265 |  | 0.906 | 0.9486 | 0.9255
|  |  |  | 335385 | 4LEROY | 138 | Yes
|  |  |  | 335380 | 4MEAUX | 138 | No | 0.9342 |  | 0.9152 |  | 0.9358
|  |  |  | 335380 | 4MEAUX | 138 | Yes
|  |  |  | 335379 | 4SCOTT1 | 138 | No | 0.9499 |  | 0.9369
|  |  |  | 335379 | 4SCOTT1 | 138 | Yes
|  |  |  | 337181 | 5HN LAK | 161 | No | 1.0605 | 1.0562 | 1.0596 | 1.0532 | 1.0555
|  |  |  | 337181 | 5HN LAK | 161 | Yes | 1.0605 | 1.0562
|  |  |  | 337084 | DELTA U2 | 69 | No |  |  |  | 1.0724
|  |  |  | 337084 | DELTA U2 | 69 | Yes |  |  |  | 1.0752
|  |  |  | 338205 | 3PARAG | 115 | No |  | 1.0533 |  | 1.0516
|  |  |  | 338205 | 3PARAG | 115 | Yes |  | 1.0535 |  | 1.0548
|  |  |  | 338581 | DELUCE1 | 69 | No | 1.0515 | 1.0581 |  | 1.0517
|  |  |  | 338581 | DELUCE1 | 69 | Yes | 1.0512 | 1.0578 |  | 1.0518
|  |  |  | 338552 | HARRISON-S1 | 69 | No |  | 1.0554
|  |  |  | 338552 | HARRISON-S1 | 69 | Yes |  | 1.0551
|  |  |  | 338585 | HEBERSP1 | 69 | No |  | 1.0545
|  |  |  | 338585 | HEBERSP1 | 69 | Yes |  | 1.0545

## Base Thermal
Contingency Scan - Thermal Overloads
Approved 2009-2011 Construction Plan Projects Included
Model | Limiting Element |  |  |  |  | Rating | Flow | % | Bus to Bus Con | Breaker to Breaker | Rating | Flow | % | C-Load
18S | 334043*4TUBULAR | 138 | 334044 4DOBBIN | 138 | 1 | 112 | 136.8 | 124.1 | BUS 334074 [4PANORAM 138.00] TO BUS 334075 [4LONGMIR 138.00] CKT 1 | Lewis Creek - Longmire | 112 | 136.8 | 124.1 | 44.7
18S | 334120 4NU LJON | 138 | 334211*4BDAYTON | 138 | 1 | 99 | 101.1 | 106.1 | BUS 334084 [4CLVELND 138.00] TO BUS 334208 [4JACINTO 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 334413 4PNEC BK | 138 | 334430*4SABINE | 138 | 1 | 288 | 297.2 | 103.2 | BUS 334413 [4PNEC BK 138.00] TO BUS 334414 [4LINDE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 303 | 105.2 | 27.3
18S | 334413 4PNEC BK | 138 | 334430*4SABINE | 138 | 1 | 288 | 312 | 108.4 | BUS 334414 [4LINDE 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 303 | 105.2 | 27.3
14S | 334413 4PNEC BK | 138 | 334430*4SABINE | 138 | 1 | 288 | 301.4 | 104.7 | BUS 334414 [4LINDE 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 293.2 | 101.8 | 25.4
18S | 334414 4LINDE | 138 | 334430*4SABINE | 138 | 1 | 288 | 300.4 | 104.3 | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 334414 4LINDE | 138 | 334430*4SABINE | 138 | 1 | 288 | 290.1 | 100.7 | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 334600 2KOLBS | 69 | 334620*2LAKEVEW | 69 | 1 | 51 | 51.7 | 102 | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 334600 2KOLBS | 69 | 334620*2LAKEVEW | 69 | 1 | 51 | 51 | 100.6 | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 334600 2KOLBS | 69 | 334620*2LAKEVEW | 69 | 1 | 51 | 51.3 | 101.4 | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335094 2MOSSVL | 69 | 335108*2L253ATP | 69 | 1 | 39 | 40.4 | 104.1 | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335094 2MOSSVL | 69 | 335107*2ALFOL | 69 | 1 | 39 | 41.2 | 106.1 | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335094 2MOSSVL | 69 | 335108*2L253ATP | 69 | 1 | 39 | 40 | 102.8 | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335094 2MOSSVL | 69 | 335107*2ALFOL | 69 | 1 | 39 | 40.9 | 104.9 | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335094 2MOSSVL | 69 | 335108*2L253ATP | 69 | 1 | 39 | 40.7 | 104.8 | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335094 2MOSSVL | 69 | 335107*2ALFOL | 69 | 1 | 39 | 41.5 | 106.8 | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335125*4MOSSVL | 138 | 335200 4NELSON | 138 | 1 | 282 | 285.2 | 102.6 | BUS 335060 [4CARLYSS 138.00] TO BUS 335061 [4CTCON W 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335125*4MOSSVL | 138 | 335200 4NELSON | 138 | 1 | 282 | 279.6 | 100.5 | BUS 335061 [4CTCON W 138.00] TO BUS 335062 [4ARZONA 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335190 6NLSON | 230 | 303101*6MOSBLF | 230 | 1 | 374 | 408 | 110 | BUS 335074 [6DYNEGY 230.00] TO BUS 335077 [6PGROVE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335190 6NLSON | 230 | 303101*6MOSBLF | 230 | 1 | 374 | 395.8 | 106.7 | BUS 335074 [6DYNEGY 230.00] TO BUS 335077 [6PGROVE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335217 2CHLOMAL | 69 | 335250*2IOWA 6 | 69 | 1 | 39 | 46 | 121.2 | BUS 335265 [2LAWTAG 69.000] TO BUS 335266 [2JENNGS 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335217 2CHLOMAL | 69 | 335250*2IOWA 6 | 69 | 1 | 39 | 42.3 | 110.6 | BUS 335265 [2LAWTAG 69.000] TO BUS 335266 [2JENNGS 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335217 2CHLOMAL | 69 | 335250*2IOWA 6 | 69 | 1 | 39 | 44.6 | 117.6 | BUS 335265 [2LAWTAG 69.000] TO BUS 335266 [2JENNGS 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335217*2CHLOMAL | 69 | 335253 2LACASNE | 69 | 1 | 33 | 43.8 | 132.4 | BUS 335258 [2COMPTON 69.000] TO BUS 335259 [2L13ATP 69.000] CKT 1 | Jennings - Elton | 33 | 36 | 107.8 | 7.6
10S | 335217*2CHLOMAL | 69 | 335253 2LACASNE | 69 | 1 | 33 | 43.8 | 132.4 | BUS 335259 [2L13ATP 69.000] TO BUS 335266 [2JENNGS 69.000] CKT 1 | Jennings - Elton | 33 | 36 | 107.8 | 7.6
18S | 335257 2ELTON | 69 | 335258*2COMPTON | 69 | 1 | 34 | 39.7 | 133.5 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 34 | 32.8 | 103.7 | 6.3
18S | 335257 2ELTON | 69 | 335258*2COMPTON | 69 | 1 | 34 | 32.5 | 102.5 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 34 | 32.8 | 103.7 | 6.3
18S | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 42.4 | 130.2 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 42.6 | 131 | 6.3
10S | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 43.5 | 134 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 33 | 36.6 | 110.4 | 6
10S | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 36.6 | 110.5 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 36.6 | 110.4 | 6
14S | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 48.1 | 149 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 33 | 39.6 | 121.4 | 6.3
14S | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 39.6 | 121.4 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 39.6 | 121.4 | 6.3
14W | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 36.1 | 108.3 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 33 | 34.7 | 104.1 | 2.7
14W | 335258 2COMPTON | 69 | 335259*2L13ATP | 69 | 1 | 33 | 34.7 | 104.1 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 34.7 | 104.1 | 2.7
18S | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 43 | 130.8 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 43 | 130.6 | 6.3
10S | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 43.9 | 133.4 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 33 | 37 | 111.7 | 6
10S | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 37 | 111.7 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 37 | 111.7 | 6
14S | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 39.7 | 121.1 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 39.7 | 121 | 6.3
14W | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 36.6 | 109.8 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 33 | 34.8 | 104.7 | 2.7
14W | 335259 2L13ATP | 69 | 335266*2JENNGS | 69 | 1 | 33 | 34.8 | 104.7 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 33 | 34.8 | 104.7 | 2.7
18S | 335342 2AVER TP | 69 | 335344*2MAURICE | 69 | 1 | 93 | 92.7 | 104.7 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335342 2AVER TP | 69 | 335344*2MAURICE | 69 | 1 | 93 | 93.6 | 102.2 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335344 2MAURICE | 69 | 335345*2RIDGMTR | 69 | 1 | 93 | 95.8 | 104.1 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335344*2MAURICE | 69 | 335345 2RIDGMTR | 69 | 1 | 93 | 97.5 | 110 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335345 2RIDGMTR | 69 | 335346*2SCOTT | 69 | 1 | 93 | 98.2 | 105.4 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335345*2RIDGMTR | 69 | 335346 2SCOTT | 69 | 1 | 93 | 102.3 | 113.2 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 2 | 100 | 115 | 115 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 1 | 100 | 115 | 115 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 1 | 100 | 112.4 | 112.4 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 2 | 100 | 112.4 | 112.4 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 2 | 100 | 109 | 109 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 1 | 100 | 109 | 109 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
14S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 1 | 100 | 102.8 | 102.8 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335346 2SCOTT | 69 | 335379*4SCOTT1 | 138 | 2 | 100 | 102.8 | 102.8 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335346*2SCOTT | 69 | 335379 4SCOTT1 | 138 | 2 | 100 | 101.8 | 101.8 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335346*2SCOTT | 69 | 335379 4SCOTT1 | 138 | 1 | 100 | 101.8 | 101.8 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
18S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 216.5 | 110.5 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 266.2 | 103.6 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335366 4RICHARD | 138 | 500400*HABETZ 4 | 138 | 1 | 296 | 276 | 100.6 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 212.4 | 107.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 260.2 | 100.3 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 201.9 | 101.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 208 | 105.6 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 263.2 | 102.8 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335366 4RICHARD | 138 | 500400*HABETZ 4 | 138 | 1 | 296 | 277 | 100.8 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 211.1 | 105.1 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 209.3 | 104.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 209.2 | 104 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 201 | 101.3 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 207.8 | 105.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 259.7 | 101 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 221 | 111.5 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 265.7 | 101.6 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 220.5 | 111.4 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335366 4RICHARD | 138 | 335379*4SCOTT1 | 138 | 1 | 289 | 264 | 101.4 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335366 4RICHARD | 138 | 335375*4COLACDY | 138 | 1 | 209 | 218.7 | 110.1 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335368*8WELLS | 500 | 500950 WELSRCT6 | 230 | 1 | 560 | 706.4 | 126.1 | BUS 335367 [8RICHARD 500.00] TO BUS 335368 [8WELLS 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335368*8WELLS | 500 | 500950 WELSRCT6 | 230 | 1 | 560 | 560 | 100 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335368*8WELLS | 500 | 500950 WELSRCT6 | 230 | 1 | 560 | 606.4 | 108.3 | BUS 335367 [8RICHARD 500.00] TO BUS 335368 [8WELLS 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 207.7 | 106 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 203.6 | 103.4 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 199.1 | 101.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 202.5 | 100.8 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 198.9 | 100.6 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 212.2 | 107 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 211.6 | 106.9 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335375*4COLACDY | 138 | 335376 4ACADGSU | 138 | 1 | 209 | 209.9 | 105.7 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335376 4ACADGSU | 138 | 335377*4SCANLN | 138 | 1 | 209 | 197.9 | 102.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335376 4ACADGSU | 138 | 335377*4SCANLN | 138 | 1 | 209 | 206.4 | 105.8 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335376 4ACADGSU | 138 | 335377*4SCANLN | 138 | 1 | 209 | 206 | 105.8 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335376 4ACADGSU | 138 | 335377*4SCANLN | 138 | 1 | 209 | 204.2 | 104.4 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 126.3 | 103.2 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 152.9 | 129.5 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 149.3 | 125.4 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 124.7 | 100.4 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 124.3 | 100.7 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 149.5 | 124.6 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 154.9 | 130.6 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 146.6 | 121.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 131.2 | 104.7 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 130.6 | 105.2 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 153.3 | 125.8 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 151.6 | 124.2 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 151.5 | 124 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 143.3 | 119.4 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 149.5 | 125.5 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 140 | 116.7 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 132 | 106.2 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 129.6 | 105.1 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 156.1 | 130.3 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 155.5 | 130.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335378*4SCOTT2 | 138 | 303152 4SEMERE | 138 | 1 | 130 | 154 | 128.2 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 235 | 104.8 | BUS 500060 [BVISTA 4 138.00] TO BUS 500100 [BERWKTP4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 226 | 100.4 | BUS 500060 [BVISTA 4 138.00] TO BUS 500290 [ELPTAP 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 235.4 | 105 | BUS 500100 [BERWKTP4 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.8 | 102.2 | BUS 500170 [CLARN 6 230.00] TO BUS 500180 [CLARN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.6 | 102.1 | BUS 500180 [CLARN 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 232.6 | 103.2 | BUS 500330 [FLANDR 4 138.00] TO BUS 502401 [FLANDER6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 228.9 | 101.6 | BUS 500380 [GUIDRY 4 138.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.6 | 102.1 | BUS 500590 [NATCH 4 138.00] TO BUS 500600 [NATCH 2 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.6 | 102.1 | BUS 500590 [NATCH 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229 | 101.6 | BUS 500920 [WSTFORK6 230.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 234.3 | 104.9 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 241 | 230.4 | 102.8 | 49
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 233.6 | 105.1 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 241 | 230.4 | 102.8 | 49
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 230.2 | 102.7 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 241 | 230.4 | 102.8 | 49
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 232.1 | 103.6 | BUS 335366 [4RICHARD 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Flanders - Richard | 241 | 236.2 | 105.3 | 47.5
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 245.2 | 109.9 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 241 | 241.9 | 108.2 | 16.1
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 242 | 108.2 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 241 | 241.9 | 108.2 | 16.1
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 227.6 | 100.9 | BUS 335410 [2BILEAUD 69.000] TO BUS 335411 [2HOLIDAY 69.000] CKT 1 | Lafayette - Billeaud | 241 | 227.4 | 100.6 | 12.4
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.9 | 102 | BUS 335411 [2HOLIDAY 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Lafayette - Billeaud | 241 | 227.4 | 100.6 | 12.4
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 332.1 | 163.4 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 306.3 | 145.7 | 27.4
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 232.2 | 103.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 232.2 | 103.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.7 | 101.9 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 234.9 | 105.5 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224.1 | 100.2 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 225.1 | 100.2 | BUS 335391 [4CECELIA 138.00] TO BUS 335424 [2CECELIA 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.8 | 102.4 | BUS 335404 [2LEBLANC 69.000] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 241.9 | 108.2 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 228.5 | 101.6 | BUS 336033 [3TEREBN 115.00] TO BUS 336041 [6TEREBN 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 226.1 | 100.4 | BUS 336042 [6RACLND 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 248.2 | 115.2 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 240.8 | 106.8 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 235.6 | 105.2 | BUS 336137 [6SLIDEL 230.00] TO BUS 500800 [SSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 228.8 | 101.8 | BUS 500330 [FLANDR 4 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 269.8 | 121.2 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224 | 101 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224.4 | 100.2 | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224.4 | 100.2 | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224 | 100.5 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224.3 | 101.2 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 221.7 | 105.4 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 243.7 | 109 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 247.9 | 111.2 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 221.8 | 104.4 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 242.3 | 107.6 | BUS 335342 [2AVER TP 69.000] TO BUS 335344 [2MAURICE 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 228.8 | 100.5 | 35.2
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 244.8 | 108.8 | BUS 335344 [2MAURICE 69.000] TO BUS 335345 [2RIDGMTR 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 228.8 | 100.5 | 35.2
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 246.4 | 109.6 | BUS 335345 [2RIDGMTR 69.000] TO BUS 335346 [2SCOTT 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 228.8 | 100.5 | 35.2
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 224.4 | 100.4 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 241 | 224.4 | 100.4 | 5.9
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 236 | 105 | BUS 335388 [4MORIL 138.00] TO BUS 335391 [4CECELIA 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 227.2 | 100.4 | BUS 335337 [2MEAUX 69.000] TO BUS 335342 [2AVER TP 69.000] CKT 1 | Scott Bulk - Meaux | * | * | * | 35.2
10S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 261.8 | 121.7 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 246.1 | 114.6 | 22.6
10S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 236.9 | 106.3 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 260.4 | 117.6 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 251.6 | 113.3 | 9.4
10W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 251.6 | 113.5 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 295.7 | 143.6 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 272.3 | 128.7 | 25.5
14S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 222.6 | 105.1 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 237.6 | 108.3 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 293.4 | 136.7 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 284.7 | 131.4 | 10.8
14W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 229.1 | 100.3 | BUS 335404 [2LEBLANC 69.000] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 233.8 | 104.9 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379 4SCOTT1 | 138 | 303132*4JUDICE | 138 | 1 | 241 | 246 | 108.2 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 229.9 | 119.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 219.5 | 109.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 224.6 | 115.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 203.2 | 100.6 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 220.7 | 113.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 210.9 | 104.3 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 228.3 | 119.3 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 235.6 | 118.2 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 216.4 | 111.1 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 271.1 | 118.1 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 224.3 | 112.3 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 225.3 | 108.3 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 221.6 | 110.8 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 216.6 | 103.9 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 221.4 | 110.6 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 215.9 | 103.6 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 215.9 | 111.2 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 224.7 | 116.9 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 226.2 | 113 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 211 | 108.6 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 239.6 | 103.8 | BUS 500060 [BVISTA 4 138.00] TO BUS 500100 [BERWKTP4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.1 | 104 | BUS 500100 [BERWKTP4 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 234 | 101.1 | BUS 500180 [CLARN 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 242.3 | 104.7 | BUS 500330 [FLANDR 4 138.00] TO BUS 502401 [FLANDER6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 231.9 | 100.1 | BUS 500380 [GUIDRY 4 138.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 233.9 | 101.1 | BUS 500590 [NATCH 4 138.00] TO BUS 500600 [NATCH 2 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 233.9 | 101.1 | BUS 500590 [NATCH 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 231.9 | 100.1 | BUS 500920 [WSTFORK6 230.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.1 | 104.3 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 241 | 235.8 | 102.2 | 50.4
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 235.4 | 101.9 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 241 | 235.8 | 102.2 | 50.4
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 236.7 | 102.6 | BUS 335366 [4RICHARD 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Flanders - Richard | 241 | 239.7 | 103.9 | 32.4
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.9 | 104.4 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 241 | 238 | 103 | 15.8
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 238 | 103 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 241 | 238 | 103 | 15.8
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 233.5 | 100.7 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 233.5 | 100.7 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 232.8 | 100.3 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.8 | 104.7 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 238 | 103 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 232.9 | 100.6 | BUS 336033 [3TEREBN 115.00] TO BUS 336041 [6TEREBN 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 246.1 | 106.1 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.2 | 104.1 | BUS 336137 [6SLIDEL 230.00] TO BUS 500800 [SSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 234.3 | 101.3 | BUS 500170 [CLARN 6 230.00] TO BUS 500180 [CLARN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 234.5 | 101.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 289.2 | 126.3 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 229.6 | 117.4 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 226.8 | 104 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 225.1 | 110.5 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 246.4 | 106.7 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 228.1 | 117.2 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 226.5 | 104.3 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 220.5 | 108.8 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303130 4NCROWL | 138 | 1 | 216 | 226.2 | 115.4 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 226.9 | 103.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 502404 BONIN 4 | 138 | 1 | 225 | 214.5 | 105.1 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 247.7 | 106.8 | BUS 335342 [2AVER TP 69.000] TO BUS 335344 [2MAURICE 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 241.1 | 103.6 | 15.8
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 248.7 | 107.2 | BUS 335344 [2MAURICE 69.000] TO BUS 335345 [2RIDGMTR 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 241.1 | 103.6 | 15.8
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 249.4 | 107.5 | BUS 335345 [2RIDGMTR 69.000] TO BUS 335346 [2SCOTT 69.000] CKT 1 | Scott Bulk - Meaux | 241 | 241.1 | 103.6 | 15.8
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 246.4 | 106.8 | BUS 335388 [4MORIL 138.00] TO BUS 335391 [4CECELIA 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335379*4SCOTT1 | 138 | 303132 4JUDICE | 138 | 1 | 241 | 240.5 | 103.7 | BUS 335337 [2MEAUX 69.000] TO BUS 335342 [2AVER TP 69.000] CKT 1 | Scott Bulk - Meaux | * | * | * | 15.8
18S | 335380 4MEAUX | 138 | 303132*4JUDICE | 138 | 1 | 185 | 185.2 | 108.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335380 4MEAUX | 138 | 303132*4JUDICE | 138 | 1 | 185 | 171.7 | 100.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335380 4MEAUX | 138 | 303132*4JUDICE | 138 | 1 | 185 | 190.8 | 109.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335380 4MEAUX | 138 | 303132*4JUDICE | 138 | 1 | 185 | 193.6 | 111.9 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335380*4MEAUX | 138 | 303132 4JUDICE | 138 | 1 | 185 | 228.9 | 155.5 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 185 | 208 | 134.3 | 27.4
10S | 335380*4MEAUX | 138 | 303132 4JUDICE | 138 | 1 | 185 | 187.5 | 116.9 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 185 | 171.5 | 107.5 | 22.6
14S | 335380*4MEAUX | 138 | 303132 4JUDICE | 138 | 1 | 185 | 206.8 | 136.9 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 185 | 187.2 | 118.9 | 25.5
14W | 335380*4MEAUX | 138 | 303132 4JUDICE | 138 | 1 | 185 | 188 | 117.8 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 185 | 180.2 | 111.6 | 10.8
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 500060 [BVISTA 4 138.00] TO BUS 500100 [BERWKTP4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100 | BUS 500060 [BVISTA 4 138.00] TO BUS 500290 [ELPTAP 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 500100 [BERWKTP4 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500170 [CLARN 6 230.00] TO BUS 500180 [CLARN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500180 [CLARN 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500230 [COUGH 4 138.00] TO BUS 500540 [MANUEL 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 500300 [EUNICE 4 138.00] TO BUS 500540 [MANUEL 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 500380 [GUIDRY 4 138.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500590 [NATCH 4 138.00] TO BUS 500600 [NATCH 2 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500590 [NATCH 4 138.00] TO BUS 500730 [PRICE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100 | BUS 500920 [WSTFORK6 230.00] TO BUS 500930 [WSTFORK4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 502411 [SEWER 2 69.000] TO BUS 502440 [SW 1477 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 502413 [ELKS 2 69.000] TO BUS 502422 [HARGIS 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 502413 [ELKS 2 69.000] TO BUS 502440 [SW 1477 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 40 | 37.5 | 100.7 | 49
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.7 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 40 | 37.5 | 100.7 | 49
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 40 | 37.5 | 100.7 | 49
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 335366 [4RICHARD 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Flanders - Richard | 40 | 37.5 | 100.3 | 47.5
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.9 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 40 | 37.5 | 100.7 | 16.1
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.7 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 40 | 37.5 | 100.7 | 16.1
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.8 | BUS 335388 [4MORIL 138.00] TO BUS 335389 [4DUBOIN 138.00] CKT 1 | Moril - Bayou Warehouse | 40 | 37.5 | 100.7 | 32.2
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.5 | BUS 335389 [4DUBOIN 138.00] TO BUS 335390 [4BUWHSE 138.00] CKT 1 | Moril - Bayou Warehouse | 40 | 37.5 | 100.7 | 32.2
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 122.7 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 40 | 37.5 | 115.1 | 27.4
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 334325 [8HARTBRG 500.00] TO BUS 335192 [8NELSON 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 335192 [8NELSON 500.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335379 [4SCOTT1 138.00] CKT 2 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335366 [4RICHARD 138.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 335366 [4RICHARD 138.00] TO BUS 335367 [8RICHARD 500.00] CKT 2 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.4 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 335366 [4RICHARD 138.00] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 335367 [8RICHARD 500.00] TO BUS 335368 [8WELLS 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.7 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 335391 [4CECELIA 138.00] TO BUS 335424 [2CECELIA 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 335404 [2LEBLANC 69.000] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100 | BUS 335836 [8MCKNT 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.7 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 336033 [3TEREBN 115.00] TO BUS 336041 [6TEREBN 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100 | BUS 336042 [6RACLND 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 334325 [8HARTBRG 500.00] TO BUS 303021 [8COTNWD2 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 110 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 335379 [4SCOTT1 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 107.6 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.4 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 335455 [4CHAMPNE 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335500 [8WEBRE 500.00] TO BUS 303005 [8CAJUN2 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.6 | BUS 336137 [6SLIDEL 230.00] TO BUS 500800 [SSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.5 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.3 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.9 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 500330 [FLANDR 4 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.9 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.2 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 102.5 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.9 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 102.7 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.1 | BUS 500880 [VILPLT 6 230.00] TO BUS 500920 [WSTFORK6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.7 | BUS 500920 [WSTFORK6 230.00] TO BUS 500940 [WELLS 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 500940 [WELLS 6 230.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 106.1 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.5 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.1 | BUS 502407 [PINHOOK2 69.000] TO BUS 502413 [ELKS 2 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 105 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335437 [2SUNSET 69.000] TO BUS 335438 [2OPEL 6 69.000] CKT 1 | Sunset - Champagne | 40 | 37.5 | 100.1 | 10.8
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335438 [2OPEL 6 69.000] TO BUS 335439 [2L658TP 69.000] CKT 1 | Sunset - Champagne | 40 | 37.5 | 100.1 | 10.8
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335439 [2L658TP 69.000] TO BUS 335441 [2L637TP 69.000] CKT 1 | Sunset - Champagne | 40 | 37.5 | 100.1 | 10.8
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335441 [2L637TP 69.000] TO BUS 335442 [2CHAMPAN 69.000] CKT 1 | Sunset - Champagne | 40 | 37.5 | 100.1 | 10.8
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 101.5 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 40 | 37.5 | 101.5 | 5.9
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335456 [4L-642TP 138.00] TO BUS 335505 [4LIVON 138.00] CKT 1 | Wilbert - Krotz Springs | 40 | 37.5 | 100.2 | 14.9
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.3 | BUS 335505 [4LIVON 138.00] TO BUS 335507 [4WILBT 138.00] CKT 1 | Wilbert - Krotz Springs | 40 | 37.5 | 100.2 | 14.9
18S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 37.5 | 100.2 | BUS 335456 [4L-642TP 138.00] TO BUS 303153 [4KSPRGS 138.00] CKT 1 | Wilbert - Krotz Springs | 40 | 37.5 | 100.2 | 14.9
14S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 34.9 | 110.3 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 40 | 34.9 | 104.9 | 25.5
14S | 335386 4ABBVIL | 138 | 500010*ABBEVL 4 | 138 | 1 | 40 | 34.9 | 102 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335387 4DELCAMB | 138 | 303150*4LEBLAN | 138 | 1 | 251 | 262.4 | 120.8 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335387 4DELCAMB | 138 | 303150*4LEBLAN | 138 | 1 | 251 | 237.4 | 105.5 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335387 4DELCAMB | 138 | 303150*4LEBLAN | 138 | 1 | 251 | 232.1 | 102.4 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335387*4DELCAMB | 138 | 335388 4MORIL | 138 | 1 | 251 | 293.3 | 133.8 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335387*4DELCAMB | 138 | 335388 4MORIL | 138 | 1 | 251 | 232.8 | 101.3 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335387*4DELCAMB | 138 | 335388 4MORIL | 138 | 1 | 251 | 265.6 | 117.2 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335387*4DELCAMB | 138 | 335388 4MORIL | 138 | 1 | 251 | 245.1 | 107.3 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 149 | 106.8 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 159.1 | 113.7 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 155.8 | 110.3 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 196 | 138.8 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 150 | 108.1 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335388 4MORIL | 138 | 335391*4CECELIA | 138 | 1 | 151 | 191.4 | 136.6 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335389*4DUBOIN | 138 | 335390 4BUWHSE | 138 | 1 | 112 | 126.6 | 125.6 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335389*4DUBOIN | 138 | 335390 4BUWHSE | 138 | 1 | 112 | 107 | 104.3 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335389*4DUBOIN | 138 | 335390 4BUWHSE | 138 | 1 | 112 | 130 | 130.2 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335390*4BUWHSE | 138 | 500440 IVANHOE4 | 138 | 1 | 145 | 140.5 | 101.1 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335390*4BUWHSE | 138 | 500440 IVANHOE4 | 138 | 1 | 145 | 144.4 | 104.5 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335391 4CECELIA | 138 | 303152*4SEMERE | 138 | 1 | 130 | 123 | 103.5 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 184.7 | 133.2 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335391 4CECELIA | 138 | 502404*BONIN 5 | 138 | 1 | 145 | 168 | 127.6 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 145 | 146.3 | 109.1 | 49
18S | 335391 4CECELIA | 138 | 502404*BONIN 6 | 138 | 1 | 145 | 146.2 | 108.8 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 145 | 146.3 | 109.1 | 49
18S | 335391 4CECELIA | 138 | 502404*BONIN 7 | 138 | 1 | 145 | 148.2 | 113 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335391 4CECELIA | 138 | 502404*BONIN 8 | 138 | 1 | 145 | 149.2 | 111.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 159 | 115.9 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 173.7 | 124.4 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 145 | 148.6 | 106.4 | 43.9
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 171.3 | 123.2 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 145 | 148.6 | 106.4 | 43.9
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 148.4 | 106.1 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 145 | 148.6 | 106.4 | 43.9
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 178.3 | 128 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 142.7 | 102.3 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 161.2 | 116.1 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 158.3 | 116.9 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 185 | 132.9 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 145 | 156.4 | 112.1 | 50.4
14W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 182.9 | 132.2 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 145 | 156.4 | 112.1 | 50.4
14W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 156.1 | 111.9 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 145 | 156.4 | 112.1 | 50.4
14W | 335391 4CECELIA | 138 | 303152*4SEMERE | 138 | 1 | 130 | 131.3 | 109.1 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 189.8 | 136.7 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335391 4CECELIA | 138 | 502404*BONIN 4 | 138 | 1 | 145 | 170.9 | 123.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335391 4CECELIA | 138 | 502404*BONIN 5 | 138 | 1 | 145 | 150.4 | 112.9 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 52.6 | 140.4 | BUS 335410 [2BILEAUD 69.000] TO BUS 335411 [2HOLIDAY 69.000] CKT 1 | Lafayette - Billeaud | 39 | 52.6 | 140.6 | 12.4
18S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 66 | 179.6 | BUS 335411 [2HOLIDAY 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Lafayette - Billeaud | 39 | 52.6 | 140.6 | 12.4
18S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 43.3 | 114.8 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 47.5 | 126.3 | BUS 335410 [2BILEAUD 69.000] TO BUS 335411 [2HOLIDAY 69.000] CKT 1 | Lafayette - Billeaud | 39 | 47.5 | 126.2 | 10.2
10S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 58.9 | 158.5 | BUS 335411 [2HOLIDAY 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Lafayette - Billeaud | 39 | 47.5 | 126.2 | 10.2
10S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 39 | 103.1 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 50.7 | 136 | BUS 335410 [2BILEAUD 69.000] TO BUS 335411 [2HOLIDAY 69.000] CKT 1 | Lafayette - Billeaud | 39 | 50.7 | 135.8 | 11.5
14S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 63.2 | 173.7 | BUS 335411 [2HOLIDAY 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Lafayette - Billeaud | 39 | 50.7 | 135.8 | 11.5
14S | 335408 2NEWIBER | 69 | 335409*2L-294TP | 69 | 1 | 39 | 42.2 | 112 | BUS 335346 [2SCOTT 69.000] TO BUS 335412 [2LAFAYET 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 46.1 | 122.9 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 42.1 | 110.5 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 47.7 | 129.4 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 45.3 | 124.7 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 38.4 | 104.5 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 40.1 | 105.2 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 40.6 | 106.7 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 39.5 | 103.4 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 39.5 | 101.7 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 39.7 | 102.5 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 41 | 108.2 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 38.4 | 100.9 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 42.1 | 108.7 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 41.2 | 106.3 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 41.1 | 110.2 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 39.6 | 107.7 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 44.7 | 120.9 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335410 2BILEAUD | 69 | 335411 2HOLIDAY | 69 | 1 | 39 | 42.9 | 118.2 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA | NA | NA
10W | 335411 2HOLIDAY | 69 | 335412*2LAFAYET | 69 | 1 | 39 | 43.8 | 111.9 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335411 2HOLIDAY | 69 | 335412*2LAFAYET | 69 | 1 | 39 | 44 | 112.6 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335411 2HOLIDAY | 69 | 335412*2LAFAYET | 69 | 1 | 39 | 41.7 | 107.3 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 335411 2HOLIDAY | 69 | 335412*2LAFAYET | 69 | 1 | 39 | 47.1 | 120.4 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335411 2HOLIDAY | 69 | 335412*2LAFAYET | 69 | 1 | 39 | 46.1 | 118 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 59.6 | 117.5 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 58.6 | 115.1 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 54.6 | 110.4 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 53.7 | 107.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 54.3 | 106.9 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 53.1 | 104.5 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335438 2OPEL 6 | 69 | 335439*2L658TP | 69 | 1 | 51 | 50.9 | 102.2 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 61.1 | 120.4 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 60 | 117.9 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 56 | 113.4 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 55.2 | 110.7 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 55.8 | 109.7 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 54.6 | 107.4 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 51.1 | 101.7 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 52.4 | 105.1 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335439*2L658TP | 69 | 335441 2L637TP | 69 | 1 | 51 | 50.6 | 100.6 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335441 2L637TP | 69 | 335442*2CHAMPAN | 69 | 1 | 56 | 62.8 | 109.6 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335441 2L637TP | 69 | 335442*2CHAMPAN | 69 | 1 | 56 | 61.6 | 107.4 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335441 2L637TP | 69 | 335442*2CHAMPAN | 69 | 1 | 56 | 57.6 | 103.2 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335441 2L637TP | 69 | 335442*2CHAMPAN | 69 | 1 | 56 | 56.6 | 100.8 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335455 4CHAMPNE | 138 | 303134*4EOPLOUS | 138 | 1 | 225 | 208.3 | 102.1 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335536 6ADDIS | 230 | 303000*6CAJUN1 | 230 | 1 | 566 | 579.9 | 101.4 | BUS 335641 [TP.ESSO 230.00] TO BUS 335770 [6JAGUAR 230.00] CKT 1 | Esso - Jaguar | 566 | 579.5 | 101.4 | 0
14W | 335536 6ADDIS | 230 | 303000*6CAJUN1 | 230 | 1 | 566 | 576.6 | 100.9 | BUS 335770 [6JAGUAR 230.00] TO BUS 335772 [6ENJAY 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335536 6ADDIS | 230 | 303000*6CAJUN1 | 230 | 1 | 566 | 585 | 102.3 | BUS 335772 [6ENJAY 230.00] TO BUS 335825 [6FANCY 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335536 6ADDIS | 230 | 303000*6CAJUN1 | 230 | 1 | 566 | 591 | 103.4 | BUS 335836 [8MCKNT 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335536 6ADDIS | 230 | 303000*6CAJUN1 | 230 | 1 | 566 | 589.6 | 103.1 | BUS 335500 [8WEBRE 500.00] TO BUS 303005 [8CAJUN2 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335595*4ALCHEM | 138 | 335601 4WGLEN-2 | 138 | 1 | 282 | 276.7 | 101.5 | BUS 335599 [4GEIGY 138.00] TO BUS 335600 [4AIRPROD 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335595*4ALCHEM | 138 | 335601 4WGLEN-2 | 138 | 1 | 282 | 278.3 | 102.1 | BUS 335600 [4AIRPROD 138.00] TO BUS 335601 [4WGLEN-2 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335625*4GONZL | 138 | 336050 4SORXFM | 138 | 1 | 130 | 181.6 | 140.3 | BUS 335610 [4WGLEN 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | * | 120.3
18S | 335625*4GONZL | 138 | 336050 4SORXFM | 138 | 1 | 130 | 181.6 | 140.4 | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | * | 120.3
18S | 335787 2MCMANUS | 69 | 335788*2BRADYH | 69 | 1 | 20 | 18.5 | 105.7 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 20 | 18.5 | 101.6 | 3
18S | 335787 2MCMANUS | 69 | 335788*2BRADYH | 69 | 1 | 20 | 18.5 | 103.8 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 20 | 18.5 | 101.6 | 3
18S | 335787 2MCMANUS | 69 | 335788*2BRADYH | 69 | 1 | 20 | 18.5 | 101.7 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 20 | 18.5 | 101.6 | 3
18S | 335791 2TEJAC | 69 | 335792*2MRYDALE | 69 | 1 | 33.5 | 36.6 | 116.1 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 33.5 | 33.6 | 103.9 | 3
18S | 335791 2TEJAC | 69 | 335792*2MRYDALE | 69 | 1 | 33.5 | 35.6 | 111.5 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 33.5 | 33.6 | 103.9 | 3
18S | 335791 2TEJAC | 69 | 335792*2MRYDALE | 69 | 1 | 33.5 | 33.6 | 104 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 33.5 | 33.6 | 103.9 | 3
18S | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 36.7 | 111.4 | BUS 335793 [2FRANCIS 69.000] TO BUS 335795 [2GRANT 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 36.7 | 111.4 | 2
18S | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 38.6 | 118 | BUS 335795 [2GRANT 69.000] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 36.7 | 111.4 | 2
14S | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 35 | 105.1 | BUS 335793 [2FRANCIS 69.000] TO BUS 335795 [2GRANT 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 35 | 105.1 | 2.1
14S | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 36.9 | 111.7 | BUS 335795 [2GRANT 69.000] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 35 | 105.1 | 2.1
14W | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 36 | 105.1 | BUS 335793 [2FRANCIS 69.000] TO BUS 335795 [2GRANT 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 36 | 105.1 | 0.9
14W | 335791*2TEJAC | 69 | 335792 2MRYDALE | 69 | 1 | 33.5 | 36.8 | 107.7 | BUS 335795 [2GRANT 69.000] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 33.5 | 36 | 105.1 | 0.9
14S | 336031 3GIBSON | 115 | 336032*3HUMPHY | 115 | 1 | 227 | 233.5 | 106.6 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336032 3HUMPHY | 115 | 303202*3GRENWD | 115 | 1 | 228 | 238.8 | 108.4 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336033*3TEREBN | 115 | 303202 3GRENWD | 115 | 1 | 227 | 239.3 | 106 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336033*3TEREBN | 115 | 303202 3GRENWD | 115 | 1 | 227 | 235.4 | 104.1 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336033*3TEREBN | 115 | 303202 3GRENWD | 115 | 1 | 227 | 279.6 | 124.5 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336037*3VLNTIN | 115 | 336080 3CLOVEL | 115 | 1 | 114 | 140.2 | 123.5 | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336037*3VLNTIN | 115 | 336080 3CLOVEL | 115 | 1 | 114 | 142.3 | 125.2 | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336050 4SORXFM | 138 | 336051*3SORNTO | 115 | 1 | 140 | 185.5 | 132.5 | BUS 335610 [4WGLEN 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | * | 120.3
18S | 336050 4SORXFM | 138 | 336051*3SORNTO | 115 | 1 | 140 | 185.6 | 132.5 | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | * | 120.3
18S | 336068*6BLPNT | 230 | 336190 6GYPSY | 230 | 1 | 436 | 482.6 | 113.1 | BUS 336069 [6TEZCUCO 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336068*6BLPNT | 230 | 336190 6GYPSY | 230 | 1 | 436 | 480.3 | 112.5 | BUS 336069 [6TEZCUCO 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336080*3CLOVEL | 115 | 336081 3GMEADW | 115 | 1 | 114 | 113.1 | 102.2 | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336080*3CLOVEL | 115 | 336081 3GMEADW | 115 | 1 | 114 | 114.3 | 103.6 | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA | NA
10S | 336092*3CARLSL | 115 | 336293 3PTNICK | 115 | 1 | 114 | 114.4 | 124.7 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336131 6ADMSCRK | 230 | 336136*6BOGALUS | 230 | 2 | 637 | 736.4 | 114.7 | BUS 336131 [6ADMSCRK 230.00] TO BUS 336136 [6BOGALUS 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 336131 6ADMSCRK | 230 | 336136*6BOGALUS | 230 | 2 | 637 | 672 | 104.9 | BUS 336131 [6ADMSCRK 230.00] TO BUS 336136 [6BOGALUS 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336220 3GYPSY | 115 | 336230*3CLAYTN | 115 | 1 | 319 | 317.1 | 100.9 | BUS 336194 [6SNFARM 230.00] TO BUS 336233 [3SNFARM 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336232*3KENNER | 115 | 336233 3SNFARM | 115 | 1 | 270 | 310.4 | 118.8 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
10S | 336232*3KENNER | 115 | 336233 3SNFARM | 115 | 1 | 270 | 265.7 | 100.4 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336232*3KENNER | 115 | 336233 3SNFARM | 115 | 1 | 270 | 264.7 | 100 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336232*3KENNER | 115 | 336233 3SNFARM | 115 | 1 | 270 | 287.6 | 109.4 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 336232*3KENNER | 115 | 336233 3SNFARM | 115 | 1 | 270 | 285.8 | 108.7 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336553*3MALIL* | 115 | 336554 3BROKHV | 115 | 1 | 199 | 205 | 103.3 | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 199 | 203.9 | 103.3 | 0
10W | 336553*3MALIL* | 115 | 336554 3BROKHV | 115 | 1 | 199 | 203.9 | 103.3 | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 199 | 203.9 | 103.3 | 0
18S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 171.5 | 117.5 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 171.4 | 117.5 | 10
18S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 189 | 134.5 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 171.4 | 117.5 | 10
10S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 155.2 | 101.8 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 155.2 | 101.8 | 8.8
10S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 167.3 | 112.1 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 155.2 | 101.8 | 8.8
14S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 165 | 111.3 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 165 | 111.3 | 9.5
14S | 336554 3BROKHV | 115 | 336770*3WESSON | 115 | 1 | 161 | 180 | 125.2 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 165 | 111.3 | 9.5
10W | 336765 3FLRNCE | 115 | 336890*3JAX-S | 115 | 1 | 161 | 171.7 | 103.3 | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 161 | 171.6 | 103.4 | 0
10W | 336765 3FLRNCE | 115 | 336890*3JAX-S | 115 | 1 | 161 | 171.6 | 103.4 | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 161 | 171.6 | 103.4 | 0
18S | 336770 3WESSON | 115 | 336771*3JAM RD* | 115 | 1 | 161 | 159.7 | 112.1 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 159.7 | 112.1 | 10
18S | 336770 3WESSON | 115 | 336771*3JAM RD* | 115 | 1 | 161 | 175 | 128.9 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 159.7 | 112.1 | 10
14S | 336770 3WESSON | 115 | 336771*3JAM RD* | 115 | 1 | 161 | 154 | 106.1 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 154 | 106.1 | 9.5
14S | 336770 3WESSON | 115 | 336771*3JAM RD* | 115 | 1 | 161 | 167.4 | 119.9 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 154 | 106.1 | 9.5
18S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 150 | 142.7 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 150 | 142.7 | 10
18S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 164.2 | 164.7 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 150 | 142.7 | 10
10S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 137.4 | 123.6 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 137.4 | 123.5 | 8.8
10S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 147.8 | 136.9 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 137.4 | 123.5 | 8.8
14S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 145.1 | 135.2 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 145.1 | 135.2 | 9.5
14S | 336771 3JAM RD* | 115 | 336772*3HZLHST | 115 | 1 | 120 | 157.6 | 153.3 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 145.1 | 135.2 | 9.5
18S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 131.7 | 125.6 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 131.7 | 125.6 | 10
18S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 146.5 | 147.6 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 131.7 | 125.6 | 10
10S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 119.3 | 107.5 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 119.3 | 107.5 | 8.8
10S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 130.5 | 121.1 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 119.3 | 107.5 | 8.8
14S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 127.1 | 118.7 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 127.1 | 118.7 | 9.5
14S | 336772 3HZLHST | 115 | 336773*3COPHSW* | 115 | 1 | 120 | 140.2 | 136.8 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 127.1 | 118.7 | 9.5
18S | 336777*3BYRAM | 115 | 336778 3ELTON | 115 | 1 | 161 | 164.1 | 103.8 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
14S | 336777*3BYRAM | 115 | 336778 3ELTON | 115 | 1 | 161 | 159.2 | 100 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
18S | 336778*3ELTON | 115 | 336870 3JAX-SW | 115 | 1 | 161 | 175.6 | 110.3 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
18S | 336778*3ELTON | 115 | 336870 3JAX-SW | 115 | 1 | 161 | 166.8 | 104.4 | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
14S | 336778*3ELTON | 115 | 336870 3JAX-SW | 115 | 1 | 161 | 169.9 | 106.1 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
14S | 336778*3ELTON | 115 | 336870 3JAX-SW | 115 | 1 | 161 | 161.5 | 100.5 | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
18S | 336805*3WATERWY | 115 | 336806 3VKB-E* | 115 | 1 | 161 | 170.6 | 106.2 | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336805*3WATERWY | 115 | 336806 3VKB-E* | 115 | 1 | 161 | 172.1 | 107 | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 336830 8B.WLSN | 500 | 336839*8R.BRAS | 500 | 1 | 732 | 1772.2 | 102.1 | BUS 336562 [8FRKLIN 500.00] TO BUS 336820 [8G.GULF 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 243.5 | 105.1 | BUS 336906 [3JX-MON 115.00] TO BUS 336907 [3JX-MIA 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 243.6 | 105.2 | 12.4
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 245.4 | 106 | BUS 336907 [3JX-MIA 115.00] TO BUS 336940 [3RX BRN 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 243.6 | 105.2 | 12.4
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 242 | 104.2 | BUS 336880 [3R.BRAS 115.00] TO BUS 336882 [3JAX-W 115.00] CKT 1 | Ray Braswell - South Jackson 115kV | 230 | 237.3 | 102 | 31.6
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 233 | 100.3 | BUS 336882 [3JAX-W 115.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Ray Braswell - South Jackson 115kV | 230 | 237.3 | 102 | 31.6
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 252.1 | 109 | BUS 336842 [6JAX-S 230.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 253.6 | 109.9 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 248.3 | 107.4 | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
18S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 243 | 104.9 | BUS 336771 [3JAM RD* 115.00] TO BUS 336772 [3HZLHST 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 109.7
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 239.3 | 102.2 | BUS 336906 [3JX-MON 115.00] TO BUS 336907 [3JX-MIA 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 239.4 | 102.2 | 11.7
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 241.1 | 103 | BUS 336907 [3JX-MIA 115.00] TO BUS 336940 [3RX BRN 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 239.4 | 102.2 | 11.7
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 250.8 | 107.2 | BUS 336842 [6JAX-S 230.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Same | NA | NA | NA | NA
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 241.4 | 103.8 | BUS 336906 [3JX-MON 115.00] TO BUS 336907 [3JX-MIA 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 241.5 | 103.9 | 12.1
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 243.3 | 104.7 | BUS 336907 [3JX-MIA 115.00] TO BUS 336940 [3RX BRN 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 241.5 | 103.9 | 12.1
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 241.7 | 103.7 | BUS 336880 [3R.BRAS 115.00] TO BUS 336882 [3JAX-W 115.00] CKT 1 | Ray Braswell - South Jackson 115kV | 230 | 237.1 | 101.6 | 30.9
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 253.2 | 109.1 | BUS 336842 [6JAX-S 230.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Same | NA | NA | NA | NA
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 244.2 | 104.4 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 102.8
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 239.4 | 102.2 | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 102.8
10S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 234.9 | 100.1 | BUS 336771 [3JAM RD* 115.00] TO BUS 336772 [3HZLHST 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 102.8
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 251 | 108.3 | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 245.9 | 105.9 | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
14S | 336871*3JAX-FH | 115 | 336880 3R.BRAS | 115 | 1 | 230 | 241 | 103.6 | BUS 336771 [3JAM RD* 115.00] TO BUS 336772 [3HZLHST 115.00] CKT 1 | Brookhaven - Byram | * | * | * | 106.7
18S | 336890 3JAX-S | 115 | 336911*3JAX-E | 115 | 1 | 161 | 170.8 | 107 | BUS 336906 [3JX-MON 115.00] TO BUS 336908 [3JX-FON 115.00] CKT 1 | Monument St. - East Jackson | * | * | * | 103.6
14S | 336890 3JAX-S | 115 | 336911*3JAX-E | 115 | 1 | 161 | 168.1 | 104.9 | BUS 336906 [3JX-MON 115.00] TO BUS 336908 [3JX-FON 115.00] CKT 1 | Monument St. - East Jackson | * | * | * | 102
10W | 336897*3PELAHE | 115 | 336898 3MORTON | 115 | 1 | 120 | 125.8 | 102.9 | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 120 | 125.7 | 102.9 | 0
10W | 336897*3PELAHE | 115 | 336898 3MORTON | 115 | 1 | 120 | 125.7 | 102.9 | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 120 | 125.7 | 102.9 | 0
10W | 336897*3PELAHE | 115 | 336898 3MORTON | 115 | 1 | 120 | 122.9 | 100.6 | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337040*6ANDRUS | 230 | 337042 3ANDRUS | 115 | 1 | 392 | 401.9 | 102.5 | BUS 337040 [6ANDRUS 230.00] TO BUS 337050 [6INDOLA 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337060 3WINONA | 115 | 337061*3SAWYR* | 115 | 1 | 108 | 113.7 | 121.4 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337060 3WINONA | 115 | 337061*3SAWYR* | 115 | 1 | 108 | 104.8 | 106 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337060 3WINONA | 115 | 337061*3SAWYR* | 115 | 1 | 108 | 109.6 | 113.7 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337061 3SAWYR* | 115 | 337062*3ELLIOT | 115 | 1 | 108 | 98.5 | 109.8 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337061 3SAWYR* | 115 | 337062*3ELLIOT | 115 | 1 | 108 | 95.9 | 103 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337098 3CLARKD | 115 | 337100*6MEPSCLK | 230 | 1 | 250 | 301.8 | 120.7 | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337098 3CLARKD | 115 | 337100*6MEPSCLK | 230 | 1 | 250 | 301.5 | 120.6 | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337098 3CLARKD | 115 | 337100*6MEPSCLK | 230 | 1 | 250 | 301.6 | 120.6 | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337098 3CLARKD | 115 | 337100*6MEPSCLK | 230 | 1 | 250 | 301.5 | 120.6 | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 337098 3CLARKD | 115 | 337100*6MEPSCLK | 230 | 1 | 250 | 300.4 | 120.2 | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337126 3BATESV | 115 | 337135*3SARDIS | 115 | 1 | 159 | 183.4 | 125 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337126 3BATESV | 115 | 337135*3SARDIS | 115 | 1 | 159 | 183.4 | 124.6 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | * | 158.6
18S | 337135 3SARDIS | 115 | 337136*3SNTOBI | 115 | 1 | 176 | 159.6 | 107 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337135 3SARDIS | 115 | 337136*3SNTOBI | 115 | 1 | 176 | 159.9 | 106.6 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | * | 158.6
18S | 337136 3SNTOBI | 115 | 337137*3CLDWTR | 115 | 1 | 108 | 119.6 | 135.2 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337136 3SNTOBI | 115 | 337137*3CLDWTR | 115 | 1 | 108 | 120 | 134.8 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | * | 158.6
18S | 337137 3CLDWTR | 115 | 337138*3HRNADO | 115 | 1 | 108 | 96.5 | 113.4 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337137 3CLDWTR | 115 | 337138*3HRNADO | 115 | 1 | 108 | 97.1 | 113.2 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | * | 158.6
18S | 337139 3GETWEL | 115 | 337141*3NESBT* | 115 | 1 | 239 | 233.7 | 104.4 | BUS 337144 [3GRNBRK 115.00] TO BUS 337150 [3HN LAK 115.00] CKT 1 | Horn Lake - Getwell | * | * | * | 217
18S | 337143*3PLUM PT | 115 | 337144 3GRNBRK | 115 | 1 | 239 | 270.1 | 119.6 | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337144*3GRNBRK | 115 | 337150 3HN LAK | 115 | 1 | 239 | 203 | 106.8 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337144*3GRNBRK | 115 | 337150 3HN LAK | 115 | 1 | 239 | 300.3 | 128.8 | BUS 337139 [3GETWEL 115.00] TO BUS 337140 [6GETWELL 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337144*3GRNBRK | 115 | 337150 3HN LAK | 115 | 1 | 239 | 366 | 159.2 | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337144*3GRNBRK | 115 | 337150 3HN LAK | 115 | 1 | 239 | 282.1 | 119.9 | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337150 3HN LAK | 115 | 337181*5HN LAK | 161 | 1 | 235 | 337.5 | 143.6 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337150 3HN LAK | 115 | 337180*6HN LAK | 230 | 1 | 392 | 415.5 | 106 | BUS 337139 [3GETWEL 115.00] TO BUS 337140 [6GETWELL 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337150 3HN LAK | 115 | 337180*6HN LAK | 230 | 1 | 392 | 475.3 | 121.2 | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337150 3HN LAK | 115 | 337181*5HN LAK | 161 | 1 | 235 | 249.7 | 106.2 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337150 3HN LAK | 115 | 337180*6HN LAK | 230 | 1 | 392 | 404.2 | 103.1 | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337181*5HN LAK | 161 | 360174 5ALLEN FP | 161 | 1 | 208 | 337.4 | 174.9 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337181*5HN LAK | 161 | 360174 5ALLEN FP | 161 | 1 | 208 | 249.7 | 123.6 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337800 3HASKEL | 115 | 337801*3BENT-S* | 115 | 1 | 159 | 149.9 | 105.1 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 167.4
18S | 337803*3BRYANT | 115 | 337804 3MABEL | 115 | 1 | 159 | 176.1 | 112.8 | BUS 337740 [3HSEHVE 115.00] TO BUS 337741 [3BUTERF 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 167.4
18S | 337803*3BRYANT | 115 | 337804 3MABEL | 115 | 1 | 159 | 168.1 | 107.4 | BUS 337741 [3BUTERF 115.00] TO BUS 337800 [3HASKEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 167.4
14S | 337803*3BRYANT | 115 | 337804 3MABEL | 115 | 1 | 159 | 157.8 | 100.4 | BUS 337740 [3HSEHVE 115.00] TO BUS 337741 [3BUTERF 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 150.2
18S | 337804 3MABEL | 115 | 337808*8MABEL | 500 | 2 | 447 | 455.3 | 101.9 | BUS 337804 [3MABEL 115.00] TO BUS 337808 [8MABEL 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337804 3MABEL | 115 | 337808*8MABEL | 500 | 1 | 448 | 456.2 | 101.8 | BUS 337804 [3MABEL 115.00] TO BUS 337808 [8MABEL 500.00] CKT 2 | Same | NA | NA | NA | NA
18S | 337905 5RUSL-E | 161 | 337906*5RUSL-N | 161 | 1 | 396 | 396 | 101 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 267.2 | 124.6 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 267.2 | 124.6 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 223 | 267.2 | 124.6 | 27
18S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 283.1 | 132.9 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 223 | 267.2 | 124.6 | 27
18S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 250.5 | 115.6 | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 223 | 231.5 | 105.8 | 88.2
18S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 219.4 | 100.4 | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 223 | 231.5 | 105.8 | 88.2
14S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 241.7 | 111 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 241.7 | 111 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 223 | 241.7 | 111 | 26
14S | 337921 5MOR-E | 161 | 337927*5GLEASN | 161 | 1 | 223 | 257.2 | 118.7 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 223 | 241.7 | 111 | 26
18S | 337923 5P HILL | 161 | 337925*5GREENB | 161 | 1 | 310 | 302.4 | 100.9 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | * | 247
18S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 257.6 | 120.3 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 257.6 | 120.3 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 223 | 257.6 | 120.3 | 27
18S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 273.3 | 128.6 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 223 | 257.6 | 120.3 | 27
18S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 240.9 | 111.4 | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 223 | 222.1 | 101.6 | 88.2
14S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 232.1 | 106.8 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 232.1 | 106.8 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 223 | 232.1 | 106.8 | 26
14S | 337927 5GLEASN | 161 | 338424*5TYLER | 161 | 1 | 223 | 247.5 | 114.4 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 223 | 232.1 | 106.8 | 26
18S | 337928*3CONW-W | 115 | 337929 3LK CON | 115 | 1 | 239 | 234.6 | 101.9 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337928*3CONW-W | 115 | 338422 5CONW-W | 161 | 1 | 224 | 234.6 | 104.7 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337929*3LK CON | 115 | 337930 3MAYFL | 115 | 1 | 239 | 278.5 | 117.8 | BUS 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 239 | 256.8 | 108.1 | 39.9
18S | 337929*3LK CON | 115 | 337930 3MAYFL | 115 | 1 | 239 | 273.7 | 115.6 | BUS 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 239 | 256.8 | 108.1 | 39.9
18S | 337929*3LK CON | 115 | 337930 3MAYFL | 115 | 1 | 239 | 257.3 | 108.3 | BUS 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 239 | 256.8 | 108.1 | 39.9
18S | 337929*3LK CON | 115 | 337930 3MAYFL | 115 | 1 | 239 | 238.4 | 100.1 | BUS 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337929*3LK CON | 115 | 337930 3MAYFL | 115 | 1 | 239 | 269 | 113.5 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 295 | 104.5 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 295.5 | 105.2 | BUS 337823 [3LR-W 1 115.00] TO BUS 337839 [3LRPALM1 115.00] CKT 1 | L. R. West - L. R. Gaines | * | * | * | 0
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 293.5 | 104.4 | BUS 337839 [3LRPALM1 115.00] TO BUS 337843 [3LR-WOD 115.00] CKT 1 | L. R. West - L. R. Gaines | * | * | * | 0
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 290.2 | 103.2 | BUS 338483 [3NLR-DX 115.00] TO BUS 338487 [3LAKEWD 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 284 | 100.9 | BUS 338484 [3NLR-LV 115.00] TO BUS 338487 [3LAKEWD 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 295 | 104.5 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 283 | 297.3 | 105.3 | 27
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 297.8 | 105.5 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 283 | 297.3 | 105.3 | 27
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282.7 | 100.4 | BUS 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 283 | 283.2 | 100.1 | 247
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 296 | 105.1 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 283 | 283.2 | 100.1 | 247
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 299 | 106.2 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 283 | 283.2 | 100.1 | 247
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 289.3 | 102.7 | BUS 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 283 | 283.2 | 100.1 | 247
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282.9 | 100.5 | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 283 | 282.3 | 100.3 | 7.1
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282.6 | 100.4 | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 283 | 282.3 | 100.3 | 7.1
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 284.4 | 101.1 | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 283 | 284.1 | 101 | 28
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285.5 | 101.5 | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 283 | 284.1 | 101 | 28
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285.6 | 101.5 | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 283 | 284.1 | 101 | 28
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 296.9 | 105.5 | BUS 337826 [3LR-PIN 115.00] TO BUS 337840 [3LR-WAL 115.00] CKT 1 | L. R. Gaines - Pinnacle | 283 | 283.7 | 100.6 | 70.1
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 287 | 101.9 | BUS 337840 [3LR-WAL 115.00] TO BUS 337841 [3LR-CAM 115.00] CKT 1 | L. R. Gaines - Pinnacle | 283 | 283.7 | 100.6 | 70.1
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.6 | 100.7 | BUS 337841 [3LR-CAM 115.00] TO BUS 337842 [3LR-GNS 115.00] CKT 1 | L. R. Gaines - Pinnacle | 283 | 283.7 | 100.6 | 70.1
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 290.8 | 103.5 | BUS 337818 [3LR-S 1 115.00] TO BUS 337821 [3LR-ROK 115.00] CKT 1 | L. R. South - L. R. West | 283 | 283.7 | 101.1 | 63.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.8 | 102.8 | BUS 337821 [3LR-ROK 115.00] TO BUS 337822 [3LR-BOY 115.00] CKT 1 | L. R. South - L. R. West | 283 | 283.7 | 101.1 | 63.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 286.7 | 102.1 | BUS 337822 [3LR-BOY 115.00] TO BUS 337823 [3LR-W 1 115.00] CKT 1 | L. R. South - L. R. West | 283 | 283.7 | 101.1 | 63.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 293.5 | 104.3 | BUS 337818 [3LR-S 1 115.00] TO BUS 337844 [3LR-SPR* 115.00] CKT 1 | L. R. South - N. L. R. Dixie | 283 | 283.6 | 100.7 | 60.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 291.3 | 103.5 | BUS 337844 [3LR-SPR* 115.00] TO BUS 337846 [3LR-FOU 115.00] CKT 1 | L. R. South - N. L. R. Dixie | 283 | 283.6 | 100.7 | 60.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 289.3 | 102.8 | BUS 337846 [3LR-FOU 115.00] TO BUS 337847 [3LR-E 1 115.00] CKT 1 | L. R. South - N. L. R. Dixie | 283 | 283.6 | 100.7 | 60.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 286.2 | 101.7 | BUS 337847 [3LR-E 1 115.00] TO BUS 338483 [3NLR-DX 115.00] CKT 1 | L. R. South - N. L. R. Dixie | 283 | 283.6 | 100.7 | 60.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.2 | 102.4 | BUS 337804 [3MABEL 115.00] TO BUS 337815 [3LR-MAN 115.00] CKT 1 | Mabelvale - L. R. South | 283 | 281.9 | 100.1 | 80.4
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 287.9 | 102.3 | BUS 337815 [3LR-MAN 115.00] TO BUS 337816 [3LR-CHI 115.00] CKT 1 | Mabelvale - L. R. South | 283 | 281.9 | 100.1 | 80.4
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 286.1 | 101.6 | BUS 337816 [3LR-CHI 115.00] TO BUS 337817 [3LR-IND 115.00] CKT 1 | Mabelvale - L. R. South | 283 | 281.9 | 100.1 | 80.4
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.8 | 100.8 | BUS 337817 [3LR-IND 115.00] TO BUS 337818 [3LR-S 1 115.00] CKT 1 | Mabelvale - L. R. South | 283 | 281.9 | 100.1 | 80.4
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.3 | 102.5 | BUS 337804 [3MABEL 115.00] TO BUS 337820 [3LR-ALX 115.00] CKT 1 | Mabelvale - L. R. South 2 | 283 | 283.5 | 100.7 | 62.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285 | 101.3 | BUS 337818 [3LR-S 1 115.00] TO BUS 337819 [3LR-HIN 115.00] CKT 1 | Mabelvale - L. R. South 2 | 283 | 283.5 | 100.7 | 62.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 286.1 | 101.6 | BUS 337819 [3LR-HIN 115.00] TO BUS 337820 [3LR-ALX 115.00] CKT 1 | Mabelvale - L. R. South 2 | 283 | 283.5 | 100.7 | 62.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 303.8 | 107.8 | BUS 337826 [3LR-PIN 115.00] TO BUS 337827 [3ROL RD* 115.00] CKT 1 | Mayflower - L. R. Pinnacle | 283 | 304.3 | 107.9 | 5
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 304.7 | 108.1 | BUS 337827 [3ROL RD* 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Mayflower - L. R. Pinnacle | 283 | 304.3 | 107.9 | 5
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282.4 | 100.4 | BUS 337919 [L&D #91 161.00] TO BUS 337920 [5MOR-W 161.00] CKT 1 | Morrilton East - AECC Hydro STA No. 9 | 283 | 282.7 | 100.5 | 17.7
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.5 | 100.8 | BUS 337920 [5MOR-W 161.00] TO BUS 337921 [5MOR-E 161.00] CKT 1 | Morrilton East - AECC Hydro STA No. 9 | 283 | 282.7 | 100.5 | 17.7
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285.1 | 101.5 | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 283 | 283.9 | 100.9 | 88.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282.7 | 100.5 | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 283 | 283.9 | 100.9 | 88.2
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 284.5 | 101.1 | BUS 337620 [3WOODW 115.00] TO BUS 337634 [3PB-DRK 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 281.7 | 100.1 | BUS 337648 [3WH BLF 115.00] TO BUS 337650 [WBLFXF 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 281.7 | 100.1 | BUS 337648 [3WH BLF 115.00] TO BUS 337650 [WBLFXF 500.00] CKT 2 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 291.9 | 103.8 | BUS 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 293.6 | 104.5 | BUS 337804 [3MABEL 115.00] TO BUS 337808 [8MABEL 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 293.6 | 104.5 | BUS 337804 [3MABEL 115.00] TO BUS 337808 [8MABEL 500.00] CKT 2 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285.5 | 101.6 | BUS 337804 [3MABEL 115.00] TO BUS 337825 [3KANIS * 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 297.6 | 105.9 | BUS 337859 [3WRIGHTS 115.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 281.9 | 100.3 | BUS 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.5 | 102.9 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 313.2 | 111.2 | BUS 337930 [3MAYFL 115.00] TO BUS 337936 [3SYLVN 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.6 | 100.8 | BUS 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.1 | 102.4 | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283 | 100.5 | BUS 338144 [8ISXF 5 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 289.6 | 103.2 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.1 | 100.6 | BUS 337818 [3LR-S 1 115.00] TO BUS 338749 [3IRNTON# 115.00] CKT 1 | Wrightsville EHV IPP - L. R. South | 283 | 282.8 | 100.5 | 9.7
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 283.5 | 100.7 | BUS 337859 [3WRIGHTS 115.00] TO BUS 338749 [3IRNTON# 115.00] CKT 1 | Wrightsville EHV IPP - L. R. South | 283 | 282.8 | 100.5 | 9.7
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 301 | 107.1 | BUS 337857 [3LR-PRT 115.00] TO BUS 337858 [3LR-145 115.00] CKT 1 | Wrightsville EHV IPP - Lynch | 283 | 295.4 | 105 | 87.9
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 294 | 104.5 | BUS 337857 [3LR-PRT 115.00] TO BUS 338480 [3FAUKLK 115.00] CKT 1 | Wrightsville EHV IPP - Lynch | 283 | 295.4 | 105 | 87.9
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 302 | 107.4 | BUS 337858 [3LR-145 115.00] TO BUS 337859 [3WRIGHTS 115.00] CKT 1 | Wrightsville EHV IPP - Lynch | 283 | 295.4 | 105 | 87.9
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 290.4 | 103.2 | BUS 337952 [3LYNCH 115.00] TO BUS 338480 [3FAUKLK 115.00] CKT 1 | Wrightsville EHV IPP - Lynch | 283 | 295.4 | 105 | 87.9
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.6 | 102.7 | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | * | * | * | 154.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 284.6 | 101.2 | BUS 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | * | * | 154.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 288.7 | 102.7 | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | * | * | * | 154.6
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 282 | 100.2 | BUS 337740 [3HSEHVE 115.00] TO BUS 337741 [3BUTERF 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 167.4
18S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 281.7 | 100.1 | BUS 337741 [3BUTERF 115.00] TO BUS 337800 [3HASKEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | * | 167.4
14S | 337930 3MAYFL | 115 | 337931*3MORGAN | 115 | 1 | 283 | 285.5 | 100.6 | BUS 337930 [3MAYFL 115.00] TO BUS 337936 [3SYLVN 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337939 5GOLDCR* | 161 | 337940*5HAMLET* | 161 | 1 | 223 | 242.3 | 118.4 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | * | 247
14S | 337939 5GOLDCR* | 161 | 337940*5HAMLET* | 161 | 1 | 223 | 212.9 | 101.2 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | * | 218.5
18S | 337951*3JXNVL-S | 115 | 338481 3MCALMT | 115 | 1 | 159 | 191.9 | 126.3 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337951*3JXNVL-S | 115 | 338481 3MCALMT | 115 | 1 | 159 | 167.8 | 109.5 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 220.7 | 141.7 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 158.3 | 100.7 | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 167.4 | 106.9 | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | * | * | * | 154.6
18S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 167.9 | 107.1 | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | * | * | * | 154.6
14S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 193.5 | 123.8 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 169.8 | 108.2 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337952 3LYNCH | 115 | 338481*3MCALMT | 115 | 1 | 159 | 175.3 | 111.9 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338022 5MOSES | 161 | 338029*5FCTY-N* | 161 | 1 | 112 | 110 | 100.2 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | * | * | 119.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 131.8 | 119.9 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 127.6 | 115.8 | 35.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 126.4 | 114.7 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 112 | 127.6 | 115.8 | 35.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 128.3 | 116.5 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 112 | 127.6 | 115.8 | 35.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 130.4 | 118.6 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 127.6 | 115.8 | 35.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 157.8 | 143.5 | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 135.2 | 122.2 | 38.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 148.5 | 134.8 | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 112 | 135.2 | 122.2 | 38.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 148.5 | 134.8 | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 135.2 | 122.2 | 38.1
18S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 133.2 | 120.7 | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 135.2 | 122.2 | 38.1
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 115.8 | 104.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 111.9 | 100.6 | 34
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 112.5 | 101.2 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 112 | 111.9 | 100.6 | 34
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 114.5 | 103.1 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 111.9 | 100.6 | 34
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 137 | 123.5 | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 116.3 | 104.3 | 35.8
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 128.5 | 115.6 | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 112 | 116.3 | 104.3 | 35.8
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 128.5 | 115.6 | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 116.3 | 104.3 | 35.8
14S | 338033*5PARKIN | 161 | 338041 5TWIST | 161 | 1 | 112 | 114.5 | 102.8 | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 116.3 | 104.3 | 35.8
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 128.4 | 117.8 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 124.4 | 113.6 | 35.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 123.2 | 112.5 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 112 | 124.4 | 113.6 | 35.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 125 | 114.3 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 112 | 124.4 | 113.6 | 35.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 127.1 | 116.4 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 124.4 | 113.6 | 35.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 153.6 | 141.4 | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 131.8 | 120.1 | 38.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 144.7 | 132.7 | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 112 | 131.8 | 120.1 | 38.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 144.7 | 132.7 | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 131.8 | 120.1 | 38.1
18S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 129.9 | 118.5 | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 131.8 | 120.1 | 38.1
14S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 133.5 | 121.3 | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 113.4 | 102.1 | 35.8
14S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 125.2 | 113.4 | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 112 | 113.4 | 102.1 | 35.8
14S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 125.3 | 113.4 | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 112 | 113.4 | 102.1 | 35.8
14S | 338041*5TWIST | 161 | 338165 5MTREE | 161 | 1 | 112 | 111.6 | 100.6 | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 113.4 | 102.1 | 35.8
14S | 338102 5HARR-W | 161 | 338681*5HARR-S | 161 | 1 | 223 | 228.1 | 106.2 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 238.1
18S | 338102*5HARR-W | 161 | 338681 5HARR-S | 161 | 1 | 223 | 248.8 | 122.8 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
18S | 338104 5HARR-E | 161 | 338681*5HARR-S | 161 | 1 | 223 | 269.7 | 132.1 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
10S | 338104*5HARR-E | 161 | 338681 5HARR-S | 161 | 1 | 223 | 225.1 | 101.1 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 217.5
14S | 338104*5HARR-E | 161 | 338681 5HARR-S | 161 | 1 | 223 | 247.4 | 114.1 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 238.1
10W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 185.3 | 109.3 | BUS 338123 [5BULLSH* 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals Dam - Harrison East | 167 | 174.8 | 102.8 | 27.2
10W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 173.8 | 102.2 | BUS 338104 [5HARR-E 161.00] TO BUS 338121 [5SUMMIT 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 174.7 | 102.7 | 22.7
10W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 179 | 105.3 | BUS 338121 [5SUMMIT 161.00] TO BUS 338122 [5FLIPN 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 174.7 | 102.7 | 22.7
10W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 183.5 | 108.1 | BUS 338122 [5FLIPN 161.00] TO BUS 338123 [5BULLSH* 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 174.7 | 102.7 | 22.7
14W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 183.7 | 109.1 | BUS 338123 [5BULLSH* 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals Dam - Harrison East | 167 | 172.2 | 101.9 | 29.8
14W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 171.2 | 101.3 | BUS 338104 [5HARR-E 161.00] TO BUS 338121 [5SUMMIT 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 172.1 | 101.8 | 24.7
14W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 176.6 | 104.6 | BUS 338121 [5SUMMIT 161.00] TO BUS 338122 [5FLIPN 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 172.1 | 101.8 | 24.7
14W | 338108 5ST_JOE | 161 | 338110*5HILLTOP | 161 | 1 | 167 | 181.6 | 107.8 | BUS 338122 [5FLIPN 161.00] TO BUS 338123 [5BULLSH* 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 172.1 | 101.8 | 24.7
18S | 338108*5ST_JOE | 161 | 338110 5HILLTOP | 161 | 1 | 167 | 158.3 | 100.4 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
18S | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 184.2 | 108.6 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 167 | 184.9 | 109 | 8.8
18S | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 188.5 | 111.2 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 167 | 184.9 | 109 | 8.8
18S | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 179.5 | 109 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
14S | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 177.2 | 103 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 167 | 177.8 | 103.4 | 8.3
14S | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 181.6 | 105.6 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 167 | 177.8 | 103.4 | 8.3
14W | 338123 5BULLSH* | 161 | 505460*BULL SH5 | 161 | 1 | 167 | 174.9 | 101.7 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 167 | 172.3 | 100.2 | 6.3
18S | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.2 | 101.5 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.7 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.1 | 105.6 | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 100.6 | BUS 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.9 | 101.5 | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 164.4 | 108 | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.6 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 337368 [8MTOLIV 500.00] TO BUS 337369 [6MTOLIV 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.8 | 106.5 | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 172.4 | 114 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.3 | 101.5 | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.9 | BUS 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.9 | 101.9 | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.7 | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.7 | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.2 | 109.5 | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 101.1 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 337304 [6MONTGY 230.00] TO BUS 500200 [COLFAX 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338020 [5BRNK-E 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | * | * | * | 24.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 101.1 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | * | * | 102.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 101.3 | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | * | 116.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.4 | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 154.6 | 101.2 | 24.4
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 101.6 | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 154.6 | 101.2 | 24.4
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 100.6 | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 153.7 | 100.7 | 4.6
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 100.7 | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 153.7 | 100.7 | 4.6
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.4 | 101.2 | BUS 338151 [5NEWPO 161.00] TO BUS 338734 [5SHOFNR 161.00] CKT 1 | Bailey SES AECC - Newport | 148 | 154.4 | 101.2 | 2.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.3 | 101.1 | BUS 338734 [5SHOFNR 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Newport | 148 | 154.4 | 101.2 | 2.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.5 | 102.5 | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 155 | 101.5 | 36.4
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 101.8 | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 155 | 101.5 | 36.4
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.2 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 148 | 154.1 | 100.9 | 5.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.7 | 101.3 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 148 | 154.1 | 100.9 | 5.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.4 | BUS 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 152.8 | 100 | 56.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.3 | BUS 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 152.8 | 100 | 56.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.1 | BUS 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 152.8 | 100 | 56.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 159.4 | 104.4 | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 148 | 167.2 | 109.6 | 0
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 164 | 107.6 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.7 | 101.3 | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.3 | 102.4 | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 158 | 103.5 | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 163 | 106.9 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.7 | 106 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 158.1 | 103.6 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.9 | 102.1 | 72.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154 | 101 | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 148 | 154.4 | 101.2 | 4.9
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101 | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 148 | 154.4 | 101.2 | 4.9
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155 | 101.6 | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.2 | 102.4 | 19.6
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 102 | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.2 | 102.4 | 19.6
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 102.1 | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.2 | 102.4 | 19.6
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 167.2 | 109.6 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.7 | 109.2 | 26.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 165.2 | 108.3 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.7 | 109.2 | 26.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 165.8 | 108.7 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.7 | 109.2 | 26.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.5 | 109.2 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.7 | 109.2 | 26.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155 | 101.6 | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 155.9 | 102.2 | 20.7
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.9 | 102.2 | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 148 | 155.9 | 102.2 | 20.7
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 101.8 | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 155.9 | 102.2 | 20.7
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.7 | 101.4 | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 153.7 | 100.6 | 30.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 100.8 | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 153.7 | 100.6 | 30.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.2 | 101 | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.1 | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.3 | 101.1 | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154 | 100.9 | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.5 | 102.5 | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 100.5 | BUS 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.5 | 101.9 | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.3 | BUS 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.4 | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.4 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 158.3 | 103.9 | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 174.2 | 114.5 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 100.5 | BUS 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.1 | 102.2 | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 175.1 | 115.2 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.7 | 106.1 | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.5 | 106 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.2 | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.3 | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.4 | BUS 300038 [7ESSEX 345.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.3 | BUS 300038 [7ESSEX 345.00] TO BUS 344974 [7LUTESVIL 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 157.7 | 103.4 | BUS 300040 [7FLETCH 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.8 | 102.7 | BUS 300041 [7FRANKS 345.00] TO BUS 300042 [7HUBEN 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 100.8 | BUS 300041 [7FRANKS 345.00] TO BUS 344154 [7BLAND 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 100.8 | BUS 300041 [7FRANKS 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100 | BUS 300045 [7MORGAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 162.8 | 106.9 | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.5 | 109.5 | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.1 | BUS 344102 [7BELLEAU 345.00] TO BUS 345747 [7SIOUX 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.4 | BUS 344154 [7BLAND 345.00] TO BUS 344886 [7LABADIE 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.4 | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100 | BUS 344886 [7LABADIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.8 | 102.1 | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.7 | 102.7 | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 100.7 | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.1 | BUS 360023 [8FREEPORT TN500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 100.7 | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.1 | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.4 | BUS 360037 [8JVILLE FP 500.00] TO BUS 360048 [8DAVIDSON TN500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 101.7 | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.1 | BUS 360042 [8PARADISE FP500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 100.5 | BUS 360050 [8MAURY TN 500.00] TO BUS 360052 [8BR FERRY NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 100.7 | BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 100.6 | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 101.9 | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.2 | BUS 382500 [8RACOONCK 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 99 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.3 | BUS 506935 [FLINTCR7 345.00] TO BUS 547481 [MON383 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.7 | 102 | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154 | 100.9 | BUS 508298 [LYDIA 7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155 | 101.6 | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 101.8 | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.5 | 101.9 | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 100.6 | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.2 | BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.2 | BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 101.6 | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.7 | 101.1 | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.1 | 100.7 | 111.9
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 100.5 | BUS 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.1 | 100.7 | 111.9
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.2 | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.1 | 100.7 | 111.9
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.3 | BUS 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 148 | 156.5 | 102.4 | 83.1
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.4 | BUS 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 155.8 | 101.9 | 70.5
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 100.7 | BUS 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 148 | 155.8 | 101.9 | 70.5
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.5 | BUS 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 155.8 | 101.9 | 70.5
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.7 | 106.2 | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 159.8 | 104.9 | 23.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 160.1 | 105.1 | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 159.8 | 104.9 | 23.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 159.4 | 104.6 | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 159.8 | 104.9 | 23.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 159 | 104.4 | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 159.8 | 104.9 | 23.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 160.8 | 105.6 | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 159.8 | 104.9 | 23.2
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.1 | 101.8 | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 148 | 164.6 | 108.2 | 0
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 164.3 | 108.1 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 163.8 | 107.8 | 9.1
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 163.6 | 107.6 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 163.8 | 107.8 | 9.1
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 163.3 | 107.4 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 163.8 | 107.8 | 9.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.3 | 101.5 | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 148 | 154.4 | 101.5 | 0
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 148 | 152.5 | 100.3 | 0
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 148 | 152.5 | 100.3 | 0
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.1 | 102 | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 154.9 | 101.9 | 25.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.5 | 102.3 | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 154.9 | 101.9 | 25.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 102.4 | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 155.9 | 102.6 | 4.6
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.8 | 102.5 | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 155.9 | 102.6 | 4.6
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 148 | 152.6 | 100.3 | 24.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.6 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 148 | 152.9 | 100.6 | 19.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.7 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 148 | 152.9 | 100.6 | 19.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.1 | BUS 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.9 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 101.1 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.5 | BUS 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 152.7 | 100.4 | 164.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.4 | 102.9 | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 154.9 | 101.9 | 36.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 102.1 | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 154.9 | 101.9 | 36.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.8 | BUS 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 152.9 | 100.5 | 23.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.6 | BUS 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 152.9 | 100.5 | 23.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.7 | BUS 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 152.9 | 100.5 | 23.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.7 | 101.8 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 148 | 154.2 | 101.5 | 6.3
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.9 | 101.9 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 148 | 154.2 | 101.5 | 6.3
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.7 | BUS 338202 [5JIMHL 161.00] TO BUS 300115 [5STFRAN 161.00] CKT 1 | Hayti South to St Francis | 148 | 153.5 | 101 | 15.9
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 101.1 | BUS 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 153.2 | 100.7 | 59.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 101 | BUS 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 153.2 | 100.7 | 59.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.9 | BUS 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 153.2 | 100.7 | 59.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.6 | 100.3 | BUS 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 153.2 | 100.7 | 59.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 160.2 | 105.4 | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 148 | 169.1 | 111.5 | 0
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 163.9 | 107.9 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.9 | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 102.4 | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 157.3 | 103.5 | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 162.8 | 107.2 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.4 | 106.3 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 157.6 | 103.7 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 155.1 | 102 | 78.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.4 | 101.6 | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 148 | 155.1 | 102 | 5.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.5 | 102.3 | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.8 | 103.2 | 20.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.1 | 102.7 | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.8 | 103.2 | 20.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.2 | 102.8 | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 156.8 | 103.2 | 20.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 169.1 | 111.5 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.4 | 111 | 27.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.9 | 110 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.4 | 111 | 27.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 167.6 | 110.5 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.4 | 111 | 27.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 168.4 | 111 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.4 | 111 | 27.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338160 [5EBON S* 161.00] TO BUS 338410 [5WM-DOV 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 148 | 153.1 | 100.7 | 94.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338160 [5EBON S* 161.00] TO BUS 338411 [5WM-GAT 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 148 | 153.1 | 100.7 | 94.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.3 | 102.2 | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 156.4 | 102.9 | 23.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.4 | 102.9 | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 148 | 156.4 | 102.9 | 23.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.6 | 102.4 | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 156.4 | 102.9 | 23.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 148 | 152.8 | 100.5 | 1.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100.4 | BUS 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 148 | 152.8 | 100.5 | 1.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 102.2 | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 153.9 | 101.3 | 45.4
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.3 | 101.5 | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 153.9 | 101.3 | 45.4
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 334204 [6CHINA 230.00] TO BUS 334327 [6AMELIA 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100.4 | BUS 334320 [8CYPRESS 500.00] TO BUS 334325 [8HARTBRG 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 334325 [8HARTBRG 500.00] TO BUS 334370 [8COTNWD1 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.7 | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.1 | BUS 334370 [8COTNWD1 500.00] TO BUS 334372 [XMFRINT1 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 335642 [6ESSO 2 230.00] TO BUS 335643 [6G5EXXON 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.1 | BUS 335836 [8MCKNT 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 336562 [8FRKLIN 500.00] TO BUS 336820 [8G.GULF 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.6 | 100.3 | BUS 336830 [8B.WLSN 500.00] TO BUS 337427 [8PERYVIL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.5 | 101.7 | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 337107 [6MOONLAK 230.00] TO BUS 337123 [6BATESV 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.3 | BUS 337320 [3PLANT 115.00] TO BUS 337322 [3MURRLA 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.2 | BUS 337515 [8MCNEIL 500.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 337515 [8MCNEIL 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101.2 | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.6 | 103 | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101 | BUS 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 337672 [4MURFRE 138.00] TO BUS 337673 [3MURF-S 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.2 | BUS 337753 [8HSEHV 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101 | BUS 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.9 | 102.6 | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101.2 | BUS 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.7 | 101.1 | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.1 | BUS 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 102.2 | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 159 | 104.6 | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 172.8 | 114 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.2 | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.6 | BUS 338193 [5BLYINT 161.00] TO BUS 338200 [5HAYTI 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.6 | 100.4 | BUS 338200 [5HAYTI 161.00] TO BUS 338202 [5JIMHL 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101 | BUS 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100.1 | BUS 337304 [6MONTGY 230.00] TO BUS 500170 [CLARN 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.4 | 101.5 | BUS 337562 [7ELDEHV 345.00] TO BUS 337569 [ 7SAREPT 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101.1 | BUS 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 164.1 | 108.1 | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 162.7 | 107.2 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338200 [5HAYTI 161.00] TO BUS 344720 [1HAYTI N 34.500] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338201 [5PRTGVL 161.00] TO BUS 345534 [1PORTGVIL 34.500] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 500200 [COLFAX 6 230.00] TO BUS 500770 [RODEMR 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 101 | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101 | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 2 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.8 | 101.8 | BUS 300038 [7ESSEX 345.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.6 | BUS 300038 [7ESSEX 345.00] TO BUS 344974 [7LUTESVIL 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 300040 [7FLETCH 345.00] TO BUS 300047 [7SALEM 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 157.7 | 103.8 | BUS 300040 [7FLETCH 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.4 | 102.9 | BUS 300041 [7FRANKS 345.00] TO BUS 300042 [7HUBEN 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.2 | 101.4 | BUS 300041 [7FRANKS 345.00] TO BUS 344154 [7BLAND 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.1 | 101.4 | BUS 300041 [7FRANKS 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.8 | BUS 300045 [7MORGAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 165 | 108.7 | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.6 | 109.9 | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.8 | BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7CHOTEAU 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.7 | BUS 337569 [ 7SAREPT 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 344088 [7BAILEY 345.00] TO BUS 345669 [7RUSH 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.2 | BUS 344088 [7BAILEY 345.00] TO BUS 345859 [7TYSON 2 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 344102 [7BELLEAU 345.00] TO BUS 344535 [7ENON 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.7 | BUS 344102 [7BELLEAU 345.00] TO BUS 345747 [7SIOUX 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.9 | BUS 344154 [7BLAND 345.00] TO BUS 344886 [7LABADIE 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.2 | 102.1 | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 344886 [7LABADIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100.4 | BUS 345088 [7MCCREDIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100.4 | BUS 345088 [7MCCREDIE 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 345669 [7RUSH 345.00] TO BUS 345858 [7TYSON 1 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 360010 [8RUTHERFORD 500.00] TO BUS 360050 [8MAURY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.1 | 102.1 | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.5 | 103 | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101.2 | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101.3 | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 360023 [8FREEPORT TN500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.7 | BUS 360023 [8FREEPORT TN500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.9 | 101.3 | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.4 | 100.3 | BUS 360033 [8UNION MS 500.00] TO BUS 360541 [8PLEASANT HL500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.6 | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 101.1 | BUS 360037 [8JVILLE FP 500.00] TO BUS 360048 [8DAVIDSON TN500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.5 | 103 | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.2 | 100.7 | BUS 360042 [8PARADISE FP500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 360048 [8DAVIDSON TN500.00] TO BUS 360581 [8PIN HOOK TN500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 101.1 | BUS 360050 [8MAURY TN 500.00] TO BUS 360052 [8BR FERRY NP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 360052 [8BR FERRY NP500.00] TO BUS 360060 [8MADISON AL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.1 | BUS 360052 [8BR FERRY NP500.00] TO BUS 360088 [8LIMESTONE 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 360060 [8MADISON AL 500.00] TO BUS 360065 [8WID CRK FP 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.7 | 100.4 | BUS 360065 [8WID CRK FP 500.00] TO BUS 360079 [8RACCOON MTN500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 101 | BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.2 | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360662 [8BRADLEY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 360085 [8WBNP #1 500.00] TO BUS 360090 [8ROANE TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 360086 [8WBNP #2 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.1 | 100.7 | BUS 360086 [8WBNP #2 500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 360086 [8WBNP #2 500.00] TO BUS 360687 [8WBNP #3 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.6 | BUS 360090 [8ROANE TN 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.2 | 101.4 | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.1 | 102.7 | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 360541 [8PLEASANT HL500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.3 | 100.2 | BUS 360662 [8BRADLEY TN 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 380004 [8BULLSLUI 500.00] TO BUS 380019 [8BIG SHANTY 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 380021 [8MOSTELLE 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 380024 [8N TIFTON 500.00] TO BUS 382500 [8RACOONCK 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.9 | BUS 382500 [8RACOONCK 500.00] TO BUS 383021 [8LONGLEAF 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.6 | 100.3 | BUS 383021 [8LONGLEAF 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 384157 [8MILLER8 500.00] TO BUS 384375 [8S.BESS 8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 384157 [8MILLER8 500.00] TO BUS 385307 [8WVERN SS 500.00] CKT 99 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 384157 [8MILLER8 500.00] TO BUS 385312 [8CLAY 8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 384375 [8S.BESS 8 500.00] TO BUS 385123 [8BILLNGSS 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 384512 [8SNOWDN8 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 385123 [8BILLNGSS 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.5 | 100.9 | BUS 506935 [FLINTCR7 345.00] TO BUS 547481 [MON383 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.6 | BUS 506945 [CHAMSPR7 345.00] TO BUS 506959 [TONTITN7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.3 | 102.9 | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 508072 [NWTXARK7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101.1 | BUS 508298 [LYDIA 7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 157.2 | 103.5 | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.8 | 102.5 | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.5 | 102.3 | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 101.2 | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.8 | BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.9 | 102.6 | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.6 | 100.4 | BUS 510907 [PITTSB-7 345.00] TO BUS 514809 [JOHNCO 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.9 | 100.6 | BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 514809 [JOHNCO 345.00] TO BUS 515136 [SUNNYSD7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 514943 [HSL 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.5 | 100.3 | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 2 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.6 | 101.7 | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.1 | 100 | BUS 338010 [3PRICE 115.00] TO BUS 338011 [3GRIFTH 115.00] CKT 1 | Searcy Price - Brinkley East | 148 | 152.2 | 100.1 | 18.8
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.3 | 102 | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.7 | 101.6 | 127.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.1 | 101.3 | BUS 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.7 | 101.6 | 127.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 102.1 | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 154.7 | 101.6 | 127.7
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.8 | 100.5 | BUS 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 148 | 157.2 | 103.4 | 93.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.4 | 100.9 | BUS 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 148 | 157.2 | 103.4 | 93.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.6 | 101.1 | BUS 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 156.4 | 102.9 | 79.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 154.1 | 101.4 | BUS 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 148 | 156.4 | 102.9 | 79.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.8 | 101.1 | BUS 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 156.4 | 102.9 | 79.2
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 163.5 | 107.6 | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.3 | 106.2 | 24.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 161.5 | 106.3 | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.3 | 106.2 | 24.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 160.9 | 105.9 | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.3 | 106.2 | 24.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 160.5 | 105.6 | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.3 | 106.2 | 24.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 162.3 | 106.9 | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.3 | 106.2 | 24.5
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.4 | 102.8 | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 148 | 164.9 | 108.8 | 0
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 152.2 | 100.1 | BUS 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69.000] CKT 1 | Vienna - Ruston | 148 | 152.2 | 100.1 | 42.9
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166.6 | 109.8 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 166.2 | 109.5 | 9.6
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 166 | 109.3 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 166.2 | 109.5 | 9.6
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 165.6 | 109.1 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 166.2 | 109.5 | 9.6
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 151.9 | 101.4 | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | * | 132.3
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153 | 100.2 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | * | 140.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 153.3 | 100.4 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | * | 140.8
10W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 155.4 | 101.8 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 186.1
14W | 338130 5CALCR | 161 | 338131*5MELBRN | 161 | 1 | 148 | 156.1 | 102.8 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 205.6
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 153.7 | 101 | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 161.6 | 107.1 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.4 | 102.4 | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 156.5 | 102.8 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 156 | 102.4 | 26.8
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 154.5 | 101.5 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 156 | 102.4 | 26.8
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.1 | 101.9 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 156 | 102.4 | 26.8
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.8 | 102.4 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 156 | 102.4 | 26.8
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 163.2 | 107.4 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 164.1 | 108.1 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 152.2 | 100 | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.8 | 102.6 | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 153.6 | 101.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 153.2 | 100.9 | 9.1
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 153 | 100.8 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 153.2 | 100.9 | 9.1
10W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 152.7 | 100.6 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 153.2 | 100.9 | 9.1
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 158.2 | 104.4 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.5 | 103.8 | 27.8
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 156.1 | 102.9 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.5 | 103.8 | 27.8
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 156.8 | 103.4 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.5 | 103.8 | 27.8
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 157.6 | 103.9 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.5 | 103.8 | 27.8
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 161.9 | 106.8 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 153.3 | 101 | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 152 | 100.2 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 154.2 | 101.7 | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.8 | 102.9 | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.8 | 102.6 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.4 | 102.4 | 9.6
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 155.1 | 102.2 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.4 | 102.4 | 9.6
14W | 338130*5CALCR | 161 | 505448 NORFORK5 | 161 | 1 | 148 | 154.8 | 102 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.4 | 102.4 | 9.6
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 161.1 | 105.6 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 160.4 | 105.1 | 35.1
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 158.6 | 103.9 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 160.4 | 105.1 | 35.1
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 159.5 | 104.5 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 160.4 | 105.1 | 35.1
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 160.5 | 105.2 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 160.4 | 105.1 | 35.1
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 166.3 | 109 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 164.4 | 108.2 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 155.7 | 102 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 158.6 | 104 | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 156.6 | 102.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.8 | 101.7 | 14
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 155.7 | 101.7 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.8 | 101.7 | 14
18S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 155.1 | 101.3 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 155.8 | 101.7 | 14
10S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 156 | 100.8 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
14S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 157.9 | 102.7 | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 157.4 | 101.7 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 155.3 | 100.7 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 154.5 | 100.1 | 34
14S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 154.6 | 100.2 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 154.5 | 100.1 | 34
14S | 338131 5MELBRN | 161 | 338132*5SAGE * | 161 | 1 | 148 | 159.1 | 103.1 | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338169*5TRUMAN | 161 | 338707 5TRUM-W# | 161 | 1 | 148 | 169.3 | 119.3 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 161.6 | 113.1 | 35.1
18S | 338169*5TRUMAN | 161 | 338707 5TRUM-W# | 161 | 1 | 148 | 161.2 | 112.8 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 161.6 | 113.1 | 35.1
18S | 338169*5TRUMAN | 161 | 338707 5TRUM-W# | 161 | 1 | 148 | 164.1 | 115 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 161.6 | 113.1 | 35.1
18S | 338169*5TRUMAN | 161 | 338707 5TRUM-W# | 161 | 1 | 148 | 167.3 | 117.6 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 161.6 | 113.1 | 35.1
18S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 156.9 | 106.2 | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 151.3 | 102 | 35.1
18S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 151.6 | 102.3 | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 151.3 | 102 | 35.1
18S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 153.5 | 103.6 | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 151.3 | 102 | 35.1
18S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 155.7 | 105.2 | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 151.3 | 102 | 35.1
18S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 174.6 | 117.9 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14S | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 167.4 | 112.5 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338186*5MONETE | 161 | 338204 5PARAG | 161 | 1 | 148 | 162.8 | 108.4 | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338422*5CONW-W | 161 | 338424 5TYLER | 161 | 1 | 223 | 225.8 | 105.8 | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338422*5CONW-W | 161 | 338424 5TYLER | 161 | 1 | 223 | 225.8 | 105.8 | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 223 | 225.8 | 105.8 | 27
18S | 338422*5CONW-W | 161 | 338424 5TYLER | 161 | 1 | 223 | 241.4 | 113.9 | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 223 | 225.8 | 105.8 | 27
18S | 338483 3NLR-DX | 115 | 338487*3LAKEWD | 115 | 1 | 159 | 161.9 | 104.8 | BUS 337930 [3MAYFL 115.00] TO BUS 337931 [3MORGAN 115.00] CKT 1 | Mayflower - N.L.R. Levy | * | * | * | 167
18S | 338682 5OSAGE # | 161 | 506932*EUREKA 5 | 161 | 1 | 223 | 246.6 | 112.6 | BUS 338102 [5HARR-W 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
18S | 338682 5OSAGE # | 161 | 506932*EUREKA 5 | 161 | 1 | 223 | 265.4 | 122.1 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 259.9
10S | 338682 5OSAGE # | 161 | 506932*EUREKA 5 | 161 | 1 | 223 | 223.9 | 100.2 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 217.5
14S | 338682 5OSAGE # | 161 | 506932*EUREKA 5 | 161 | 1 | 223 | 227.2 | 102.3 | BUS 338102 [5HARR-W 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 238.1
14S | 338682 5OSAGE # | 161 | 506932*EUREKA 5 | 161 | 1 | 223 | 243.9 | 110.6 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | * | 238.1
18S | 338813*5MIDWAY# | 161 | 505460 BULL SH5 | 161 | 1 | 162 | 163.9 | 103 | BUS 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | * | 156.8
18S | 338814*5SOLAND# | 161 | 505448 NORFORK5 | 161 | 1 | 162 | 165.3 | 106 | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | * | 156.8

## Base Voltage
Contingency Scan - Voltages
Approved 2009-2011 Construction Plan Projects Included
Model | Monitored Bus |  |  | Vcont | Bus to Bus Con | Brk to Brk Con | Vcont | C-Load
10S | 334020 | 4BRYAN | 138 | 1.0545 | BUS 334022 [4SPEEDWY 138.00] TO BUS 334023 [4NAVSOTA 138.00] CKT 1 | Same | NA | NA
10S | 334020 | 4BRYAN | 138 | 1.0538 | BUS 334021 [4COLSTTA 138.00] TO BUS 334022 [4SPEEDWY 138.00] CKT 1 | Bryan - Grimes | 1.0702 | 0
14S | 334111 | 4NEWCANY | 138 | 0.91145 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334111 | 4NEWCANY | 138 | 0.85595 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334112 | 4HICKORY | 138 | 0.87188 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334113 | 4EASTGAT | 138 | 0.88851 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334114 | 4HUFFMAN | 138 | 0.88471 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334115 | 6L533TP8 | 138 | 0.91212 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334116 | 4KLMP-EX | 138 | 0.91209 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334209 | 4ROLKERD | 138 | 0.91525 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334210 | 4ADAYTON | 138 | 0.91617 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334211 | 4BDAYTON | 138 | 0.91621 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334216 | 4GORDON | 138 | 0.91502 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
14W | 334283 | 4MILLCR | 138 | 0.90724 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
18S | 334283 | 4MILLCR | 138 | 0.91803 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334284 | 4PINELND | 138 | 0.91042 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334285 | 4BROADUS | 138 | 0.9117 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334286 | 4ETOIL | 138 | 0.91213 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334300 | 4PEACH | 138 | 0.91577 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
18S | 334437 | 6KOLBS | 230 | 0.91863 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
18S | 334438 | 6HANKS | 230 | 0.9184 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
18S | 334439 | 6VFWPK | 230 | 0.91775 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
10S | 335137 | 2PPC NO | 69 | 0.89986 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
10W | 335137 | 2PPC NO | 69 | 0.87554 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
14S | 335137 | 2PPC NO | 69 | 0.88753 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
14W | 335137 | 2PPC NO | 69 | 0.87167 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
18S | 335137 | 2PPC NO | 69 | 0.8921 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
14S | 335254 | 2CARTER | 69 | 0.76504 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.91847 | 6.3
14S | 335254 | 2CARTER | 69 | 0.91793 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.91847 | 6.3
18S | 335254 | 2CARTER | 69 | 0.69569 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.8876 | 6.3
18S | 335254 | 2CARTER | 69 | 0.88984 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.8876 | 6.3
14S | 335255 | 2SERPENT | 69 | 0.80761 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.91222 | 6.3
14S | 335255 | 2SERPENT | 69 | 0.9117 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.91222 | 6.3
18S | 335255 | 2SERPENT | 69 | 0.74798 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.88361 | 6.3
18S | 335255 | 2SERPENT | 69 | 0.88504 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.88361 | 6.3
14S | 335256 | 2TUPPER | 69 | 0.81189 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.90641 | 6.3
14S | 335256 | 2TUPPER | 69 | 0.90591 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.90641 | 6.3
18S | 335256 | 2TUPPER | 69 | 0.75642 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.87973 | 6.3
18S | 335256 | 2TUPPER | 69 | 0.88118 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.87973 | 6.3
14S | 335257 | 2ELTON | 69 | 0.82009 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.90937 | 6.3
14S | 335257 | 2ELTON | 69 | 0.90888 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.90937 | 6.3
18S | 335257 | 2ELTON | 69 | 0.76705 | BUS 335217 [2CHLOMAL 69.000] TO BUS 335253 [2LACASNE 69.000] CKT 1 | Carter - Chlomal | 0.8839 | 6.3
18S | 335257 | 2ELTON | 69 | 0.8853 | BUS 335253 [2LACASNE 69.000] TO BUS 335254 [2CARTER 69.000] CKT 1 | Carter - Chlomal | 0.8839 | 6.3
10S | 335275 | 2LKARTHR | 69 | 0.91888 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335275 | 2LKARTHR | 69 | 0.90921 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335275 | 2LKARTHR | 69 | 0.9067 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335275 | 2LKARTHR | 69 | 0.86021 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.89783 | 25.5
14S | 335275 | 2LKARTHR | 69 | 0.9115 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335275 | 2LKARTHR | 69 | 0.8786 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335275 | 2LKARTHR | 69 | 0.83043 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.87538 | 27.4
18S | 335275 | 2LKARTHR | 69 | 0.86367 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335275 | 2LKARTHR | 69 | 0.90864 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335275 | 2LKARTHR | 69 | 0.90645 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335275 | 2LKARTHR | 69 | 0.91915 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335276 | 2KLONDKE | 69 | 0.91233 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335276 | 2KLONDKE | 69 | 0.90983 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335276 | 2KLONDKE | 69 | 0.86366 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.90112 | 25.5
14S | 335276 | 2KLONDKE | 69 | 0.91474 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335276 | 2KLONDKE | 69 | 0.88196 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335276 | 2KLONDKE | 69 | 0.83399 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.87874 | 27.4
18S | 335276 | 2KLONDKE | 69 | 0.86708 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335276 | 2KLONDKE | 69 | 0.91188 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335276 | 2KLONDKE | 69 | 0.9097 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335330 | 2L-270TP | 69 | 0.91922 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335330 | 2L-270TP | 69 | 0.87422 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.91122 | 25.5
14S | 335330 | 2L-270TP | 69 | 0.89229 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335330 | 2L-270TP | 69 | 0.84535 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.88949 | 27.4
18S | 335330 | 2L-270TP | 69 | 0.87798 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335331 | 2GUEYDAN | 69 | 0.91854 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335331 | 2GUEYDAN | 69 | 0.87348 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.91051 | 25.5
14S | 335331 | 2GUEYDAN | 69 | 0.89157 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335331 | 2GUEYDAN | 69 | 0.84458 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.88876 | 27.4
18S | 335331 | 2GUEYDAN | 69 | 0.87724 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335331 | 2GUEYDAN | 69 | 0.91935 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335332 | 2MORSE | 69 | 0.91787 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335332 | 2MORSE | 69 | 0.87277 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.90983 | 25.5
14S | 335332 | 2MORSE | 69 | 0.89087 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335332 | 2MORSE | 69 | 0.84388 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.88809 | 27.4
18S | 335332 | 2MORSE | 69 | 0.87656 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335332 | 2MORSE | 69 | 0.9187 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335333 | 2CAMPBEL | 69 | 0.87539 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.91233 | 25.5
14S | 335333 | 2CAMPBEL | 69 | 0.89344 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335333 | 2CAMPBEL | 69 | 0.84659 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.89066 | 27.4
18S | 335333 | 2CAMPBEL | 69 | 0.87917 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335334 | 2L610TP | 69 | 0.91313 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335335 | 2DUHON | 69 | 0.91924 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335335 | 2DUHON | 69 | 0.87551 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.91762 | 27.4
18S | 335335 | 2DUHON | 69 | 0.90661 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335336 | 2HUNTER | 69 | 0.91642 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335375 | 4COLACDY | 138 | 0.89871 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14W | 335375 | 4COLACDY | 138 | 0.9153 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335375 | 4COLACDY | 138 | 0.90544 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14S | 335376 | 4ACADGSU | 138 | 0.90045 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14W | 335376 | 4ACADGSU | 138 | 0.917 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335376 | 4ACADGSU | 138 | 0.90717 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14S | 335377 | 4SCANLN | 138 | 0.89959 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14W | 335377 | 4SCANLN | 138 | 0.91603 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335377 | 4SCANLN | 138 | 0.90631 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
10S | 335378 | 4SCOTT2 | 138 | 0.91258 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335378 | 4SCOTT2 | 138 | 0.911 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 0.913 | 44
14S | 335378 | 4SCOTT2 | 138 | 0.87521 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 0.913 | 44
14S | 335378 | 4SCOTT2 | 138 | 0.91344 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 0.913 | 44
14S | 335378 | 4SCOTT2 | 138 | 0.90026 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14S | 335378 | 4SCOTT2 | 138 | 0.91622 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335378 | 4SCOTT2 | 138 | 0.91779 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14W | 335378 | 4SCOTT2 | 138 | 0.91923 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335378 | 4SCOTT2 | 138 | 0.90766 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335378 | 4SCOTT2 | 138 | 0.90853 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335378 | 4SCOTT2 | 138 | 0.91597 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335379 | 4SCOTT1 | 138 | 0.89861 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335379 | 4SCOTT1 | 138 | 0.88575 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335379 | 4SCOTT1 | 138 | 0.90189 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.90488 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.91829 | 25.5
14S | 335379 | 4SCOTT1 | 138 | 0.91831 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.91037 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.91193 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.89907 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.9094 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.88978 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335379 | 4SCOTT1 | 138 | 0.89924 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335379 | 4SCOTT1 | 138 | 0.90508 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14W | 335379 | 4SCOTT1 | 138 | 0.90091 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335379 | 4SCOTT1 | 138 | 0.90734 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335379 | 4SCOTT1 | 138 | 0.88921 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335379 | 4SCOTT1 | 138 | 0.89786 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.90926 | BUS 335380 [4MEAUX 138.00] TO BUS 335386 [4ABBVIL 138.00] CKT 1 | Meaux - Leblanc | 0.90824 | 30.9
10S | 335380 | 4MEAUX | 138 | 0.8668 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.86215 | 22.6
10S | 335380 | 4MEAUX | 138 | 0.91764 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.91637 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.89007 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.91755 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.87624 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.89337 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335380 | 4MEAUX | 138 | 0.89729 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.90428 | 9.4
10W | 335380 | 4MEAUX | 138 | 0.91667 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10W | 335380 | 4MEAUX | 138 | 0.90284 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Same | NA | NA
14W | 335380 | 4MEAUX | 138 | 0.86237 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.87312 | 10.8
14W | 335380 | 4MEAUX | 138 | 0.87821 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14W | 335380 | 4MEAUX | 138 | 0.91884 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14W | 335380 | 4MEAUX | 138 | 0.90916 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14W | 335380 | 4MEAUX | 138 | 0.90458 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335380 | 4MEAUX | 138 | 0.90978 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.79591 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.83732 | 27.4
18S | 335380 | 4MEAUX | 138 | 0.83896 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.8765 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.915 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.91385 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.91895 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.91283 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.87558 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.88534 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.88595 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335380 | 4MEAUX | 138 | 0.88008 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335380 | 4MEAUX | 138 | 0.91358 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.8778 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91865 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 0.91946 | 38.6
10S | 335385 | 4LEROY | 138 | 0.91562 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 0.91946 | 38.6
10S | 335385 | 4LEROY | 138 | 0.91993 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 0.91946 | 38.6
10S | 335385 | 4LEROY | 138 | 0.91909 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 0.91992 | 15.2
10S | 335385 | 4LEROY | 138 | 0.91992 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 0.91992 | 15.2
10S | 335385 | 4LEROY | 138 | 0.90132 | BUS 335380 [4MEAUX 138.00] TO BUS 335386 [4ABBVIL 138.00] CKT 1 | Meaux - Leblanc | 0.9003 | 30.9
10S | 335385 | 4LEROY | 138 | 0.9173 | BUS 335386 [4ABBVIL 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Meaux - Leblanc | 0.9003 | 30.9
10S | 335385 | 4LEROY | 138 | 0.91848 | BUS 335388 [4MORIL 138.00] TO BUS 335389 [4DUBOIN 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91958 | 27.9
10S | 335385 | 4LEROY | 138 | 0.91413 | BUS 335389 [4DUBOIN 138.00] TO BUS 335390 [4BUWHSE 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91958 | 27.9
10S | 335385 | 4LEROY | 138 | 0.85845 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.85376 | 22.6
10S | 335385 | 4LEROY | 138 | 0.91851 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91716 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91556 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91377 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.90978 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91801 | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91797 | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91428 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.9085 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91981 | BUS 500880 [VILPLT 6 230.00] TO BUS 500920 [WSTFORK6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.88195 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.9194 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91742 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.90969 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.86799 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.88528 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91379 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 0.91379 | 5.7
10S | 335385 | 4LEROY | 138 | 0.91883 | BUS 336032 [3HUMPHY 115.00] TO BUS 303202 [3GRENWD 115.00] CKT 1 | Terrebonne - Humphrey | 0.91911 | 34
10S | 335385 | 4LEROY | 138 | 0.91424 | BUS 336033 [3TEREBN 115.00] TO BUS 303202 [3GRENWD 115.00] CKT 1 | Terrebonne - Humphrey | 0.91911 | 34
10W | 335385 | 4LEROY | 138 | 0.88747 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.89455 | 9.4
10W | 335385 | 4LEROY | 138 | 0.90707 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10W | 335385 | 4LEROY | 138 | 0.89308 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Same | NA | NA
14W | 335385 | 4LEROY | 138 | 0.85042 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.86133 | 10.8
14W | 335385 | 4LEROY | 138 | 0.8665 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14W | 335385 | 4LEROY | 138 | 0.90768 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14W | 335385 | 4LEROY | 138 | 0.89787 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14W | 335385 | 4LEROY | 138 | 0.89323 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335385 | 4LEROY | 138 | 0.8985 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90996 | BUS 335379 [4SCOTT1 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91837 | BUS 336137 [6SLIDEL 230.00] TO BUS 500800 [SSLID 6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91898 | BUS 500060 [BVISTA 4 138.00] TO BUS 500100 [BERWKTP4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91887 | BUS 500100 [BERWKTP4 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91694 | BUS 500920 [WSTFORK6 230.00] TO BUS 500940 [WELLS 6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91842 | BUS 502413 [ELKS 2 69.000] TO BUS 502422 [HARGIS 69.000] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91436 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 0.9178 | 49
18S | 335385 | 4LEROY | 138 | 0.90904 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 0.9178 | 49
18S | 335385 | 4LEROY | 138 | 0.91823 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 0.9178 | 49
18S | 335385 | 4LEROY | 138 | 0.91418 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 0.91683 | 16.1
18S | 335385 | 4LEROY | 138 | 0.91682 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 0.91683 | 16.1
18S | 335385 | 4LEROY | 138 | 0.91956 | BUS 335380 [4MEAUX 138.00] TO BUS 335386 [4ABBVIL 138.00] CKT 1 | Meaux - Leblanc | 0.91908 | 35.7
18S | 335385 | 4LEROY | 138 | 0.91774 | BUS 335388 [4MORIL 138.00] TO BUS 335389 [4DUBOIN 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91899 | 32.2
18S | 335385 | 4LEROY | 138 | 0.91246 | BUS 335389 [4DUBOIN 138.00] TO BUS 335390 [4BUWHSE 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91899 | 32.2
18S | 335385 | 4LEROY | 138 | 0.78375 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.8258 | 27.4
18S | 335385 | 4LEROY | 138 | 0.9175 | BUS 335192 [8NELSON 500.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91842 | BUS 335366 [4RICHARD 138.00] TO BUS 335367 [8RICHARD 500.00] CKT 2 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91116 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91866 | BUS 335366 [4RICHARD 138.00] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91413 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91669 | BUS 335404 [2LEBLANC 69.000] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91682 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.82747 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.86553 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91772 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91384 | BUS 335455 [4CHAMPNE 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91107 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90452 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91301 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91466 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90336 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91602 | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91596 | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90852 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90232 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91288 | BUS 500880 [VILPLT 6 230.00] TO BUS 500920 [WSTFORK6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.86461 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91501 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91105 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91264 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.87449 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.91201 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 0.91201 | 5.9
10S | 335385 | 4LEROY | 138 | 0.91492 | BUS 335368 [8WELLS 500.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91992 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91302 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.87186 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91848 | BUS 335192 [8NELSON 500.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91753 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91982 | BUS 335366 [4RICHARD 138.00] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA
10S | 335385 | 4LEROY | 138 | 0.91932 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.9182 | BUS 335368 [8WELLS 500.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA
18S | 335385 | 4LEROY | 138 | 0.90309 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335386 | 4ABBVIL | 138 | 0.88573 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335386 | 4ABBVIL | 138 | 0.89614 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335386 | 4ABBVIL | 138 | 0.84916 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.84843 | 22.6
10S | 335386 | 4ABBVIL | 138 | 0.9016 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335386 | 4ABBVIL | 138 | 0.88784 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335386 | 4ABBVIL | 138 | 0.90478 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335386 | 4ABBVIL | 138 | 0.88352 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.89235 | 9.4
10W | 335386 | 4ABBVIL | 138 | 0.89085 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91792 | BUS 502413 [ELKS 2 69.000] TO BUS 502422 [HARGIS 69.000] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91279 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 0.91594 | 44
14S | 335386 | 4ABBVIL | 138 | 0.90787 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 0.91594 | 44
14S | 335386 | 4ABBVIL | 138 | 0.9164 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 0.91594 | 44
14S | 335386 | 4ABBVIL | 138 | 0.91893 | BUS 335366 [4RICHARD 138.00] TO BUS 500400 [HABETZ 4 138.00] CKT 1 | Flanders - Richard | 0.91983 | 46.9
14S | 335386 | 4ABBVIL | 138 | 0.91762 | BUS 336031 [3GIBSON 115.00] TO BUS 336032 [3HUMPHY 115.00] CKT 1 | Humphrey - Ramos | 0.9186 | 16.3
14S | 335386 | 4ABBVIL | 138 | 0.91861 | BUS 336030 [4GIBSON 138.00] TO BUS 500740 [RAMOS 4 138.00] CKT 1 | Humphrey - Ramos | 0.9186 | 16.3
14S | 335386 | 4ABBVIL | 138 | 0.91537 | BUS 335388 [4MORIL 138.00] TO BUS 335389 [4DUBOIN 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91589 | 30.3
14S | 335386 | 4ABBVIL | 138 | 0.91084 | BUS 335389 [4DUBOIN 138.00] TO BUS 335390 [4BUWHSE 138.00] CKT 1 | Moril - Bayou Warehouse | 0.91589 | 30.3
14S | 335386 | 4ABBVIL | 138 | 0.79171 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.83257 | 25.5
14S | 335386 | 4ABBVIL | 138 | 0.9155 | BUS 335192 [8NELSON 500.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91795 | BUS 335366 [4RICHARD 138.00] TO BUS 335367 [8RICHARD 500.00] CKT 2 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91061 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91523 | BUS 335366 [4RICHARD 138.00] TO BUS 335379 [4SCOTT1 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90647 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91961 | BUS 335404 [2LEBLANC 69.000] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91855 | BUS 336030 [4GIBSON 138.00] TO BUS 336031 [3GIBSON 115.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91496 | BUS 335368 [8WELLS 500.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.88643 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91949 | BUS 335379 [4SCOTT1 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90628 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.8567 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.9149 | BUS 335455 [4CHAMPNE 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91419 | BUS 335455 [4CHAMPNE 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.9184 | BUS 336137 [6SLIDEL 230.00] TO BUS 500800 [SSLID 6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91591 | BUS 303133 [4VATCAN 138.00] TO BUS 303134 [4EOPLOUS 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91008 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90461 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.9186 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90822 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90259 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91404 | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91396 | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90798 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90106 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91174 | BUS 500880 [VILPLT 6 230.00] TO BUS 500920 [WSTFORK6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91641 | BUS 500920 [WSTFORK6 230.00] TO BUS 500940 [WELLS 6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.9199 | BUS 500940 [WELLS 6 230.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90451 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91495 | BUS 502401 [FLANDER6 230.00] TO BUS 502402 [ACADIAN6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91225 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90512 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.89486 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.90161 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335386 | 4ABBVIL | 138 | 0.91019 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 0.9102 | 5.8
14W | 335386 | 4ABBVIL | 138 | 0.84297 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.85627 | 10.8
14W | 335386 | 4ABBVIL | 138 | 0.89237 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14W | 335386 | 4ABBVIL | 138 | 0.9161 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14W | 335386 | 4ABBVIL | 138 | 0.91821 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14W | 335386 | 4ABBVIL | 138 | 0.91383 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335386 | 4ABBVIL | 138 | 0.91928 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.76453 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.81506 | 27.4
18S | 335386 | 4ABBVIL | 138 | 0.85275 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.87141 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.91465 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.91341 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.88377 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.89349 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335386 | 4ABBVIL | 138 | 0.91798 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335387 | 4DELCAMB | 138 | 0.88394 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335387 | 4DELCAMB | 138 | 0.91538 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335387 | 4DELCAMB | 138 | 0.9141 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335387 | 4DELCAMB | 138 | 0.90074 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335387 | 4DELCAMB | 138 | 0.91706 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91636 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.90296 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91762 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.85475 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91646 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91529 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.90894 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91516 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.90718 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91411 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91771 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.90495 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91099 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335387 | 4DELCAMB | 138 | 0.91755 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 0.91755 | 5.8
14W | 335387 | 4DELCAMB | 138 | 0.90977 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14W | 335387 | 4DELCAMB | 138 | 0.9107 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.87328 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.86594 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.91529 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.9138 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.89443 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335387 | 4DELCAMB | 138 | 0.90385 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335388 | 4MORIL | 138 | 0.89873 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335388 | 4MORIL | 138 | 0.87288 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335388 | 4MORIL | 138 | 0.91758 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335388 | 4MORIL | 138 | 0.88315 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335389 | 4DUBOIN | 138 | 0.91605 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335389 | 4DUBOIN | 138 | 0.8914 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335389 | 4DUBOIN | 138 | 0.9 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335391 | 4CECELIA | 138 | 0.89877 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335391 | 4CECELIA | 138 | 0.89634 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335391 | 4CECELIA | 138 | 0.88332 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335391 | 4CECELIA | 138 | 0.8994 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335391 | 4CECELIA | 138 | 0.91652 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10W | 335391 | 4CECELIA | 138 | 0.91779 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335391 | 4CECELIA | 138 | 0.91851 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91062 | BUS 335375 [4COLACDY 138.00] TO BUS 335376 [4ACADGSU 138.00] CKT 1 | Colonial Academy - Scott | 0.91342 | 44
14S | 335391 | 4CECELIA | 138 | 0.89707 | BUS 335376 [4ACADGSU 138.00] TO BUS 335377 [4SCANLN 138.00] CKT 1 | Colonial Academy - Scott | 0.91342 | 44
14S | 335391 | 4CECELIA | 138 | 0.91386 | BUS 335377 [4SCANLN 138.00] TO BUS 335378 [4SCOTT2 138.00] CKT 1 | Colonial Academy - Scott | 0.91342 | 44
14S | 335391 | 4CECELIA | 138 | 0.91947 | BUS 335192 [8NELSON 500.00] TO BUS 335367 [8RICHARD 500.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.90603 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91504 | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91122 | BUS 335388 [4MORIL 138.00] TO BUS 335391 [4CECELIA 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91967 | BUS 335368 [8WELLS 500.00] TO BUS 500950 [WELSRCT6 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91373 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91921 | BUS 335380 [4MEAUX 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.8797 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91466 | BUS 500190 [COCODR 6 230.00] TO BUS 500880 [VILPLT 6 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91153 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91796 | BUS 500330 [FLANDR 4 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91706 | BUS 500410 [HOPKINS4 138.00] TO BUS 500580 [MORBHAN4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91262 | BUS 500410 [HOPKINS4 138.00] TO BUS 500660 [PATOUT 4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91667 | BUS 500580 [MORBHAN4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91149 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91615 | BUS 500880 [VILPLT 6 230.00] TO BUS 500920 [WSTFORK6 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.89677 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91704 | BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.90784 | BUS 502403 [BONIN 6 230.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.88774 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.89532 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335391 | 4CECELIA | 138 | 0.91846 | BUS 335390 [4BUWHSE 138.00] TO BUS 500440 [IVANHOE4 138.00] CKT 1 | Teche - Bayou Warehouse | 0.91846 | 5.8
14W | 335391 | 4CECELIA | 138 | 0.91885 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
14W | 335391 | 4CECELIA | 138 | 0.91519 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
14W | 335391 | 4CECELIA | 138 | 0.90001 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14W | 335391 | 4CECELIA | 138 | 0.89623 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14W | 335391 | 4CECELIA | 138 | 0.90239 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.91558 | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.90417 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.89077 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.91618 | BUS 335391 [4CECELIA 138.00] TO BUS 502404 [BONIN 4 138.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.91959 | BUS 500660 [PATOUT 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.88381 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
18S | 335391 | 4CECELIA | 138 | 0.89266 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335428 | 2L625OP | 69 | 0.91092 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
10S | 335428 | 2L625OP | 69 | 0.91872 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335428 | 2L625OP | 69 | 0.89915 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
14S | 335428 | 2L625OP | 69 | 0.89687 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335428 | 2L625OP | 69 | 0.9181 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
18S | 335428 | 2L625OP | 69 | 0.89784 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
18S | 335428 | 2L625OP | 69 | 0.91529 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335429 | 2STMARTN | 69 | 0.91793 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335429 | 2STMARTN | 69 | 0.90555 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
10S | 335429 | 2STMARTN | 69 | 0.91339 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335429 | 2STMARTN | 69 | 0.91475 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
14S | 335429 | 2STMARTN | 69 | 0.89367 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
14S | 335429 | 2STMARTN | 69 | 0.89138 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335429 | 2STMARTN | 69 | 0.91279 | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA
18S | 335429 | 2STMARTN | 69 | 0.8924 | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA
18S | 335429 | 2STMARTN | 69 | 0.90996 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
18S | 335429 | 2STMARTN | 69 | 0.91527 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335455 | 4CHAMPNE | 138 | 0.9158 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
10S | 335455 | 4CHAMPNE | 138 | 0.91698 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
14S | 335455 | 4CHAMPNE | 138 | 0.91407 | BUS 335455 [4CHAMPNE 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335455 | 4CHAMPNE | 138 | 0.88929 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335455 | 4CHAMPNE | 138 | 0.89514 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335455 | 4CHAMPNE | 138 | 0.91881 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
14S | 335456 | 4L-642TP | 138 | 0.90274 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335456 | 4L-642TP | 138 | 0.90406 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
14S | 335457 | 4COLSPRG | 138 | 0.90269 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335457 | 4COLSPRG | 138 | 0.90401 | BUS 500230 [COUGH 4 138.00] TO BUS 500720 [PLAISAN4 138.00] CKT 1 | Same | NA | NA
18S | 335788 | 2BRADYH | 69 | 0.87538 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
18S | 335788 | 2BRADYH | 69 | 0.89184 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
18S | 335788 | 2BRADYH | 69 | 0.91009 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
18S | 335789 | 2CLINTON | 69 | 0.87456 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.9104 | 3
18S | 335789 | 2CLINTON | 69 | 0.89103 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.9104 | 3
18S | 335789 | 2CLINTON | 69 | 0.9093 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.9104 | 3
18S | 335790 | 2CLNTREA | 69 | 0.87538 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
18S | 335790 | 2CLNTREA | 69 | 0.89184 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
18S | 335790 | 2CLNTREA | 69 | 0.91009 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.91119 | 3
10S | 336085 | 3ALLIA | 115 | 0.46393 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10S | 336092 | 3CARLSL | 115 | 0.80506 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10S | 336092 | 3CARLSL | 115 | 0.87102 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
14S | 336092 | 3CARLSL | 115 | 0.84242 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
14W | 336092 | 3CARLSL | 115 | 0.86616 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
18S | 336092 | 3CARLSL | 115 | 0.83556 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
10W | 336092 | 3CARLSL | 115 | 0.87402 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
18S | 336230 | 3CLAYTN | 115 | 0.91282 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
18S | 336231 | 3NORCO | 115 | 0.91534 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
18S | 336770 | 3WESSON | 115 | 0.90627 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.9064 | 10
18S | 336770 | 3WESSON | 115 | 0.87274 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.9064 | 10
14S | 336771 | 3JAM RD* | 115 | 0.90191 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.90202 | 9.5
14S | 336771 | 3JAM RD* | 115 | 0.8675 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.90202 | 9.5
18S | 336771 | 3JAM RD* | 115 | 0.88486 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.88501 | 10
18S | 336771 | 3JAM RD* | 115 | 0.84311 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.88501 | 10
14S | 336772 | 3HZLHST | 115 | 0.89433 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.89443 | 9.5
14S | 336772 | 3HZLHST | 115 | 0.85689 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.89443 | 9.5
18S | 336772 | 3HZLHST | 115 | 0.87611 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.87625 | 10
18S | 336772 | 3HZLHST | 115 | 0.83059 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.87625 | 10
14S | 336773 | 3COPHSW* | 115 | 0.89215 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.89226 | 9.5
14S | 336773 | 3COPHSW* | 115 | 0.854 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.89226 | 9.5
18S | 336773 | 3COPHSW* | 115 | 0.87367 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.87382 | 10
18S | 336773 | 3COPHSW* | 115 | 0.82726 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.87382 | 10
10S | 336774 | 3GALLMAN | 115 | 0.91803 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.91814 | 8.8
10S | 336774 | 3GALLMAN | 115 | 0.88821 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.91814 | 8.8
14S | 336774 | 3GALLMAN | 115 | 0.88345 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.88356 | 9.5
14S | 336774 | 3GALLMAN | 115 | 0.84172 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.88356 | 9.5
18S | 336774 | 3GALLMAN | 115 | 0.86378 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.86394 | 10
18S | 336774 | 3GALLMAN | 115 | 0.81296 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.86394 | 10
10S | 336775 | 3CRYSPG | 115 | 0.91203 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.91214 | 8.8
10S | 336775 | 3CRYSPG | 115 | 0.87908 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.91214 | 8.8
14S | 336775 | 3CRYSPG | 115 | 0.87509 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.87521 | 9.5
14S | 336775 | 3CRYSPG | 115 | 0.82905 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.87521 | 9.5
18S | 336775 | 3CRYSPG | 115 | 0.85402 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.85418 | 10
18S | 336775 | 3CRYSPG | 115 | 0.7979 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.85418 | 10
10S | 336776 | 3TERRY | 115 | 0.89623 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.89634 | 8.8
10S | 336776 | 3TERRY | 115 | 0.85743 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.89634 | 8.8
14S | 336776 | 3TERRY | 115 | 0.85534 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.85547 | 9.5
14S | 336776 | 3TERRY | 115 | 0.80144 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.85547 | 9.5
18S | 336776 | 3TERRY | 115 | 0.832 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.83217 | 10
18S | 336776 | 3TERRY | 115 | 0.76633 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.83217 | 10
10S | 336777 | 3BYRAM | 115 | 0.89141 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.89152 | 8.8
10S | 336777 | 3BYRAM | 115 | 0.84972 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.89152 | 8.8
14S | 336777 | 3BYRAM | 115 | 0.84872 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.84885 | 9.5
14S | 336777 | 3BYRAM | 115 | 0.79105 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.84885 | 9.5
18S | 336777 | 3BYRAM | 115 | 0.82441 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.82459 | 10
18S | 336777 | 3BYRAM | 115 | 0.75426 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.82459 | 10
10W | 337010 | 8WOLFCRK | 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
10S | 337010 | 8WOLFCRK | 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
14S | 337010 | 8WOLFCRK | 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
14W | 337010 | 8WOLFCRK | 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
18S | 337010 | 8WOLFCRK | 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
18S | 337054 | 3GRNWOD | 115 | 0.91236 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337055 | 3BROWN* | 115 | 0.90565 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337056 | 3CRLTN* | 115 | 0.91181 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337056 | 3CRLTN* | 115 | 0.89174 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337057 | 3CARLTN | 115 | 0.9115 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337057 | 3CARLTN | 115 | 0.89141 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337060 | 3WINONA | 115 | 0.90991 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337060 | 3WINONA | 115 | 0.88718 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337061 | 3SAWYR* | 115 | 0.91555 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337061 | 3SAWYR* | 115 | 0.89229 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337061 | 3SAWYR* | 115 | 0.8668 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337062 | 3ELLIOT | 115 | 0.88977 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337062 | 3ELLIOT | 115 | 0.86143 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337062 | 3ELLIOT | 115 | 0.83064 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337063 | 3S GREN | 115 | 0.88615 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337063 | 3S GREN | 115 | 0.85623 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337063 | 3S GREN | 115 | 0.82382 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337064 | 3GRNADA | 115 | 0.88026 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337064 | 3GRNADA | 115 | 0.84914 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337064 | 3GRNADA | 115 | 0.81548 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337065 | 3TILTOB | 115 | 0.87226 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337065 | 3TILTOB | 115 | 0.84035 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337065 | 3TILTOB | 115 | 0.8059 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337066 | 3TVA-SHE | 115 | 0.87137 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337066 | 3TVA-SHE | 115 | 0.83942 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337066 | 3TVA-SHE | 115 | 0.80492 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337067 | 3CHRSTN | 115 | 0.86159 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337067 | 3CHRSTN | 115 | 0.82858 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
18S | 337067 | 3CHRSTN | 115 | 0.79305 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337084 | DELTA U2 | 69 | 1.0513 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.059 | 28.2
10S | 337084 | DELTA U2 | 69 | 1.0573 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.059 | 28.2
10S | 337084 | DELTA U2 | 69 | 1.0556 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.059 | 28.2
14S | 337084 | DELTA U2 | 69 | 1.0545 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0621 | 29.9
14S | 337084 | DELTA U2 | 69 | 1.0601 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.0621 | 29.9
14S | 337084 | DELTA U2 | 69 | 1.0586 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0621 | 29.9
18S | 337084 | DELTA U2 | 69 | 1.0517 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0595 | 31
18S | 337084 | DELTA U2 | 69 | 1.0574 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.0595 | 31
18S | 337084 | DELTA U2 | 69 | 1.0559 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0595 | 31
14S | 337136 | 3SNTOBI | 115 | 0.90459 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337136 | 3SNTOBI | 115 | 0.84756 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337136 | 3SNTOBI | 115 | 0.91791 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 129.7
18S | 337136 | 3SNTOBI | 115 | 0.85191 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
14S | 337137 | 3CLDWTR | 115 | 0.88758 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337137 | 3CLDWTR | 115 | 0.81921 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337137 | 3CLDWTR | 115 | 0.90397 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 129.7
18S | 337137 | 3CLDWTR | 115 | 0.82424 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
10S | 337138 | 3HRNADO | 115 | 0.91668 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337138 | 3HRNADO | 115 | 0.87 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337138 | 3HRNADO | 115 | 0.78792 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337138 | 3HRNADO | 115 | 0.89103 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 129.7
18S | 337138 | 3HRNADO | 115 | 0.79393 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
10S | 337139 | 3GETWEL | 115 | 0.91389 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337139 | 3GETWEL | 115 | 0.86804 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337139 | 3GETWEL | 115 | 0.78759 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337140 | 6GETWELL | 230 | 0.91135 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337140 | 6GETWELL | 230 | 0.86715 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337140 | 6GETWELL | 230 | 0.78955 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337141 | 3NESBT* | 115 | 0.91305 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337141 | 3NESBT* | 115 | 0.86672 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337141 | 3NESBT* | 115 | 0.78558 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337142 | 3NESBIT | 115 | 0.91111 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337142 | 3NESBIT | 115 | 0.86415 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337142 | 3NESBIT | 115 | 0.78204 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337143 | 3PLUM PT | 115 | 0.91351 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337143 | 3PLUM PT | 115 | 0.86713 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337143 | 3PLUM PT | 115 | 0.78597 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337144 | 3GRNBRK | 115 | 0.91773 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337144 | 3GRNBRK | 115 | 0.87316 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337144 | 3GRNBRK | 115 | 0.79512 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337144 | 3GRNBRK | 115 | 0.91545 | BUS 337144 [3GRNBRK 115.00] TO BUS 337150 [3HN LAK 115.00] CKT 1 | Horn Lake - Getwell | * | 217
14S | 337150 | 3HN LAK | 115 | 0.88678 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337150 | 3HN LAK | 115 | 0.81543 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337151 | 3DESOTO-MS | 115 | 0.89139 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337151 | 3DESOTO-MS | 115 | 0.82262 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337152 | 3WALLS | 115 | 0.90817 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337152 | 3WALLS | 115 | 0.84759 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337153 | 3BANKSW | 115 | 0.89118 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337180 | 6HN LAK | 230 | 0.91206 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337180 | 6HN LAK | 230 | 0.8696 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337180 | 6HN LAK | 230 | 0.79503 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10W | 337368 | 8MTOLIV | 500 | 1.0666 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
10S | 337368 | 8MTOLIV | 500 | 1.0691 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
14S | 337368 | 8MTOLIV | 500 | 1.0697 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
14W | 337368 | 8MTOLIV | 500 | 1.0717 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
18S | 337368 | 8MTOLIV | 500 | 1.072 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
18S | 337555 | 3T.E. F | 115 | 0.91695 | BUS 337539 [3ELDEHV 115.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
18S | 337800 | 3HASKEL | 115 | 0.919 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
14S | 337801 | 3BENT-S* | 115 | 0.91344 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 150.2
18S | 337801 | 3BENT-S* | 115 | 0.89725 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
10S | 337802 | 3BAUXIT | 115 | 0.90969 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
14S | 337802 | 3BAUXIT | 115 | 0.89479 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 150.2
18S | 337802 | 3BAUXIT | 115 | 0.87556 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
10S | 337803 | 3BRYANT | 115 | 0.90678 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
14S | 337803 | 3BRYANT | 115 | 0.89133 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 150.2
18S | 337803 | 3BRYANT | 115 | 0.8714 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 337939 | 5GOLDCR* | 161 | 0.91848 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 337940 | 5HAMLET* | 161 | 0.91769 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 337941 | 5HAMLT | 161 | 0.91767 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
10S | 337967 | 3RICUS | 115 | 1.0509 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 31.1
10S | 337967 | 3RICUS | 115 | 1.0511 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 31.1
10S | 337967 | 3RICUS | 115 | 1.0523 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 31.1
10S | 337967 | 3RICUS | 115 | 1.0556 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 31.1
10S | 337967 | 3RICUS | 115 | 1.0525 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 31.1
10W | 337967 | 3RICUS | 115 | 1.0515 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | NA | NA
10W | 337967 | 3RICUS | 115 | 1.0511 | BUS 337627 [3PB-IP* 115.00] TO BUS 337628 [3PB-IP 115.00] CKT 1 | Same | NA | NA
10W | 337967 | 3RICUS | 115 | 1.0529 | BUS 337967 [3RICUS 115.00] TO BUS 337972 [3ALMYRA 115.00] CKT 1 | Stuttgart Ricuskey - Gillett | 1.0531 | 29.5
10W | 337967 | 3RICUS | 115 | 1.057 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
10W | 337967 | 3RICUS | 115 | 1.0571 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
10W | 337967 | 3RICUS | 115 | 1.0578 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
10W | 337967 | 3RICUS | 115 | 1.0507 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
10W | 337967 | 3RICUS | 115 | 1.0601 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
10W | 337967 | 3RICUS | 115 | 1.058 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.061 | 22.8
14S | 337967 | 3RICUS | 115 | 1.0527 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0543 | 34.7
14W | 337967 | 3RICUS | 115 | 1.0522 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 25.8
14W | 337967 | 3RICUS | 115 | 1.0523 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 25.8
14W | 337967 | 3RICUS | 115 | 1.0531 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 25.8
14W | 337967 | 3RICUS | 115 | 1.0559 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 25.8
14W | 337967 | 3RICUS | 115 | 1.0533 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.057 | 25.8
10W | 337969 | 3STUTT-I | 115 | 1.0513 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 22.8
10W | 337969 | 3STUTT-I | 115 | 1.0514 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 22.8
10W | 337969 | 3STUTT-I | 115 | 1.0521 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 22.8
10W | 337969 | 3STUTT-I | 115 | 1.0543 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 22.8
10W | 337969 | 3STUTT-I | 115 | 1.0522 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 22.8
10W | 337970 | 3ULM 11 | 115 | 1.0506 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0514 | 22.8
18S | 337981 | 3MARVEL | 115 | 0.9158 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337982 | 3BARTON | 115 | 0.91231 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337983 | 3HELN-W* | 115 | 0.90929 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337984 | 3HELN-C | 115 | 0.90765 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
14S | 338006 | 3CABOT | 115 | 0.90877 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 137.4
18S | 338006 | 3CABOT | 115 | 0.85711 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
14S | 338007 | 3BEEBE | 115 | 0.91567 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 137.4
14S | 338007 | 3BEEBE | 115 | 0.91734 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 137.4
18S | 338007 | 3BEEBE | 115 | 0.87081 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338007 | 3BEEBE | 115 | 0.89261 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338008 | 3GARNER* | 115 | 0.89052 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338008 | 3GARNER* | 115 | 0.91186 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338009 | 3T.E.MC | 115 | 0.89039 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338009 | 3T.E.MC | 115 | 0.91173 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338050 | 3T.E.#6 | 115 | 0.91906 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338100 | 5BERRYV | 161 | 0.86699 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338101 | 5GR FOR | 161 | 0.87791 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338102 | 5HARR-W | 161 | 0.90841 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338103 | 5GRFORS | 161 | 0.8798 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338112 | 5HEBR-S | 161 | 0.90641 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
18S | 338113 | 5HEBR-I | 161 | 0.90432 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
18S | 338160 | 5EBON S* | 161 | 0.91853 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
10S | 338205 | 3PARAG | 115 | 1.0534 | BUS 338170 [5JONES 161.00] TO BUS 338703 [5JONE-N# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
10S | 338205 | 3PARAG | 115 | 1.0545 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
10S | 338205 | 3PARAG | 115 | 1.0534 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
10S | 338205 | 3PARAG | 115 | 1.0588 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 | 3PARAG | 115 | 1.0581 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 | 3PARAG | 115 | 1.0578 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 | 3PARAG | 115 | 1.0584 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
14S | 338205 | 3PARAG | 115 | 1.0519 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0521 | 19.6
14S | 338205 | 3PARAG | 115 | 1.0506 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0521 | 19.6
14S | 338205 | 3PARAG | 115 | 1.0569 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338205 | 3PARAG | 115 | 1.0571 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0571 | 17.1
14S | 338205 | 3PARAG | 115 | 1.0561 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0571 | 17.1
14S | 338205 | 3PARAG | 115 | 1.0558 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0571 | 17.1
14S | 338205 | 3PARAG | 115 | 1.0565 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0571 | 17.1
10S | 338205 | 3PARAG | 115 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338206 | 3SEDGWK* | 115 | 1.0649 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338206 | 3SEDGWK* | 115 | 1.0564 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338206 | 3SEDGWK* | 115 | 1.0648 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338206 | 3SEDGWK* | 115 | 1.0586 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338207 | 3T.E.#7 | 115 | 1.0633 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338207 | 3T.E.#7 | 115 | 1.0548 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338207 | 3T.E.#7 | 115 | 1.0632 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338207 | 3T.E.#7 | 115 | 1.0571 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338208 | 3WALNUT | 115 | 1.0651 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338208 | 3WALNUT | 115 | 1.0567 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338208 | 3WALNUT | 115 | 1.065 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338208 | 3WALNUT | 115 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
18S | 338410 | 5WM-DOV | 161 | 0.91701 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338411 | 5WM-GAT | 161 | 0.91723 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338413 | 5WM-LH2 | 161 | 0.91629 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338414 | 5WM-POK | 161 | 0.9125 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338420 | 5DONAGHE | 161 | 0.89413 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338421 | 5CONW-S | 161 | 0.91478 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338421 | 5CONW-S | 161 | 0.89506 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338423 | 5CONIND | 161 | 0.9157 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338423 | 5CONIND | 161 | 0.89646 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
14W | 338552 | HARRISON-S1 | 69 | 1.0537 | BUS 338101 [5GR FOR 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | * | 205.6
14W | 338552 | HARRISON-S1 | 69 | 1.0556 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | * | 205.6
10S | 338552 | HARRISON-S1 | 69 | 1.0523 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | * | 217.5
14S | 338552 | HARRISON-S1 | 69 | 1.0558 | BUS 338100 [5BERRYV 161.00] TO BUS 338682 [5OSAGE # 161.00] CKT 1 | Eureka Springs - Harrison East | * | 238.1
18S | 338554 | OSAGE-CR1 | 69 | 0.88471 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338556 | OSAGE-CR2 | 69 | 0.88471 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
10W | 338570 | BLACKROCK1 | 69 | 1.0508 | BUS 338144 [8ISXF 5 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA
14W | 338570 | BLACKROCK1 | 69 | 1.051 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 1.0506 | 9.6
14W | 338570 | BLACKROCK1 | 69 | 1.0503 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0506 | 9.6
14W | 338570 | BLACKROCK1 | 69 | 1.0506 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0506 | 9.6
18S | 338570 | BLACKROCK1 | 69 | 1.0641 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 1.0656 | 14
18S | 338570 | BLACKROCK1 | 69 | 1.0643 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0656 | 14
18S | 338570 | BLACKROCK1 | 69 | 1.0657 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0656 | 14
10W | 338578 | OPPELO | 69 | 1.0506 | BUS 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 | OPPELO | 69 | 1.0506 | BUS 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 | OPPELO | 69 | 1.05 | BUS 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 | OPPELO | 69 | 1.0502 | BUS 337940 [5HAMLET* 161.00] TO BUS 337941 [5HAMLT 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 | OPPELO | 69 | 1.0501 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 | OPPELO | 69 | 1.0501 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 | OPPELO | 69 | 1.0507 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 1.0509 | 72.8
10W | 338578 | OPPELO | 69 | 1.0506 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0509 | 72.8
10W | 338578 | OPPELO | 69 | 1.0505 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0509 | 72.8
10W | 338578 | OPPELO | 69 | 1.0512 | BUS 337826 [3LR-PIN 115.00] TO BUS 337829 [5LR-PIN 161.00] CKT 1 | Same | NA | NA
10W | 338578 | OPPELO | 69 | 1.0503 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 111.9
14S | 338581 | DELUCE1 | 69 | 1.0511 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | NA | NA
14S | 338581 | DELUCE1 | 69 | 1.055 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
14S | 338581 | DELUCE1 | 69 | 1.0552 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
14S | 338581 | DELUCE1 | 69 | 1.0562 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
14S | 338581 | DELUCE1 | 69 | 1.0507 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
14S | 338581 | DELUCE1 | 69 | 1.0592 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
14S | 338581 | DELUCE1 | 69 | 1.0564 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0604 | 34.7
18S | 338581 | DELUCE1 | 69 | 1.0536 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.055 | 38.9
18S | 338581 | DELUCE1 | 69 | 1.0502 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.055 | 38.9
18S | 338583 | WARD1 | 69 | 0.87719 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338583 | WARD1 | 69 | 0.89715 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
10S | 338585 | HEBERSP1 | 69 | 1.0546 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0547 | 188.3
14W | 338585 | HEBERSP1 | 69 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0545 | 164.1
14W | 338585 | HEBERSP1 | 69 | 1.0528 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 1.0532 | 78.7
14W | 338585 | HEBERSP1 | 69 | 1.0517 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0532 | 78.7
14W | 338585 | HEBERSP1 | 69 | 1.0509 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0532 | 78.7
14W | 338585 | HEBERSP1 | 69 | 1.0507 | BUS 337939 [5GOLDCR* 161.00] TO BUS 337940 [5HAMLET* 161.00] CKT 1 | Same | NA | NA
14W | 338585 | HEBERSP1 | 69 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14W | 338585 | HEBERSP1 | 69 | 1.0545 | BUS 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14W | 338585 | HEBERSP1 | 69 | 1.0547 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14S | 338585 | HEBERSP1 | 69 | 1.0546 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 110.2
18S | 338681 | 5HARR-S | 161 | 0.91572 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
18S | 338682 | 5OSAGE # | 161 | 0.8626 | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | 259.9
10S | 338704 | 3LIGHT # | 115 | 1.0582 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338704 | 3LIGHT # | 115 | 1.0645 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338704 | 3LIGHT # | 115 | 1.056 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338704 | 3LIGHT # | 115 | 1.0644 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338710 | 3CRO-RG# | 115 | 1.0584 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338710 | 3CRO-RG# | 115 | 1.05 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0503 | 19.2
10W | 338710 | 3CRO-RG# | 115 | 1.0644 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338710 | 3CRO-RG# | 115 | 1.0562 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338710 | 3CRO-RG# | 115 | 1.0644 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338756 | 3WARD # | 115 | 0.91804 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 127.7
14S | 338756 | 3WARD # | 115 | 0.906 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 137.4
14S | 338756 | 3WARD # | 115 | 0.90222 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 137.4
18S | 338756 | 3WARD # | 115 | 0.85526 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338006 [3CABOT 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
18S | 338756 | 3WARD # | 115 | 0.87472 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 154.6
10S | 338757 | 3BRYNTS# | 115 | 0.90753 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
14S | 338757 | 3BRYNTS# | 115 | 0.8922 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 150.2
18S | 338757 | 3BRYNTS# | 115 | 0.87244 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 338757 | 3BRYNTS# | 115 | 0.91929 | BUS 337803 [3BRYANT 115.00] TO BUS 338757 [3BRYNTS# 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 338758 | 5HEBR-N# | 161 | 0.90247 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
18S | 338880 | 3HELN-I | 115 | 0.90733 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA

## Draft Thermal
Contingency Scan - Thermal Overloads
Draft 2010-2012 Construction Plan Approved and Proposed Projects Included
Model | LIMITING ELEMENT |  | RATING (MVA) | FLOW (MW) | % | BUS TO BUS CON | BREAKER TO BREAKER | % | Flow (MW) | C-LOAD
18S | 334043 4TUBULAR 138 | 334044 4DOBBIN 138 1 | 112 | 137 | 124.1% | BUS 334074 [4PANORAM 138.00] TO BUS 334075 [4LONGMIR 138.00] CKT 1 | Lewis Creek - Longmire | 124% | 137 | 44.7
18S | 334043 4TUBULAR 138 | 334044 4DOBBIN 138 1 | 112 | 139 | 133.7% | BUS 334073 [4EGYPT 138] TO BUS 334074 [4PANORAM 138.00] CKT 1 | Lewis Creek - Longmire | 124% | 137 | 44.7
18S | 334120 4NU LJON 138 | 334211 4BDAYTON 138 1 | 99 | 101 | 106.6% | BUS 334084 [4CLVELND 138.00] TO BUS 334208 [4JACINTO 138.00] CKT 1 | Same | NA | NA | NA
18S | 334282 4RAYBURN 138 | 334330 4JASPER 138 1 | 112 | 112 | 101.1% | BUS 334320 [8CYPRESS 500.00] TO BUS 334325 [8HARTBRG 500.00] CKT 1 | Same | NA | NA | NA
18S | 334413 4PNEC BK 138 | 334430 4SABINE 138 1 | 288 | 298 | 103.5% | BUS 334413 [4PNEC BK 138.00] TO BUS 334414 [4LINDE 138] CKT 1 | Sabine - Port Neches (via Linde) | 106% | 304 | 27.3
18S | 334413 4PNEC BK 138 | 334430 4SABINE 138 1 | 288 | 313 | 108.7% | BUS 334414 [4LINDE 138] TO BUS 334430 [4SABINE 138] CKT 1 | Sabine - Port Neches (via Linde) | 106% | 304 | 27.3
14S | 334413 4PNEC BK 138 | 334430 4SABINE 138 1 | 288 | 288 | 100.1% | BUS 334413 [4PNEC BK 138.00] TO BUS 334414 [4LINDE 138] CKT 1 | Sabine - Port Neches (via Linde) | 102% | 294 | 24.9
14S | 334413 4PNEC BK 138 | 334430 4SABINE 138 1 | 288 | 302 | 104.8% | BUS 334414 [4LINDE 138] TO BUS 334430 [4SABINE 138] CKT 1 | Sabine - Port Neches (via Linde) | 102% | 294 | 24.9
18S | 334414 4LINDE 138 | 334430 4SABINE 138 1 | 288 | 301 | 104.6% | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138] CKT 1 | Same | NA | NA | NA
14S | 334414 4LINDE 138 | 334430 4SABINE 138 1 | 288 | 290 | 100.9% | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138] CKT 1 | Same | NA | NA | NA
18S | 334600 2KOLBS 69 | 334620 2LAKEVEW 69 1 | 51 | 52 | 102.1% | BUS 334624 [2ATLANTI 69 ] TO BUS 334627 [PNECBK2B 69 ] CKT 1 | Same | NA | NA | NA
14S | 334600 2KOLBS 69 | 334620 2LAKEVEW 69 1 | 51 | 51 | 100.7% | BUS 334624 [2ATLANTI 69 ] TO BUS 334627 [PNECBK2B 69 ] CKT 1 | Same | NA | NA | NA
14W | 334600 2KOLBS 69 | 334620 2LAKEVEW 69 1 | 51 | 51 | 101.6% | BUS 334624 [2ATLANTI 69 ] TO BUS 334627 [PNECBK2B 69 ] CKT 1 | Same | NA | NA | NA
18S | 335094 2MOSSVL 69 | 335108 2L253ATP 69 1 | 39 | 40 | 104.1% | BUS 335094 [2MOSSVL 69 ] TO BUS 335107 [2ALFOL 69 ] CKT 1 | Same | NA | NA | NA
18S | 335094 2MOSSVL 69 | 335107 2ALFOL 69 1 | 39 | 41 | 106.1% | BUS 335094 [2MOSSVL 69 ] TO BUS 335108 [2L253ATP 69 ] CKT 1 | Same | NA | NA | NA
10S | 335094 2MOSSVL 69 | 335108*2L253ATP 69 1 | 39 | 40 | 102.9% | BUS 335094 [2MOSSVL 69 ] TO BUS 335107 [2ALFOL 69 ] CKT 1 | Same | NA | NA | NA
10S | 335094 2MOSSVL 69 | 335107*2ALFOL 69 1 | 39 | 40.9 | 104.9% | BUS 335094 [2MOSSVL 69 ] TO BUS 335108 [2L253ATP 69 ] CKT 1 | Same | NA | NA | NA
14S | 335094 2MOSSVL 69 | 335108 2L253ATP 69 1 | 39 | 41 | 104.8% | BUS 335094 [2MOSSVL 69 ] TO BUS 335107 [2ALFOL 69 ] CKT 1 | Same | NA | NA | NA
14S | 335094 2MOSSVL 69 | 335107 2ALFOL 69 1 | 39 | 42 | 106.8% | BUS 335094 [2MOSSVL 69 ] TO BUS 335108 [2L253ATP 69 ] CKT 1 | Same | NA | NA | NA
18S | 335125 4MOSSVL 138 | 335200 4NELSON 138 1 | 282 | 282 | 101.3% | BUS 335061 [4CTCON W 138.00] TO BUS 335062 [4ARZONA 138] CKT 1 | Same | NA | NA | NA
18S | 335125 4MOSSVL 138 | 335200 4NELSON 138 1 | 282 | 288 | 103.4% | BUS 335060 [4CARLYSS 138.00] TO BUS 335061 [4CTCON W 138.00] CKT 1 | Same | NA | NA | NA
18S | 335190 6NLSON 230 | 303101 6MOSBLF 230 1 | 374 | 411 | 110.7% | BUS 335074 [6DYNEGY 230.00] TO BUS 335077 [6PGROVE 230.00] CKT 1 | Same | NA | NA | NA
14S | 335190 6NLSON 230 | 303101 6MOSBLF 230 1 | 374 | 395 | 106.4% | BUS 335074 [6DYNEGY 230.00] TO BUS 335077 [6PGROVE 230.00] CKT 1 | Same | NA | NA | NA
10S | 335217 2CHLOMAL 69 | 335250*2IOWA 6 69 1 | 39 | 41.9 | 108.9% | BUS 335265 [2LAWTAG 69 ] TO BUS 335266 [2JENNGS 69 ] CKT 1 | Same | NA | NA | NA
10S | 335217*2CHLOMAL 69 | 335253 2LACASNE 69 1 | 33 | 43.8 | 132.3% | BUS 335259 [2L13ATP 69 ] TO BUS 335266 [2JENNGS 69 ] CKT 1 | Jennings - Elton | 107.9% | 36 | 7.6
10S | 335217*2CHLOMAL 69 | 335253 2LACASNE 69 1 | 33 | 43.8 | 132.4% | BUS 335258 [2COMPTON 69 ] TO BUS 335259 [2L13ATP 69 ] CKT 1 | Jennings - Elton | 107.9% | 36 | 7.6
10S | 335217*2CHLOMAL 69 | 335253 2LACASNE 69 1 | 33 | 35.9 | 107.7% | BUS 335257 [2ELTON 69 ] TO BUS 335258 [2COMPTON 69 ] CKT 1 | Jennings - Elton | 109.1% | 119.9 | 7.6
10S | 335258 2COMPTON 69 | 335259*2L13ATP 69 1 | 33 | 36.6 | 110.3% | BUS 335253 [2LACASNE 69 ] TO BUS 335254 [2CARTER 69 ] CKT 1 | Carter - Chlomal | 110.3% | 36.6 | 6
10S | 335258 2COMPTON 69 | 335259*2L13ATP 69 1 | 33 | 43.4 | 133.5% | BUS 335217 [2CHLOMAL 69 ] TO BUS 335253 [2LACASNE 69 ] CKT 1 | Carter - Chlomal | 110.3% | 36.6 | 6
10S | 335259 2L13ATP 69 | 335266*2JENNGS 69 1 | 33 | 37.1 | 111.6% | BUS 335253 [2LACASNE 69 ] TO BUS 335254 [2CARTER 69 ] CKT 1 | Carter - Chlomal | 111.6% | 37.1 | 6
10S | 335259 2L13ATP 69 | 335266*2JENNGS 69 1 | 33 | 43.9 | 133% | BUS 335217 [2CHLOMAL 69 ] TO BUS 335253 [2LACASNE 69 ] CKT 1 | Carter - Chlomal | 111.6% | 37.1 | 6
18S | 335346 2SCOTT 69 | 335435 2CARNCRO 69 1 | 42 | 49 | 122% | BUS 335441 [2L637TP 69 ] TO BUS 335442 [2CHAMPAN 69 ] CKT 1 | Sunset - Champagne | * | * | 10.8
10S | 335378*4SCOTT2 138 | 303152 4SEMERE 138 1 | 130 | 124.5 | 101.9% | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA
10S | 335378*4SCOTT2 138 | 303152 4SEMERE 138 1 | 130 | 130 | 107.2% | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA
10W | 335379 4SCOTT1 138 | 303132*4JUDICE 138 1 | 241 | 250.6 | 113.6% | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138] CKT 1 | Moril - Leblanc | 108.8% | 241.7 | 9.4
10S | 335379 4SCOTT1 138 | 303132*4JUDICE 138 1 | 241 | 257.4 | 119.6% | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138] CKT 1 | Moril - Leblanc | 109.3% | 239.1 | 22.6
10S | 335379*4SCOTT1 138 | 303130 4NCROWL 138 1 | 216 | 204.7 | 104.2% | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA
10S | 335380*4MEAUX 138 | 303132 4JUDICE 138 1 | 185 | 182.6 | 114.1% | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138] CKT 1 | Moril - Leblanc | 101.4% | 166.1 | 22.6
10S | 335387*4DELCAMB 138 | 335388 4MORIL 138 1 | 251 | 240.7 | 103.1% | BUS 335379 [4SCOTT1 138] TO BUS 303132 [4JUDICE 138] CKT 1 | Same | NA | NA | NA
10S | 335389*4DUBOIN 138 | 335390 4BUWHSE 138 1 | 112 | 131.3 | 126.9% | BUS 335388 [4MORIL 138] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA
10S | 335390*4BUWHSE 138 | 500440 IVANHOE4 138 1 | 145 | 143.6 | 101.9% | BUS 335388 [4MORIL 138] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA
14W | 335391 4CECELIA 138 | 303152 4SEMERE 138 1 | 130 | 131 | 103.7% | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA
18S | 335400 2FIVEPTS 69 | 335401 2TIGRE 69 1 | 39 | 43 | 113.2% | BUS 335388 [4MORIL 138] TO BUS 335405 [2MORIL 69 ] CKT 1 | Same | NA | NA | NA
14S | 335400 2FIVEPTS 69 | 335401 2TIGRE 69 1 | 39 | 40 | 105.6% | BUS 335388 [4MORIL 138] TO BUS 335405 [2MORIL 69 ] CKT 1 | Same | NA | NA | NA
18S | 335401 2TIGRE 69 | 335403 2L-247TP 69 1 | 39 | 39 | 103.7% | BUS 335388 [4MORIL 138] TO BUS 335405 [2MORIL 69 ] CKT 1 | Same | NA | NA | NA
18S | 335411 2HOLIDAY 69 | 335412 2LAFAYET 69 1 | 39 | 39 | 101.7% | BUS 335405 [2MORIL 69 ] TO BUS 335408 [2NEWIBER 69 ] CKT 1 | Same | NA | NA | NA
10S | 335411*2HOLIDAY 69 | 335412 2LAFAYET 69 1 | 39 | 43.5 | 115.4% | BUS 335405 [2MORIL 69 ] TO BUS 335408 [2NEWIBER 69 ] CKT 1 | Same | NA | NA | NA
10S | 335411*2HOLIDAY 69 | 335412 2LAFAYET 69 1 | 39 | 44.4 | 116.3% | BUS 335388 [4MORIL 138] TO BUS 335405 [2MORIL 69 ] CKT 1 | Same | NA | NA | NA
18S | 335439 2L658TP 69 | 335441 2L637TP 69 1 | 51 | 50 | 100% | BUS 335346 [2SCOTT 69 ] TO BUS 335435 [2CARNCRO 69 ] CKT 1 | Same | NA | NA | NA
14W | 335536 6ADDIS 230 | 303000 6CAJUN1 230 1 | 566 | 579 | 101.3% | BUS 335641 [TP.ESSO 230.00] TO BUS 335770 [6JAGUAR 230.00] CKT 1 | Esso - Jaguar | 101.2% | 579 | 0
14W | 335536 6ADDIS 230 | 303000 6CAJUN1 230 1 | 566 | 577 | 100.9% | BUS 335770 [6JAGUAR 230.00] TO BUS 335772 [6ENJAY 230.00] CKT 1 | Same | NA | NA | NA
14W | 335536 6ADDIS 230 | 303000 6CAJUN1 230 1 | 566 | 584 | 102.2% | BUS 335500 [8WEBRE 500.00] TO BUS 303005 [8CAJUN2 500.00] CKT 1 | Same | NA | NA | NA
14W | 335536 6ADDIS 230 | 303000 6CAJUN1 230 1 | 566 | 585 | 102.4% | BUS 335772 [6ENJAY 230.00] TO BUS 335825 [6FANCY 230.00] CKT 1 | Same | NA | NA | NA
14W | 335536 6ADDIS 230 | 303000 6CAJUN1 230 1 | 566 | 589 | 103.1% | BUS 335836 [8MCKNT 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA
10W | 335593 4MONOCM1 138 | 335595*4ALCHEM 138 1 | 225 | 219 | 100.5% | BUS 335574 [6LICAR 230.00] TO BUS 335575 [6BELL HE 230.00] CKT 1 | AAC Corp - Belle Helene | 100.8% | 219.7 | 14.8
10W | 335593 4MONOCM1 138 | 335595*4ALCHEM 138 1 | 225 | 222.1 | 101.9% | BUS 335573 [6A.A.C. 230.00] TO BUS 335574 [6LICAR 230.00] CKT 1 | AAC Corp - Belle Helene | 100.8% | 219.7 | 14.8
10W | 335593 4MONOCM1 138 | 335595*4ALCHEM 138 1 | 225 | 219.8 | 100.9% | BUS 335568 [6WGLEN 230.00] TO BUS 335569 [6POLSCAR 230.00] CKT 1 | Willow Glen - AAC | 102.1% | 222.3 | 0
10W | 335593 4MONOCM1 138 | 335595*4ALCHEM 138 1 | 225 | 223 | 102.3% | BUS 335569 [6POLSCAR 230.00] TO BUS 335573 [6A.A.C. 230.00] CKT 1 | Willow Glen - AAC | 102.1% | 222.3 | 0
18S | 335595 4ALCHEM 138 | 335601 4WGLEN-2 138 1 | 282 | 274 | 100.5% | BUS 335599 [4GEIGY 138] TO BUS 335600 [4AIRPROD 138.00] CKT 1 | Same | NA | NA | NA
18S | 335595 4ALCHEM 138 | 335601 4WGLEN-2 138 1 | 282 | 275 | 101.1% | BUS 335600 [4AIRPROD 138.00] TO BUS 335601 [4WGLEN-2 138.00] CKT 1 | Same | NA | NA | NA
10W | 335595*4ALCHEM 138 | 335601 4WGLEN-2 138 1 | 282 | 269.3 | 100.3% | BUS 335599 [4GEIGY 138] TO BUS 335600 [4AIRPROD 138.00] CKT 1 | Same | NA | NA | NA
10W | 335595*4ALCHEM 138 | 335601 4WGLEN-2 138 1 | 282 | 271 | 101% | BUS 335600 [4AIRPROD 138.00] TO BUS 335601 [4WGLEN-2 138.00] CKT 1 | Same | NA | NA | NA
18S | 335610 4WGLEN 138 | 335628 T300/331 138 1 | 216 | 221 | 102.3% | BUS 335591 [4GEISMAR 138.00] TO BUS 335610 [4WGLEN 138] CKT 1 | Same | NA | NA | NA
18S | 335625 4GONZL 138 | 336050 4SORXFM 138 1 | 130 | 182 | 141% | BUS 335610 [4WGLEN 138] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | 120.3
18S | 335625 4GONZL 138 | 336050 4SORXFM 138 1 | 130 | 182 | 141.1% | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | 120.3
18S | 335627 4OAKGROV 138 | 335628 T300/331 138 1 | 216 | 220 | 102.3% | BUS 335591 [4GEISMAR 138.00] TO BUS 335610 [4WGLEN 138] CKT 1 | Same | NA | NA | NA
18S | 335782 2PTHUDSONA 69 | 335805 4PT HUD 138 1 | 100 | 100 | 100.1% | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335815 [6PT.HUD 230.00] CKT 1 | Same | NA | NA | NA
18S | 335787 2MCMANUS 69 | 335788 2BRADYH 69 1 | 20 | 18 | 100.6% | BUS 335784 [ 2GRAVEL 69 ] TO BUS 335785 [2JACKSON 69 ] CKT 1 | Port Hudson - Jackson | 101% | 18 | 3
18S | 335787 2MCMANUS 69 | 335788 2BRADYH 69 1 | 20 | 18 | 102.4% | BUS 335783 [2SANDYC 69 ] TO BUS 335784 [ 2GRAVEL 69 ] CKT 1 | Port Hudson - Jackson | 101% | 18 | 3
18S | 335787 2MCMANUS 69 | 335788 2BRADYH 69 1 | 20 | 18 | 104% | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69 ] CKT 1 | Port Hudson - Jackson | 101% | 18 | 3
18S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 33 | 103.5% | BUS 335784 [ 2GRAVEL 69 ] TO BUS 335785 [2JACKSON 69 ] CKT 1 | Port Hudson - Jackson | 103% | 33 | 3
18S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 35 | 110.9% | BUS 335783 [2SANDYC 69 ] TO BUS 335784 [ 2GRAVEL 69 ] CKT 1 | Port Hudson - Jackson | 103% | 33 | 3
18S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 36 | 115.3% | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69 ] CKT 1 | Port Hudson - Jackson | 103% | 33 | 3
18S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 37 | 111% | BUS 335793 [2FRANCIS 69 ] TO BUS 335795 [2GRANT 69 ] CKT 1 | Port Hudson B - Francis | 111% | 37 | 2
18S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 38 | 117.5% | BUS 335795 [2GRANT 69 ] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 111% | 37 | 2
14S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 35 | 104.9% | BUS 335793 [2FRANCIS 69 ] TO BUS 335795 [2GRANT 69 ] CKT 1 | Port Hudson B - Francis | 104.8% | 35 | 0.9
14S | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 37 | 111.6% | BUS 335795 [2GRANT 69 ] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 104.8% | 35 | 0.9
14W | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 36 | 104.9% | BUS 335793 [2FRANCIS 69 ] TO BUS 335795 [2GRANT 69 ] CKT 1 | Port Hudson B - Francis | 104.9% | 36 | 0.9
14W | 335791 2TEJAC 69 | 335792 2MRYDALE 69 1 | 33.5 | 37 | 107.7% | BUS 335795 [2GRANT 69 ] TO BUS 335796 [2PTHUDSONB 69.000] CKT 1 | Port Hudson B - Francis | 104.9% | 36 | 0.9
18S | 335796 2PTHUDSONB 69 | 335805 4PT HUD 138 2 | 100 | 100 | 100.1% | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335815 [6PT.HUD 230.00] CKT 1 | Same | NA | NA | NA
18S | 336037 3VLNTIN 115 | 336080 3CLOVEL 115 1 | 114 | 141 | 123.7% | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA
14S | 336037 3VLNTIN 115 | 336080 3CLOVEL 115 1 | 114 | 142 | 125.1% | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA
18S | 336050 4SORXFM 138 | 336051 3SORNTO 115 1 | 140 | 185 | 132.4% | BUS 335610 [4WGLEN 138] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | 120.3
18S | 336050 4SORXFM 138 | 336051 3SORNTO 115 1 | 140 | 185 | 132.4% | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | * | * | 120.3
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 516.7 | 102.6% | BUS 335574 [6LICAR 230.00] TO BUS 335575 [6BELL HE 230.00] CKT 1 | AAC Corp - Belle Helene | 102.6% | 525.3 | 14.8
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 520 | 103.4% | BUS 335573 [6A.A.C. 230.00] TO BUS 335574 [6LICAR 230.00] CKT 1 | AAC Corp - Belle Helene | 102.6% | 525.3 | 14.8
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 517.7 | 102.8% | BUS 335568 [6WGLEN 230.00] TO BUS 335569 [6POLSCAR 230.00] CKT 1 | Willow Glen - AAC | 103.6% | 529.4 | 0
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 521.1 | 103.6% | BUS 335569 [6POLSCAR 230.00] TO BUS 335573 [6A.A.C. 230.00] CKT 1 | Willow Glen - AAC | 103.6% | 529.4 | 0
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 504.9 | 100% | BUS 335575 [6BELL HE 230.00] TO BUS 335576 [6WOODSTK 230.00] CKT 1 | Same | NA | NA | NA
10W | 336060*6SORR 2 230 | 303200 6VIGNES 230 1 | 520 | 503.6 | 100.1% | BUS 335576 [6WOODSTK 230.00] TO BUS 335579 [6VULCHLR 230.00] CKT 1 | Same | NA | NA | NA
18S | 336068 6BLPNT 230 | 336190 6GYPSY 230 1 | 436 | 483 | 113.7% | BUS 336069 [6TEZCUCO 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA
14S | 336068 6BLPNT 230 | 336190 6GYPSY 230 1 | 436 | 484 | 113.7% | BUS 336069 [6TEZCUCO 230.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA
18S | 336069 6TEZCUCO 230 | 336154 6WATFRD 230 1 | 639 | 631 | 101.6% | BUS 336068 [6BLPNT 230.00] TO BUS 336190 [6GYPSY 230.00] CKT 1 | Same | NA | NA | NA
14S | 336069 6TEZCUCO 230 | 336154 6WATFRD 230 1 | 639 | 632 | 101.7% | BUS 336068 [6BLPNT 230.00] TO BUS 336190 [6GYPSY 230.00] CKT 1 | Same | NA | NA | NA
18S | 336080 3CLOVEL 115 | 336081 3GMEADW 115 1 | 114 | 113 | 102.4% | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA
14S | 336080 3CLOVEL 115 | 336081 3GMEADW 115 1 | 114 | 114 | 103.5% | BUS 336084 [3BARATA 115.00] TO BUS 336280 [39MILE 115.00] CKT 1 | Same | NA | NA | NA
18S | 336092 3CARLSL 115 | 336293 3PTNICK 115 1 | 114 | 115 | 126.3% | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA
14S | 336092 3CARLSL 115 | 336293 3PTNICK 115 1 | 114 | 115 | 126.9% | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA
14W | 336092 3CARLSL 115 | 336293 3PTNICK 115 1 | 114 | 114 | 123.8% | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA
10S | 336092*3CARLSL 115 | 336293 3PTNICK 115 1 | 114 | 114.1 | 124.4% | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA
10W | 336092*3CARLSL 115 | 336293 3PTNICK 115 1 | 114 | 113.4 | 122% | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA
10W | 336111 3AMITE 115 | 336517*3GILBR* 115 1 | 108 | 108.8 | 105% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 105% | 108.8 | 0
10W | 336111 3AMITE 115 | 336517*3GILBR* 115 1 | 108 | 109.3 | 105.2% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 105% | 108.8 | 0
10W | 336131 6ADMSCRK 230 | 336136*6BOGALUS 230 2 | 637 | 800 | 126.3% | BUS 336131 [6ADMSCRK 230.00] TO BUS 336136 [6BOGALUS 230.00] CKT 1 | Same | NA | NA | NA
18S | 336220 3GYPSY 115 | 336230 3CLAYTN 115 1 | 319 | 316 | 100.6% | BUS 336194 [6SNFARM 230.00] TO BUS 336233 [3SNFARM 115.00] CKT 1 | Same | NA | NA | NA
18S | 336220 3GYPSY 115 | 336230 3CLAYTN 115 1 | 319 | 320 | 101.6% | BUS 336190 [6GYPSY 230.00] TO BUS 336220 [3GYPSY 115.00] CKT 1 | Same | NA | NA | NA
18S | 336232 3KENNER 115 | 336233 3SNFARM 115 1 | 270 | 310 | 118.9% | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA
14S | 336232 3KENNER 115 | 336233 3SNFARM 115 1 | 270 | 288 | 109.4% | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA
14W | 336232 3KENNER 115 | 336233 3SNFARM 115 1 | 270 | 286 | 108.6% | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA
10S | 336232*3KENNER 115 | 336233 3SNFARM 115 1 | 270 | 265.6 | 100.3% | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA
10W | 336515*3LIBRTY 115 | 336517 3GILBR* 115 1 | 115 | 117.3 | 102.3% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 102.3% | 117.3 | 0
10W | 336515*3LIBRTY 115 | 336517 3GILBR* 115 1 | 115 | 118 | 102.5% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 102.3% | 117.3 | 0
10W | 336552 3NORFLD 115 | 336553*3MALIL* 115 1 | 199 | 202.6 | 104.1% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 104.1% | 202.6 | 0
10W | 336552 3NORFLD 115 | 336553*3MALIL* 115 1 | 199 | 203.8 | 104.2% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 104.1% | 202.6 | 0
10W | 336553*3MALIL* 115 | 336554 3BROKHV 115 1 | 199 | 210.9 | 108.4% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 108.4% | 210.9 | 0
10W | 336553*3MALIL* 115 | 336554 3BROKHV 115 1 | 199 | 212.2 | 108.5% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 108.4% | 210.9 | 0
10S | 336554 3BROKHV 115 | 336770*3WESSON 115 1 | 161 | 155.7 | 103.1% | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 103.1% | 155.7 | 8.8
10S | 336554 3BROKHV 115 | 336770*3WESSON 115 1 | 161 | 168 | 113.8% | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 103.1% | 155.7 | 8.8
10W | 336765 3FLRNCE 115 | 336890*3JAX-S 115 1 | 161 | 176 | 106.1% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 106.2% | 175.9 | 0
10W | 336765 3FLRNCE 115 | 336890*3JAX-S 115 1 | 161 | 175.9 | 106.2% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 106.2% | 175.9 | 0
10S | 336771 3JAM RD* 115 | 336772*3HZLHST 115 1 | 120 | 137.8 | 125.3% | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 125.2% | 137.8 | 8.8
10S | 336771 3JAM RD* 115 | 336772*3HZLHST 115 1 | 120 | 148.3 | 139.1% | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 125.2% | 137.8 | 8.8
10S | 336772 3HZLHST 115 | 336773*3COPHSW* 115 1 | 120 | 119.9 | 109.2% | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 109.1% | 119.9 | 8.8
10S | 336772 3HZLHST 115 | 336773*3COPHSW* 115 1 | 120 | 131.1 | 123.3% | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 109.1% | 119.9 | 8.8
18S | 336805 3WATERWY 115 | 336806 3VKB-E* 115 1 | 161 | 172 | 107.7% | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA
14S | 336805 3WATERWY 115 | 336806 3VKB-E* 115 1 | 161 | 173 | 107.9% | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA
14W | 336830 8B.WLSN 500 | 336839 8R.BRAS 500 1 | 1732 | 1772 | 102.2% | BUS 336562 [8FRKLIN 500.00] TO BUS 336820 [8G.GULF 500.00] CKT 1 | Same | NA | NA | NA
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 239.4 | 102.1% | BUS 336880 [3R.BRAS 115.00] TO BUS 336882 [3JAX-W 115.00] CKT 1 | Ray Braswell - South Jackson 115kV | 100.1% | 235 | 30
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 240 | 102.6% | BUS 336906 [3JX-MON 115.00] TO BUS 336907 [3JX-MIA 115.00] CKT 1 | Monument - Rex Brown Jackson | 102.6% | 240.1 | 11.7
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 241.8 | 103.4% | BUS 336907 [3JX-MIA 115.00] TO BUS 336940 [3RX BRN 115.00] CKT 1 | Monument - Rex Brown Jackson | 102.6% | 240.1 | 11.7
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 235.9 | 100.7% | BUS 336771 [3JAM RD* 115.00] TO BUS 336772 [3HZLHST 115.00] CKT 1 | Brookhaven - Byram | * | * | 102.8
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 240.4 | 102.8% | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | * | * | 102.8
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 245.2 | 105% | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | * | * | 102.8
10S | 336871*3JAX-FH 115 | 336880 3R.BRAS 115 1 | 230 | 252.4 | 108.1% | BUS 336842 [6JAX-S 230.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Same | NA | NA | NA
18S | 336890 3JAX-S 115 | 336911 3JAX-E 115 1 | 161 | 166 | 103.6% | BUS 336906 [3JX-MON 115.00] TO BUS 336908 [3JX-FON 115.00] CKT 1 | Monument St. - East Jackson | * | * | 103.6
10W | 336897*3PELAHE 115 | 336898 3MORTON 115 1 | 120 | 127.9 | 104.8% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 104.9% | 127.7 | 0
10W | 336897*3PELAHE 115 | 336898 3MORTON 115 1 | 120 | 127.7 | 104.9% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 104.9% | 127.7 | 0
10W | 336897*3PELAHE 115 | 336898 3MORTON 115 1 | 120 | 123.7 | 101.5% | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA
18S | 337040 6ANDRUS 230 | 337042 3ANDRUS 115 1 | 392 | 404 | 103.1% | BUS 337040 [6ANDRUS 230.00] TO BUS 337050 [6INDOLA 230.00] CKT 1 | Same | NA | NA | NA
10S | 337060 3WINONA 115 | 337061*3SAWYR* 115 1 | 108 | 105.2 | 106.6% | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA
18S | 337098 3CLARKD 115 | 337100 6MEPSCLK 230 1 | 250 | 301 | 120.5% | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA
10S | 337098 3CLARKD 115 | 337100*6MEPSCLK 230 1 | 250 | 301.5 | 120.6% | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA
10W | 337098 3CLARKD 115 | 337100*6MEPSCLK 230 1 | 250 | 301.7 | 120.7% | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA
14S | 337098 3CLARKD 115 | 337100 6MEPSCLK 230 1 | 250 | 301 | 120.5% | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA
14W | 337098 3CLARKD 115 | 337100 6MEPSCLK 230 1 | 250 | 300 | 120.1% | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA
18S | 337126 3BATESV 115 | 337135 3SARDIS 115 1 | 159 | 183 | 124.4% | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | 158.6
18S | 337135 3SARDIS 115 | 337136 3SNTOBI 115 1 | 176 | 160 | 106.4% | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | 158.6
18S | 337136 3SNTOBI 115 | 337137 3CLDWTR 115 1 | 108 | 120 | 134.4% | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | 158.6
18S | 337137 3CLDWTR 115 | 337138 3HRNADO 115 1 | 108 | 97 | 112.7% | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | * | 158.6
18S | 337139 3GETWEL 115 | 337141 3NESBT* 115 1 | 239 | 234 | 104.2% | BUS 337144 [3GRNBRK 115.00] TO BUS 337150 [3HN LAK 115.00] CKT 1 | Horn Lake - Getwell | * | * | 247.1
18S | 337143 3PLUM PT 115 | 337144 3GRNBRK 115 1 | 239 | 273 | 120.2% | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA
18S | 337144 3GRNBRK 115 | 337150 3HN LAK 115 1 | 239 | 303 | 129.3% | BUS 337139 [3GETWEL 115.00] TO BUS 337140 [6GETWELL 230.00] CKT 1 | Same | NA | NA | NA
18S | 337144 3GRNBRK 115 | 337150 3HN LAK 115 1 | 239 | 369 | 159.5% | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA
14S | 337144 3GRNBRK 115 | 337150 3HN LAK 115 1 | 239 | 240 | 100.7% | BUS 337139 [3GETWEL 115.00] TO BUS 337140 [6GETWELL 230.00] CKT 1 | Same | NA | NA | NA
14S | 337144 3GRNBRK 115 | 337150 3HN LAK 115 1 | 239 | 285 | 120.5% | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA
18S | 337150 3HN LAK 115 | 337150 3HN LAK 230 1 | 392 | 393 | 100.4% | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA
18S | 337361 3MINDEN 115 | 303302 3MNDENLG 115 1 | 80 | 80 | 103.4% | BUS 337367 [3ARCADIA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | * | * | 101.6
18S | 337361 3MINDEN 115 | 303302 3MNDENLG 115 1 | 80 | 106 | 142.6% | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | * | * | 101.6
14S | 337361 3MINDEN 115 | 303302 3MNDENLG 115 1 | 80 | 96 | 127.2% | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | * | * | 101.6
14W | 337361 3MINDEN 115 | 303302 3MNDENLG 115 1 | 80 | 93 | 121% | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | * | * | 101.6
10W | 337674 3AMITY * 115 | 338850*3ALPINE# 115 1 | 176 | 94.2 | 100.5% | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 100.5% | 94.2 | 0
10W | 337674 3AMITY * 115 | 338850*3ALPINE# 115 1 | 176 | 94.2 | 100.5% | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 337678 3BISMRK 115 | 337685*3HSEHVW 115 1 | 176 | 109.9 | 111.6% | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 111.6% | 109.9 | 0
10S | 337678 3BISMRK 115 | 337685*3HSEHVW 115 1 | 176 | 98.8 | 100.7% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10W | 337678 3BISMRK 115 | 337685*3HSEHVW 115 1 | 176 | 99.7 | 101.2% | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA
10W | 337678 3BISMRK 115 | 337685*3HSEHVW 115 1 | 176 | 104.6 | 106.2% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10W | 337678 3BISMRK 115 | 337685*3HSEHVW 115 1 | 176 | 109.9 | 111.6% | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 337678*3BISMRK 115 | 338850 3ALPINE# 115 1 | 176 | 99.3 | 104.8% | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 104.8% | 99.3 | 0
10W | 337678*3BISMRK 115 | 338850 3ALPINE# 115 1 | 176 | 99.3 | 104.8% | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA
18S | 337800 3HASKEL 115 | 337801 3BENT-S* 115 1 | 159 | 150 | 105% | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | 167.4
18S | 337803 3BRYANT 115 | 337804 3MABEL 115 1 | 159 | 168 | 107.3% | BUS 337741 [3BUTERF 115.00] TO BUS 337800 [3HASKEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | 167.4
18S | 337803 3BRYANT 115 | 337804 3MABEL 115 1 | 159 | 176 | 112.6% | BUS 337740 [3HSEHVE 115.00] TO BUS 337741 [3BUTERF 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | 167.4
14S | 337803 3BRYANT 115 | 337804 3MABEL 115 1 | 159 | 158 | 100.2% | BUS 337740 [3HSEHVE 115.00] TO BUS 337741 [3BUTERF 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | * | 113.9
18S | 337905 5RUSL-E 161 | 337906 5RUSL-N 161 1 | 396 | 395 | 100.6% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
18S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 238 | 109.6% | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 100% | 220 | 88.2
18S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 256 | 118.9% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 119% | 256 | 27
18S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 272 | 127.2% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 119% | 256 | 27
18S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 256 | 118.9% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
14S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 231 | 105.7% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 105.7% | 231 | 19.7
14S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 246 | 113.4% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 105.7% | 231 | 19.7
14S | 337921 5MOR-E 161 | 337927 5GLEASN 161 1 | 223 | 231 | 105.7% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
18S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 246 | 114.7% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 115% | 247 | 27
18S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 262 | 122.9% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 115% | 247 | 27
18S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 246 | 114.7% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
14S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 221 | 101.5% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 101.5% | 221 | 19.7
14S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 237 | 109.2% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 101.5% | 221 | 19.7
14S | 337927 5GLEASN 161 | 338424 5TYLER 161 1 | 223 | 221 | 101.5% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
18S | 337928 3CONW-W 115 | 338422 5CONW-W 161 1 | 224 | 230 | 102.7% | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA
18S | 337929 3LK CON 115 | 337930 3MAYFL 115 1 | 239 | 271 | 114.1% | BUS 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 104% | 249 | 39.9
18S | 337929 3LK CON 115 | 337930 3MAYFL 115 1 | 239 | 250 | 104.7% | BUS 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 104.4% | 249 | 39.9
18S | 337929 3LK CON 115 | 337930 3MAYFL 115 1 | 239 | 266 | 111.9% | BUS 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 104.4% | 249 | 39.9
18S | 337929 3LK CON 115 | 337930 3MAYFL 115 1 | 239 | 264 | 111% | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA
18S | 337936 3SYLVN 115 | 337938 5SYLVN 161 1 | 140 | 155 | 110.8% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 247
18S | 337938 5SYLVN 161 | 338748 5GRAVEL# 161 1 | 140 | 137 | 102.3% | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 247
18S | 337938 5SYLVN 161 | 338748 5GRAVEL# 161 1 | 140 | 152 | 114.6% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 247
18S | 337939 5GOLDCR* 161 | 337940 5HAMLET* 161 1 | 223 | 242 | 117.4% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 247
14S | 337939 5GOLDCR* 161 | 337940 5HAMLET* 161 1 | 223 | 213 | 100.6% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 164.1
10S | 337952 3LYNCH 115 | 338481*3MCALMT 115 1 | 159 | 175.4 | 111.9% | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 126 | 113.9% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 115% | 127 | 35.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 127 | 115.7% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 115% | 127 | 35.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 130 | 117.7% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 115% | 127 | 35.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 131 | 119.1% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 115% | 127 | 35.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 131 | 118.8% | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 121% | 133 | 38.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 147 | 133% | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 121% | 133 | 38.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 147 | 133% | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 121% | 133 | 38.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 156 | 141.7% | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 121% | 133 | 38.1
18S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 116 | 105.4% | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 113 | 101.3% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 100.7% | 112 | 27.8
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 115 | 103.2% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 100.7% | 112 | 27.8
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 116 | 104.4% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 100.7% | 112 | 27.8
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 113 | 101.8% | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 103.4% | 115 | 30.1
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 127 | 114.6% | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 103.4% | 115 | 30.1
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 127 | 114.7% | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 103.4% | 115 | 30.1
14S | 338033 5PARKIN 161 | 338041 5TWIST 161 1 | 112 | 136 | 122.5% | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 103.4% | 115 | 30.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 122 | 111.7% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 113% | 124 | 35.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 124 | 113.5% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 113% | 124 | 35.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 126 | 115.6% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 113% | 124 | 35.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 128 | 116.9% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 113% | 124 | 35.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 128 | 116.4% | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 118% | 130 | 38.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 143 | 130.8% | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 118% | 130 | 38.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 143 | 130.9% | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 118% | 130 | 38.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 152 | 139.5% | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 118% | 130 | 38.1
18S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 113 | 103.2% | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA
14S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 124 | 112.4% | BUS 338163 [5EBON N* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - West EHV | 101.2% | 112 | 30.1
14S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 124 | 112.5% | BUS 338163 [5EBON N* 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 101.2% | 112 | 30.1
14S | 338041 5TWIST 161 | 338165 5MTREE 161 1 | 112 | 132 | 120.3% | BUS 338161 [5WM-EHV 161.00] TO BUS 338412 [5WM-LH1 161.00] CKT 1 | Marked Tree - West EHV | 101.2% | 112 | 30.1
10S | 338104*5HARR-E 161 | 338681 5HARR-S 161 1 | 223 | 225.1 | 101.1% | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | 217.5
10W | 338108 5ST_JOE 161 | 338110*5HILLTOP 161 1 | 167 | 173.9 | 102.3% | BUS 338104 [5HARR-E 161.00] TO BUS 338121 [5SUMMIT 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 102.8% | 174.8 | 22.7
10W | 338108 5ST_JOE 161 | 338110*5HILLTOP 161 1 | 167 | 179.1 | 105.4% | BUS 338121 [5SUMMIT 161.00] TO BUS 338122 [5FLIPN 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 102.8% | 174.8 | 22.7
10W | 338108 5ST_JOE 161 | 338110*5HILLTOP 161 1 | 167 | 183.5 | 108.1% | BUS 338122 [5FLIPN 161.00] TO BUS 338123 [5BULLSH* 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 102.8% | 174.8 | 22.7
10W | 338108 5ST_JOE 161 | 338110*5HILLTOP 161 1 | 167 | 185.3 | 109.3% | BUS 338123 [5BULLSH* 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals Dam - Harrison East | 102.9% | 175 | 27.2
14W | 338108 5ST_JOE 161 | 338110 5HILLTOP 161 1 | 167 | 170 | 100.7% | BUS 338104 [5HARR-E 161.00] TO BUS 338121 [5SUMMIT 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 101.2% | 171 | 24.7
14W | 338108 5ST_JOE 161 | 338110 5HILLTOP 161 1 | 167 | 176 | 103.9% | BUS 338121 [5SUMMIT 161.00] TO BUS 338122 [5FLIPN 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 101.2% | 171 | 24.7
14W | 338108 5ST_JOE 161 | 338110 5HILLTOP 161 1 | 167 | 181 | 107% | BUS 338122 [5FLIPN 161.00] TO BUS 338123 [5BULLSH* 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 101.2% | 171 | 24.7
14W | 338108 5ST_JOE 161 | 338110 5HILLTOP 161 1 | 167 | 183 | 108.3% | BUS 338123 [5BULLSH* 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals Dam - Harrison East | 101.3% | 171 | 29.8
18S | 338123 5BULLSH* 161 | 505460 BULL SH5 161 1 | 167 | 180 | 105.7% | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 106% | 180 | 8.8
14S | 338123 5BULLSH* 161 | 505460 BULL SH5 161 1 | 167 | 173 | 100.7% | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 101.1% | 174 | 6.3
14S | 338123 5BULLSH* 161 | 505460 BULL SH5 161 1 | 167 | 177 | 103.1% | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 101.1% | 174 | 6.3
18S | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
18S | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 151 | 100% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 334200 [6PORTER 230.00] TO BUS 334202 [6CHPTSR2 230.00] CKT 1 | China - Porter | 100.1% | 152 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 334202 [6CHPTSR2 230.00] TO BUS 334203 [6CHPTSR1 230.00] CKT 2 | China - Porter | 100.1% | 152 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 334203 [6CHPTSR1 230.00] TO BUS 334204 [6CHINA 230.00] CKT 1 | China - Porter | 100.1% | 152 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69 ] CKT 1 | Vienna - Ruston | 100.1% | 152 | 42.9
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 100.3% | 153 | 24.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 100.4% | 153 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 100.4% | 153 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338012 [3DESARC 115.00] TO BUS 338013 [3COT PL 115.00] CKT 1 | Searcy Price - Brinkley East | 100.5% | 153 | 18.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338013 [3COT PL 115.00] TO BUS 338014 [3BRNK-W 115.00] CKT 1 | Searcy Price - Brinkley East | 100.5% | 153 | 18.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 100.5% | 153 | 103.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 100.5% | 153 | 103.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338011 [3GRIFTH 115.00] TO BUS 338012 [3DESARC 115.00] CKT 1 | Searcy Price - Brinkley East | 100.5% | 153 | 18.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 338010 [3PRICE 115.00] TO BUS 338011 [3GRIFTH 115.00] CKT 1 | Searcy Price - Brinkley East | 100.5% | 153 | 18.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 100.5% | 153 | 1.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 100.5% | 153 | 1.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 100.6% | 153 | 19.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 100.6% | 153 | 19.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338160 [5EBON S* 161.00] TO BUS 338410 [5WM-DOV 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 100.7% | 153 | 94.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338160 [5EBON S* 161.00] TO BUS 338411 [5WM-GAT 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 100.7% | 153 | 94.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 337939 [5GOLDCR* 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 100.7% | 153 | 23.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 100.7% | 153 | 23.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 100.7% | 153 | 23.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 100.7% | 153 | 164.1
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.8% | 153 | 59.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.8% | 153 | 59.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101% | BUS 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.8% | 153 | 59.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.8% | 153 | 59.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 338202 [5JIMHL 161.00] TO BUS 300115 [5STFRAN 161.00] CKT 1 | Hayti South to St Francis | 101% | 154 | 15.9
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 338191 [5BLYELM 161.00] TO BUS 338193 [5BLYINT 161.00] CKT 1 | Blytheville Elm Street - Blyethville I-55 | 101% | 154 | 4.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.5% | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 101.2% | 154 | 45.4
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 101.2% | 154 | 45.4
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.8% | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 101.5% | 154 | 6.3
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.9% | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 101.5% | 154 | 6.3
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.3% | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 101.7% | 155 | 5.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.4% | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 101.7% | 155 | 5.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.1% | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 101.9% | 155 | 25.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.4% | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 101.9% | 155 | 25.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 102% | 155 | 36.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 102% | 155 | 36.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.9% | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.6% | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 158 | 103.7% | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 158 | 104% | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 162 | 106.5% | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 163 | 107.5% | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 164 | 108.2% | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 102.3% | 156 | 78.7
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 155 | 102% | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 102.5% | 156 | 9.6
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 155 | 102.3% | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 102.5% | 156 | 9.6
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 156 | 102.7% | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 102.5% | 156 | 9.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.7% | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 102.6% | 156 | 20.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.1% | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 102.6% | 156 | 20.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 102.6% | 156 | 20.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.4% | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 102.6% | 156 | 4.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.5% | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 102.6% | 156 | 4.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 102.7% | 156 | 79.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 102.7% | 156 | 79.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 102.7% | 156 | 79.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.3% | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 103% | 157 | 23.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.5% | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 103% | 157 | 23.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 103% | 157 | 23.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 103.2% | 157 | 93.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 103.2% | 157 | 93.5
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 156 | 103% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 103.9% | 158 | 27.8
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 157 | 103.4% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 103.9% | 158 | 27.8
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 158 | 104% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 103.9% | 158 | 27.8
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 158 | 104.4% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 103.9% | 158 | 27.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 161 | 105.7% | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 106.3% | 162 | 24.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 161 | 106% | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 106.3% | 162 | 24.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 162 | 106.4% | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 106.3% | 162 | 24.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 163 | 107% | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 106.3% | 162 | 24.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 164 | 107.7% | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 106.3% | 162 | 24.5
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 102.9% | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 108.9% | 165 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 166 | 109.2% | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 109.6% | 166 | 9.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 166 | 109.4% | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 109.6% | 166 | 9.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 167 | 109.9% | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 109.6% | 166 | 9.6
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 167 | 110.1% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 111% | 169 | 27.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 168 | 110.5% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 111% | 169 | 27.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 169 | 111.1% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 111% | 169 | 27.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 169 | 111.5% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 111% | 169 | 27.8
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 160 | 105.5% | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 111.5% | 169 | 0
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | * | 102.2
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 336840 [6R.BRAS 230.00] TO BUS 336849 [6CLNT-IN 230.00] CKT 1 | Ray Braswell - Gerald Andrus SES | * | * | 19.643
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 335836 [8MCKNT 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 337368 [8MTOLIV 500.00] TO BUS 337369 [6MTOLIV 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 337672 [4MURFRE 138] TO BUS 337673 [3MURF-S 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 337859 [3WRIGHTS 115.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 338201 [5PRTGVL 161.00] TO BUS 345534 [1PORTGVIL 34.500] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 500170 [CLARN 6 230.00] TO BUS 500570 [MESSICK6 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 344102 [7BELLEAU 345.00] TO BUS 344535 [7ENON 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 360023 [8FREEPORT TN500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 360040 [8CUMBERLAND 500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 360044 [8MONTGOMERY 500.00] TO BUS 360071 [8WILSON TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360086 [8WBNP #2 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 514908 [ARCADIA7 345.00] TO BUS 514943 [HSL 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100% | BUS 514943 [HSL 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 334204 [6CHINA 230.00] TO BUS 334327 [6AMELIA 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 335368 [8WELLS 500.00] TO BUS 335500 [8WEBRE 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 335642 [6ESSO 2 230.00] TO BUS 335643 [6G5EXXON 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 335836 [8MCKNT 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 337304 [6MONTGY 230.00] TO BUS 500170 [CLARN 6 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 337304 [6MONTGY 230.00] TO BUS 500200 [COLFAX 6 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338200 [5HAYTI 161.00] TO BUS 344720 [1HAYTI N 34.500] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 500200 [COLFAX 6 230.00] TO BUS 500770 [RODEMR 6 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 360010 [8RUTHERFORD 500.00] TO BUS 360050 [8MAURY TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 360052 [8BR FERRY NP500.00] TO BUS 360060 [8MADISON AL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 360086 [8WBNP #2 500.00] TO BUS 360687 [8WBNP #3 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 380004 [8BULLSLUI 500.00] TO BUS 380019 [8BIG SHANTY 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 380024 [8N TIFTON 500.00] TO BUS 382500 [8RACOONCK 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 384157 [8MILLER8 500.00] TO BUS 385312 [8CLAY 8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 384375 [8S.BESS 8 500.00] TO BUS 385123 [8BILLNGSS 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 508072 [NWTXARK7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 514809 [JOHNCO 345.00] TO BUS 515136 [SUNNYSD7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.1% | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 2 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 334325 [8HARTBRG 500.00] TO BUS 334370 [8COTNWD1 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 334370 [8COTNWD1 500.00] TO BUS 334372 [XMFRINT1 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 337515 [8MCNEIL 500.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.2% | BUS 337515 [8MCNEIL 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 337753 [8HSEHV 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 344088 [7BAILEY 345.00] TO BUS 345859 [7TYSON 2 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 360052 [8BR FERRY NP500.00] TO BUS 360088 [8LIMESTONE 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 360060 [8MADISON AL 500.00] TO BUS 360065 [8WID CRK FP 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360662 [8BRADLEY TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 360085 [8WBNP #1 500.00] TO BUS 360090 [8ROANE TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.2% | BUS 360662 [8BRADLEY TN 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 152 | 100.2% | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 337107 [6MOONLAK 230.00] TO BUS 337123 [6BATESV 230.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 337320 [3PLANT 115.00] TO BUS 337322 [3MURRLA 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 100.3% | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 300040 [7FLETCH 345.00] TO BUS 300047 [7SALEM 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 345669 [7RUSH 345.00] TO BUS 345858 [7TYSON 1 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 360033 [8UNION MS 500.00] TO BUS 360541 [8PLEASANT HL500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 360048 [8DAVIDSON TN500.00] TO BUS 360581 [8PIN HOOK TN500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 360541 [8PLEASANT HL500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 384157 [8MILLER8 500.00] TO BUS 384375 [8S.BESS 8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 384157 [8MILLER8 500.00] TO BUS 385307 [8WVERN SS 500.00] CKT 99 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 384512 [8SNOWDN8 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 385123 [8BILLNGSS 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.3% | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 334320 [8CYPRESS 500.00] TO BUS 334325 [8HARTBRG 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 336830 [8B.WLSN 500.00] TO BUS 337427 [8PERYVIL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 338200 [5HAYTI 161.00] TO BUS 338202 [5JIMHL 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 360065 [8WID CRK FP 500.00] TO BUS 360079 [8RACCOON MTN500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 360086 [8WBNP #2 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 383021 [8LONGLEAF 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.4% | BUS 510907 [PITTSB-7 345.00] TO BUS 514809 [JOHNCO 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 336562 [8FRKLIN 500.00] TO BUS 336820 [8G.GULF 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 344088 [7BAILEY 345.00] TO BUS 345669 [7RUSH 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 345088 [7MCCREDIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.5% | BUS 345088 [7MCCREDIE 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 338193 [5BLYINT 161.00] TO BUS 338200 [5HAYTI 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 300038 [7ESSEX 345.00] TO BUS 344974 [7LUTESVIL 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 344886 [7LABADIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 380021 [8MOSTELLE 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 506945 [CHAMSPR7 345.00] TO BUS 506959 [TONTITN7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.6% | BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 344102 [7BELLEAU 345.00] TO BUS 345747 [7SIOUX 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 360086 [8WBNP #2 500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.7% | BUS 360090 [8ROANE TN 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 360023 [8FREEPORT TN500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 360042 [8PARADISE FP500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.8% | BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 337950 [3JXNVL-N 115.00] TO BUS 338016 [3HOLBT-J 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 338015 [5HOLBT 161.00] TO BUS 338016 [3HOLBT-J 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 300045 [7MORGAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 153 | 100.9% | BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7CHOTEAU 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 382500 [8RACOONCK 500.00] TO BUS 383021 [8LONGLEAF 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101% | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101% | BUS 344154 [7BLAND 345.00] TO BUS 344886 [7LABADIE 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101% | BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101% | BUS 506935 [FLINTCR7 345.00] TO BUS 547481 [MON383 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 153 | 101% | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 2 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.1% | BUS 508298 [LYDIA 7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.2% | BUS 360037 [8JVILLE FP 500.00] TO BUS 360048 [8DAVIDSON TN500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.2% | BUS 360050 [8MAURY TN 500.00] TO BUS 360052 [8BR FERRY NP500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.2% | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.3% | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.3% | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.3% | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.3% | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.4% | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 152 | 101.5% | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.5% | BUS 300041 [7FRANKS 345.00] TO BUS 344154 [7BLAND 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.5% | BUS 300041 [7FRANKS 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.6% | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.6% | BUS 337562 [7ELDEHV 345.00] TO BUS 337569 [ 7SAREPT 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 154 | 101.6% | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.7% | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 154 | 101.7% | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.8% | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.8% | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.8% | BUS 337569 [ 7SAREPT 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.8% | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 101.9% | BUS 300038 [7ESSEX 345.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102% | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.1% | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 155 | 102.2% | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.4% | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.5% | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.6% | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.8% | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.9% | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 156 | 102.9% | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 156 | 102.9% | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 337957 [8KEO 50 500.00] TO BUS 338140 [8HOLBT 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 300041 [7FRANKS 345.00] TO BUS 300042 [7HUBEN 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103% | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 157 | 103.5% | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 157 | 103.8% | BUS 338140 [8HOLBT 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 158 | 103.9% | BUS 300040 [7FLETCH 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 162 | 106.6% | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 162 | 106.6% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 162 | 107.1% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 163 | 107.2% | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 164 | 108.1% | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 165 | 108.8% | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 167 | 109.9% | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 168 | 110.9% | BUS 338140 [8HOLBT 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 172 | 113.8% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
14W | 338130 5CALCR 161 | 338131 5MELBRN 161 1 | 148 | 173 | 114.1% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.9 | 100.2% | BUS 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.1% | 152.9 | 56.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.3% | BUS 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.1% | 152.9 | 56.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.2 | 100.4% | BUS 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 100.1% | 152.9 | 56.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.9 | 100.1% | BUS 338191 [5BLYELM 161.00] TO BUS 338193 [5BLYINT 161.00] CKT 1 | Blytheville Elm Street - Blyethville I-55 | 100.2% | 153 | 4.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 100.7% | 153.7 | 30.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.7 | 101.4% | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 100.7% | 153.7 | 30.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.6 | 100.6% | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 100.8% | 153.9 | 4.6
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.8 | 100.7% | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 100.8% | 153.9 | 4.6
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.6 | 100.5% | BUS 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 100.8% | 154.2 | 111.9
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.7 | 101.1% | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 100.8% | 154.2 | 111.9
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.8 | 101.2% | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 100.8% | 154.2 | 111.9
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.6 | 101.3% | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 101% | 154.2 | 5.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.8 | 101.4% | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 101% | 154.2 | 5.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.3 | 101.1% | BUS 338734 [5SHOFNR 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Newport | 101.2% | 154.4 | 2.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.4 | 101.2% | BUS 338151 [5NEWPO 161.00] TO BUS 338734 [5SHOFNR 161.00] CKT 1 | Bailey SES AECC - Newport | 101.2% | 154.4 | 2.3
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.9 | 100.9% | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 101.3% | 154.4 | 4.9
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154 | 101% | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 101.3% | 154.4 | 4.9
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.8 | 101.4% | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 101.3% | 154.6 | 24.4
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.2 | 101.7% | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 101.3% | 154.6 | 24.4
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.3 | 101.7% | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 101.6% | 155.1 | 36.4
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.6 | 102.6% | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 101.6% | 155.1 | 36.4
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.3 | 100.4% | BUS 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 102% | 155.8 | 70.5
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.4 | 100.5% | BUS 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 102% | 155.8 | 70.5
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.7 | 100.7% | BUS 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 102% | 155.8 | 70.5
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.8 | 101.4% | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.3 | 102.4% | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 158 | 103.5% | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 158.3 | 103.7% | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 161.8 | 106.1% | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 163.1 | 106.9% | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 164.1 | 107.6% | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 102.1% | 156 | 72.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155 | 101.6% | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 102.3% | 156 | 20.7
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.2 | 101.8% | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 102.3% | 156 | 20.7
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.9 | 102.2% | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 102.3% | 156 | 20.7
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.1 | 102.3% | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 102.3% | 156.1 | 0
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155 | 101.6% | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 102.4% | 156.2 | 19.6
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.6 | 102% | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 102.4% | 156.2 | 19.6
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.6 | 102.1% | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 102.4% | 156.2 | 19.6
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.3% | BUS 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 102.5% | 156.6 | 83.1
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 159 | 104.4% | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 104.9% | 159.8 | 23.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 159.4 | 104.6% | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 104.9% | 159.8 | 23.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 160.1 | 105.1% | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 104.9% | 159.8 | 23.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 160.8 | 105.6% | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 104.9% | 159.8 | 23.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 161.9 | 106.3% | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 104.9% | 159.8 | 23.2
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 163.4 | 107.5% | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 107.8% | 163.8 | 9.1
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 163.7 | 107.7% | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 107.8% | 163.8 | 9.1
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 164.3 | 108.1% | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 107.8% | 163.8 | 9.1
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.1 | 101.8% | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 108.2% | 164.7 | 0
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 165.2 | 108.4% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 109.3% | 166.7 | 26.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 165.9 | 108.8% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 109.3% | 166.7 | 26.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 166.6 | 109.3% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 109.3% | 166.7 | 26.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 167.3 | 109.7% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 109.3% | 166.7 | 26.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 159.4 | 104.5% | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 109.7% | 167.3 | 0
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.8 | 101.4% | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Norfork SPA - Bull Shoals Dam SPA | * | * | 118
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153 | 100.2% | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 140.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.3 | 100.4% | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | * | 140.8
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.5 | 101.8% | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | 186.1
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.2 | 100.4% | BUS 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.4 | 100.5% | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.6 | 100.6% | BUS 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.3 | 101.1% | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.8 | 101.4% | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 158.3 | 103.9% | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 174.4 | 114.7% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.6 | 100% | BUS 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.8 | 100% | BUS 344886 [7LABADIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.8 | 100% | BUS 345088 [7MCCREDIE 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.8 | 100% | BUS 384512 [8SNOWDN8 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.9 | 100.1% | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.8 | 100.1% | BUS 344102 [7BELLEAU 345.00] TO BUS 345747 [7SIOUX 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.9 | 100.1% | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.2% | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 152.9 | 100.2% | BUS 360023 [8FREEPORT TN500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153 | 100.2% | BUS 360042 [8PARADISE FP500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153 | 100.2% | BUS 382500 [8RACOONCK 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 99 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.2% | BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.2% | BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.3 | 100.3% | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.1 | 100.3% | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 2 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.3 | 100.4% | BUS 344154 [7BLAND 345.00] TO BUS 344886 [7LABADIE 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.3 | 100.4% | BUS 506935 [FLINTCR7 345.00] TO BUS 547481 [MON383 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.4 | 100.5% | BUS 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.5 | 100.5% | BUS 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.5 | 100.5% | BUS 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.5 | 100.5% | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.4 | 100.5% | BUS 360037 [8JVILLE FP 500.00] TO BUS 360048 [8DAVIDSON TN500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.6 | 100.6% | BUS 360050 [8MAURY TN 500.00] TO BUS 360052 [8BR FERRY NP500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.5 | 100.6% | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.7 | 100.6% | BUS 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.8 | 100.7% | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.8 | 100.7% | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.8 | 100.7% | BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.7 | 100.7% | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 153.7 | 100.7% | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154 | 100.9% | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.1 | 100.9% | BUS 508298 [LYDIA 7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.4 | 101.1% | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.6 | 101.3% | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.6 | 101.3% | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.9 | 101.5% | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 154.9 | 101.5% | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.2 | 101.6% | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.3 | 101.7% | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.2 | 101.7% | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.4 | 101.8% | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.5 | 101.9% | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.6 | 101.9% | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.7 | 102% | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.7 | 102% | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 155.8 | 102.1% | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.1 | 102.3% | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.5 | 102.6% | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 156.8 | 102.8% | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 161.2 | 105.7% | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 161.7 | 106.1% | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 161.6 | 106.1% | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 164.3 | 107.9% | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130 5CALCR 161 | 338131*5MELBRN 161 1 | 148 | 175.2 | 115.3% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 152.8 | 100.7% | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 101% | 153.2 | 9.1
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 153.1 | 100.9% | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 101% | 153.2 | 9.1
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 153.7 | 101.3% | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 101% | 153.2 | 9.1
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 154.5 | 101.5% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 102.5% | 156.1 | 26.8
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 155.2 | 101.9% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 102.5% | 156.1 | 26.8
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 155.9 | 102.4% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 102.5% | 156.1 | 26.8
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 156.6 | 102.9% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 102.5% | 156.1 | 26.8
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 163.5 | 107.6% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 153.5 | 100.9% | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA
10W | 338130*5CALCR 161 | 505448 NORFORK5 161 1 | 148 | 164.3 | 108.2% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 156 | 101.8% | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 101% | 155 | 14
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 154 | 100.8% | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 101.3% | 155 | 14
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 155 | 101.3% | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 101.3% | 155 | 14
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 158 | 103.4% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 105% | 160 | 35.1
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 159 | 104% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 105% | 160 | 35.1
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 160 | 104.7% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 105% | 160 | 35.1
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 160 | 105.2% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 105% | 160 | 35.1
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 165 | 108% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 155 | 101.5% | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 158 | 103.4% | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA
18S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 164 | 107.6% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10S | 338131 5MELBRN 161 | 338132*5SAGE * 161 1 | 148 | 155.9 | 100.7% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
10S | 338131 5MELBRN 161 | 338132*5SAGE * 161 1 | 148 | 157.3 | 101.7% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
14S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 158 | 102.4% | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA
14S | 338131 5MELBRN 161 | 338132 5SAGE * 161 1 | 148 | 157 | 102.4% | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA
18S | 338169 5TRUMAN 161 | 338707 5TRUM-W# 161 1 | 148 | 159 | 110.8% | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 111% | 159 | 35.1
18S | 338169 5TRUMAN 161 | 338707 5TRUM-W# 161 1 | 148 | 161 | 113% | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 111% | 159 | 35.1
18S | 338169 5TRUMAN 161 | 338707 5TRUM-W# 161 1 | 148 | 165 | 115.5% | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 111% | 159 | 35.1
18S | 338169 5TRUMAN 161 | 338707 5TRUM-W# 161 1 | 148 | 166 | 117.2% | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 111% | 159 | 35.1
18S | 338169 5TRUMAN 161 | 338707 5TRUM-W# 161 1 | 148 | 148 | 104.3% | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA
18S | 338422 5CONW-W 161 | 338424 5TYLER 161 1 | 223 | 215 | 100.2% | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 100% | 215 | 27
18S | 338422 5CONW-W 161 | 338424 5TYLER 161 1 | 223 | 230 | 108.3% | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 100% | 215 | 27
18S | 338422 5CONW-W 161 | 338424 5TYLER 161 1 | 223 | 215 | 100.2% | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA
18S | 338483 3NLR-DX 115 | 338487 3LAKEWD 115 1 | 159 | 170 | 108.8% | BUS 337930 [3MAYFL 115.00] TO BUS 337931 [3MORGAN 115.00] CKT 1 | Mayflower - N.L.R. Levy | * | * | 167
10S | 338682 5OSAGE # 161 | 506932*EUREKA 5 161 1 | 223 | 223.9 | 100.2% | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | * | * | 217.5
18S | 338813 5MIDWAY# 161 | 505460 BULL SH5 161 1 | 162 | 164 | 102.9% | BUS 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | 156.8
18S | 338814 5SOLAND# 161 | 505448 NORFORK5 161 1 | 162 | 165 | 105.9% | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | * | * | 156.8

## Draft Voltage
Contingency Scan - Voltages
Draft 2010-2012 Construction Plan Approved and Proposed Projects Included
Model | MONITORED | V-CONT | BUS TO BUS CON | BREAKER TO BREAKER | V-CONT | C-LOAD
10S | 334020 4BRYAN 138 | 1.0537 | BUS 334021 [4COLSTTA 138.00] TO BUS 334022 [4SPEEDWY 138.00] CKT 1 | Bryan-Navasota | NA | 0.1
10S | 334020 4BRYAN 138 | 1.0544 | BUS 334022 [4SPEEDWY 138.00] TO BUS 334023 [4NAVSOTA 138.00] CKT 1 | Bryan-Navasota | NA | 0.1
18S | 334084 4CLVELND 138 | 0.91965 | BUS 334084 [4CLVELND 138.00] TO BUS 334208 [4JACINTO 138.00] CKT 1 | Same | NA | NA
14S | 334111 4NEWCANY 138 | 0.91047 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334111 4NEWCANY 138 | 0.85733 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
14S | 334112 4HICKORY 138 | 0.91951 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334112 4HICKORY 138 | 0.8732 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334113 4EASTGAT 138 | 0.88978 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334114 4HUFFMAN 138 | 0.88598 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334115 6L533TP8 138 | 0.91332 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334116 4KLMP-EX 138 | 0.91329 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334209 4ROLKERD 138 | 0.91643 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334210 4ADAYTON 138 | 0.91736 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334211 4BDAYTON 138 | 0.91739 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
18S | 334216 4GORDON 138 | 0.91621 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
14W | 334283 4MILLCR 138 | 0.9068 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
18S | 334283 4MILLCR 138 | 0.91716 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334284 4PINELND 138 | 0.90997 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334285 4BROADUS 138 | 0.91125 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334286 4ETOIL 138 | 0.91168 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
14W | 334300 4PEACH 138 | 0.91528 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
18S | 334437 6KOLBS 230 | 0.91861 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
18S | 334438 6HANKS 230 | 0.91839 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
18S | 334439 6VFWPK 230 | 0.91773 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
14S | 335137 2PPC NO 69 | 0.88766 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
14W | 335137 2PPC NO 69 | 0.87173 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
18S | 335137 2PPC NO 69 | 0.89218 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
10S | 335137 2PPC NO 69 | 0.89984 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
10W | 335137 2PPC NO 69 | 0.87558 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
10S | 335379 4SCOTT1 138 | 0.91909 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335379 4SCOTT1 138 | 0.90912 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335380 4MEAUX 138 | 0.89162 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.90169 | 9.4
10S | 335380 4MEAUX 138 | 0.86469 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.88486 | 22.6
10S | 335380 4MEAUX 138 | 0.90819 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335380 4MEAUX 138 | 0.91118 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335380 4MEAUX 138 | 0.91248 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335385 4LEROY 138 | 0.88173 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.89194 | 9.4
10S | 335385 4LEROY 138 | 0.85632 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.87669 | 22.6
10S | 335385 4LEROY 138 | 0.90026 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335385 4LEROY 138 | 0.90327 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335385 4LEROY 138 | 0.91395 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335385 4LEROY 138 | 0.90458 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335385 4LEROY 138 | 0.91663 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10W | 335386 4ABBVIL 138 | 0.87646 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.88859 | 9.4
10S | 335386 4ABBVIL 138 | 0.84549 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 0.87069 | 22.6
10S | 335386 4ABBVIL 138 | 0.91775 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
10S | 335386 4ABBVIL 138 | 0.90618 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335386 4ABBVIL 138 | 0.91868 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335387 4DELCAMB 138 | 0.89938 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335388 4MORIL 138 | 0.90993 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335391 4CECELIA 138 | 0.91198 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
10S | 335391 4CECELIA 138 | 0.91439 | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA
10S | 335391 4CECELIA 138 | 0.90667 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
10S | 335391 4CECELIA 138 | 0.9172 | BUS 502410 [PMOUTON6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
18S | 335435 2CARNCRO 69 | 0.91825 | BUS 335346 [2SCOTT 69.000] TO BUS 335435 [2CARNCRO 69.000] CKT 1 | Same | NA | NA
18S | 335788 2BRADYH 69 | 0.87899 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
18S | 335788 2BRADYH 69 | 0.89468 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
18S | 335788 2BRADYH 69 | 0.91222 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
18S | 335789 2CLINTON 69 | 0.87818 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.9125 | 3
18S | 335789 2CLINTON 69 | 0.89388 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.9125 | 3
18S | 335789 2CLINTON 69 | 0.91144 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.9125 | 3
18S | 335790 2CLNTREA 69 | 0.87899 | BUS 335782 [2PTHUDSONA 69.000] TO BUS 335783 [2SANDYC 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
18S | 335790 2CLNTREA 69 | 0.89468 | BUS 335783 [2SANDYC 69.000] TO BUS 335784 [ 2GRAVEL 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
18S | 335790 2CLNTREA 69 | 0.91222 | BUS 335784 [ 2GRAVEL 69.000] TO BUS 335785 [2JACKSON 69.000] CKT 1 | Port Hudson - Jackson | 0.91328 | 3
14S | 336085 3ALLIA 115 | 0.43307 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
14W | 336085 3ALLIA 115 | 0.48933 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
18S | 336085 3ALLIA 115 | 0.45638 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10S | 336085 3ALLIA 115 | 0.46607 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10W | 336085 3ALLIA 115 | 0.50149 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
14S | 336092 3CARLSL 115 | 0.83723 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
14W | 336092 3CARLSL 115 | 0.85815 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
14S | 336092 3CARLSL 115 | 0.79543 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
14W | 336092 3CARLSL 115 | 0.81089 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
18S | 336092 3CARLSL 115 | 0.79952 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
18S | 336092 3CARLSL 115 | 0.83165 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
10S | 336092 3CARLSL 115 | 0.80455 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10S | 336092 3CARLSL 115 | 0.86495 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
10W | 336092 3CARLSL 115 | 0.81563 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
10W | 336092 3CARLSL 115 | 0.86582 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
18S | 336230 3CLAYTN 115 | 0.91203 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
18S | 336231 3NORCO 115 | 0.91456 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
10S | 336772 3HZLHST 115 | 0.91682 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.91694 | 8.8
10S | 336772 3HZLHST 115 | 0.8885 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.91694 | 8.8
10S | 336773 3COPHSW* 115 | 0.91501 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.91514 | 8.8
10S | 336773 3COPHSW* 115 | 0.88615 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.91514 | 8.8
10S | 336774 3GALLMAN 115 | 0.90794 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.90806 | 8.8
10S | 336774 3GALLMAN 115 | 0.87637 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.90806 | 8.8
10S | 336775 3CRYSPG 115 | 0.90155 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.90168 | 8.8
10S | 336775 3CRYSPG 115 | 0.86671 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.90168 | 8.8
10S | 336776 3TERRY 115 | 0.88515 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.88529 | 8.8
10S | 336776 3TERRY 115 | 0.84423 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.88529 | 8.8
10S | 336777 3BYRAM 115 | 0.88006 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 0.88021 | 8.8
10S | 336777 3BYRAM 115 | 0.83615 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 0.88021 | 8.8
18S | 336898 3MORTON 115 | 0.91876 | BUS 336897 [3PELAHE 115.00] TO BUS 336898 [3MORTON 115.00] CKT 1 | ?? | NA | NA
14S | 337010 8WOLFCRK 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
14W | 337010 8WOLFCRK 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
10S | 337010 8WOLFCRK 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
10W | 337010 8WOLFCRK 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
10W | 337011 6ATTALA 230 | 1.0573 | BUS 337000 [6MCADAM 230.00] TO BUS 337011 [6ATTALA 230.00] CKT 1 | Same | NA | NA
10S | 337061 3SAWYR* 115 | 0.914 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337062 3ELLIOT 115 | 0.88784 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337063 3S GREN 115 | 0.88409 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337064 3GRNADA 115 | 0.87811 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337065 3TILTOB 115 | 0.87005 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337066 3TVA-SHE 115 | 0.86915 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
10S | 337067 3CHRSTN 115 | 0.85929 | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA
14S | 337084 DELTA U2 69 | 1.0519 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337095 [3SHLBY* 115.00] CKT 1 | Delta SES - Clarksdale | 1.0519 | 11.7
14S | 337084 DELTA U2 69 | 1.0509 | BUS 337095 [3SHLBY* 115.00] TO BUS 337097 [3SHELBY-MS 115.00] CKT 1 | Delta SES - Clarksdale | 1.0519 | 11.7
14S | 337084 DELTA U2 69 | 1.0561 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0637 | 22.3
14S | 337084 DELTA U2 69 | 1.0636 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.0637 | 22.3
14S | 337084 DELTA U2 69 | 1.062 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0637 | 22.3
14S | 337084 DELTA U2 69 | 1.05 | BUS 336993 [3BLZONI 115.00] TO BUS 336994 [3ISOLA* 115.00] CKT 1 | Indianola - Yazoo | 1.0506 | 24.6
14S | 337084 DELTA U2 69 | 1.0502 | BUS 336995 [3INVER* 115.00] TO BUS 337051 [3INDIAN 115.00] CKT 1 | Indianola - Yazoo | 1.0506 | 24.6
14S | 337084 DELTA U2 69 | 1.0504 | BUS 337052 [3MORHED 115.00] TO BUS 337053 [3I.BENA 115.00] CKT 1 | Indianola - Greenwood | 1.0546 | 27.7
14S | 337084 DELTA U2 69 | 1.0519 | BUS 337053 [3I.BENA 115.00] TO BUS 337054 [3GRNWOD 115.00] CKT 1 | Indianola - Greenwood | 1.0546 | 27.7
14S | 337084 DELTA U2 69 | 1.0516 | BUS 337000 [6MCADAM 230.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA
14S | 337084 DELTA U2 69 | 1.0505 | BUS 337056 [3CRLTN* 115.00] TO BUS 337057 [3CARLTN 115.00] CKT 1 | Same | NA | NA
14S | 337084 DELTA U2 69 | 1.0537 | BUS 337086 [3CLEVND 115.00] TO BUS 337087 [3S CLEV 115.00] CKT 1 | Same | NA | NA
14S | 337084 DELTA U2 69 | 1.05 | BUS 336864 [6CANTONS 230.00] TO BUS 336866 [6CANTON 230.00] CKT 1 | South Canton - Pickens | 1.0508 | 49.9
14S | 337084 DELTA U2 69 | 1.0508 | BUS 336866 [6CANTON 230.00] TO BUS 337015 [6PICKNS 230.00] CKT 1 | South Canton - Pickens | 1.0508 | 49.9
14S | 337084 DELTA U2 69 | 1.052 | BUS 337080 [3PACE 1 115.00] TO BUS 337081 [3WCLEVLD 115.00] CKT 1 | Delta SES - North Greenville | 1.057 | 35.4
14S | 337084 DELTA U2 69 | 1.0563 | BUS 337081 [3WCLEVLD 115.00] TO BUS 337085 [3DELTA-MS 115.00] CKT 1 | Delta SES - North Greenville | 1.057 | 35.4
14S | 337084 DELTA U2 69 | 1.0567 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Batesville - Delta SES | 1.057 | 31.2
14S | 337084 DELTA U2 69 | 1.0533 | BUS 337113 [3DREWMS 115.00] TO BUS 337115 [3WEBB 1 115.00] CKT 1 | Batesville - Delta SES | 1.057 | 31.2
14S | 337084 DELTA U2 69 | 1.0506 | BUS 337115 [3WEBB 1 115.00] TO BUS 337116 [3MARKS 115.00] CKT 1 | Batesville - Delta SES | 1.057 | 31.2
14S | 337084 DELTA U2 69 | 1.0511 | BUS 337116 [3MARKS 115.00] TO BUS 337126 [3BATESV 115.00] CKT 1 | Batesville - Delta SES | 1.057 | 31.2
10S | 337084 DELTA U2 69 | 1.0512 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0589 | 28.2
10S | 337084 DELTA U2 69 | 1.0572 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.0589 | 28.2
10S | 337084 DELTA U2 69 | 1.0555 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.0589 | 28.2
10S | 337084 DELTA U2 69 | 1.0509 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Delta SES - Batesville | 1.0511 | 30.4
18S | 337084 DELTA U2 69 | 1.052 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.06 | 31
18S | 337084 DELTA U2 69 | 1.0609 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 1.06 | 31
18S | 337084 DELTA U2 69 | 1.0593 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 1.06 | 31
18S | 337084 DELTA U2 69 | 1.0508 | BUS 337033 [3KSCUKO 115.00] TO BUS 337060 [3WINONA 115.00] CKT 1 | Attala - Winona | 1.0504 | 31.4
18S | 337084 DELTA U2 69 | 1.0512 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Batesville - Delta SES | 1.052 | 31.9
18S | 337084 DELTA U2 69 | 1.0516 | BUS 337081 [3WCLEVLD 115.00] TO BUS 337085 [3DELTA-MS 115.00] CKT 1 | Delta SES - North Greenville | 1.052 | 36.8
18S | 337136 3SNTOBI 115 | 0.89932 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337137 3CLDWTR 115 | 0.88167 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337138 3HRNADO 115 | 0.91437 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337138 3HRNADO 115 | 0.8638 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337138 3HRNADO 115 | 0.91669 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337139 3GETWEL 115 | 0.91424 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337139 3GETWEL 115 | 0.86552 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337139 3GETWEL 115 | 0.91389 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337140 6GETWELL 230 | 0.91634 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337140 6GETWELL 230 | 0.87128 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337140 6GETWELL 230 | 0.91135 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337141 3NESBT* 115 | 0.91187 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337141 3NESBT* 115 | 0.86198 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337141 3NESBT* 115 | 0.91305 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337142 3NESBIT 115 | 0.90943 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337142 3NESBIT 115 | 0.85877 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337142 3NESBIT 115 | 0.9111 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337143 3PLUM PT 115 | 0.91116 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337143 3PLUM PT 115 | 0.86067 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337143 3PLUM PT 115 | 0.9135 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
14S | 337144 3GRNBRK 115 | 0.91589 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337144 3GRNBRK 115 | 0.86748 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337144 3GRNBRK 115 | 0.91772 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337150 3HN LAK 115 | 0.88377 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337151 3DESOTO-MS 115 | 0.88752 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337152 3WALLS 115 | 0.90385 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
18S | 337180 6HN LAK 230 | 0.87896 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337180 6HN LAK 230 | 0.91205 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
10S | 337366 3HAYNVL 115 | 0.85468 | BUS 337516 [3MCNEIL 115.00] TO BUS 337522 [3MAG-E 115.00] CKT 1 | McNeil - Emerson |  | 41.2
14S | 337368 8MTOLIV 500 | 1.0697 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
14W | 337368 8MTOLIV 500 | 1.0723 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
18S | 337368 8MTOLIV 500 | 1.0718 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
10S | 337368 8MTOLIV 500 | 1.0685 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
10W | 337368 8MTOLIV 500 | 1.0666 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
10S | 337522 3MAG-E 115 | 0.81585 | BUS 337516 [3MCNEIL 115.00] TO BUS 337522 [3MAG-E 115.00] CKT 1 | McNeil - Emerson |  | 41.2
10S | 337523 3MAG-ST 115 | 0.81994 | BUS 337516 [3MCNEIL 115.00] TO BUS 337522 [3MAG-E 115.00] CKT 1 | McNeil - Emerson |  | 41.2
10S | 337524 3KERLIN* 115 | 0.8217 | BUS 337516 [3MCNEIL 115.00] TO BUS 337522 [3MAG-E 115.00] CKT 1 | McNeil - Emerson |  | 41.2
10S | 337525 3KERLIN 115 | 0.82154 | BUS 337516 [3MCNEIL 115.00] TO BUS 337522 [3MAG-E 115.00] CKT 1 | McNeil - Emerson |  | 41.2
18S | 337555 3T.E. F 115 | 0.91447 | BUS 337539 [3ELDEHV 115.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
14S | 337967 3RICUS 115 | 1.0527 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0542 | 25.8
14W | 337967 3RICUS 115 | 1.0523 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0571 | 25.8
14W | 337967 3RICUS 115 | 1.0525 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0571 | 25.8
14W | 337967 3RICUS 115 | 1.0533 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0571 | 25.8
14W | 337967 3RICUS 115 | 1.0561 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0571 | 25.8
14W | 337967 3RICUS 115 | 1.0535 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0571 | 25.8
10W | 337967 3RICUS 115 | 1.0568 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0569 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0576 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0504 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0599 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0577 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0608 | 22.8
10W | 337967 3RICUS 115 | 1.0527 | BUS 337967 [3RICUS 115.00] TO BUS 337972 [3ALMYRA 115.00] CKT 1 | Stuttgart Ricuskey - Gillett | 1.0529 | 29.5
10S | 337967 3RICUS 115 | 1.0506 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0567 | 31.1
10S | 337967 3RICUS 115 | 1.0508 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0567 | 31.1
10S | 337967 3RICUS 115 | 1.052 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0567 | 31.1
10S | 337967 3RICUS 115 | 1.0554 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0567 | 31.1
10S | 337967 3RICUS 115 | 1.0522 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0567 | 31.1
10W | 337967 3RICUS 115 | 1.0513 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | NA | NA
10W | 337967 3RICUS 115 | 1.0507 | BUS 337627 [3PB-IP* 115.00] TO BUS 337628 [3PB-IP 115.00] CKT 1 | Same | NA | NA
10W | 337969 3STUTT-I 115 | 1.0511 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0549 | 22.8
10W | 337969 3STUTT-I 115 | 1.0512 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0549 | 22.8
10W | 337969 3STUTT-I 115 | 1.0518 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0549 | 22.8
10W | 337969 3STUTT-I 115 | 1.054 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0549 | 22.8
10W | 337969 3STUTT-I 115 | 1.052 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0549 | 22.8
10W | 337970 3ULM 11 115 | 1.0504 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0512 | 22.8
18S | 337981 3MARVEL 115 | 0.91545 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337982 3BARTON 115 | 0.91194 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337983 3HELN-W* 115 | 0.9089 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 337984 3HELN-C 115 | 0.90725 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
14S | 338006 3CABOT 115 | 0.9086 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338006 3CABOT 115 | 0.90908 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338006 3CABOT 115 | 0.85767 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338006 3CABOT 115 | 0.85818 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338007 3BEEBE 115 | 0.91551 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338007 3BEEBE 115 | 0.91586 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338007 3BEEBE 115 | 0.87125 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338007 3BEEBE 115 | 0.87163 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338008 3GARNER* 115 | 0.89085 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338008 3GARNER* 115 | 0.89115 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338009 3T.E.MC 115 | 0.89071 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338009 3T.E.MC 115 | 0.89102 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338017 3HOLBT-C 115 | 0.85819 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338017 3HOLBT-C 115 | 0.90909 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338050 3T.E.#6 115 | 0.91914 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338050 3T.E.#6 115 | 0.91925 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338205 3PARAG 115 | 1.0597 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0598 | 16.7
14S | 338205 3PARAG 115 | 1.059 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0598 | 16.7
14S | 338205 3PARAG 115 | 1.0586 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0598 | 16.7
14S | 338205 3PARAG 115 | 1.0593 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0598 | 16.7
14S | 338205 3PARAG 115 | 1.0517 | BUS 338170 [5JONES 161.00] TO BUS 338703 [5JONE-N# 161.00] CKT 1 | Jonesboro - Paragould | 1.0536 | 21.5
14S | 338205 3PARAG 115 | 1.0534 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0536 | 21.5
14S | 338205 3PARAG 115 | 1.0522 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0536 | 21.5
14S | 338205 3PARAG 115 | 1.0598 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338205 3PARAG 115 | 1.0588 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 3PARAG 115 | 1.0581 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 3PARAG 115 | 1.0578 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 3PARAG 115 | 1.0584 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0588 | 15.7
10S | 338205 3PARAG 115 | 1.0534 | BUS 338170 [5JONES 161.00] TO BUS 338703 [5JONE-N# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
10S | 338205 3PARAG 115 | 1.0545 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
10S | 338205 3PARAG 115 | 1.0534 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 1.0546 | 17.5
18S | 338205 3PARAG 115 | 1.0514 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0515 | 18.6
18S | 338205 3PARAG 115 | 1.0503 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0515 | 18.6
18S | 338205 3PARAG 115 | 1.0508 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 1.0515 | 18.6
18S | 338205 3PARAG 115 | 1.0511 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338205 3PARAG 115 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338206 3SEDGWK* 115 | 1.0592 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338206 3SEDGWK* 115 | 1.0679 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
18S | 338206 3SEDGWK* 115 | 1.0502 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338206 3SEDGWK* 115 | 1.0586 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338206 3SEDGWK* 115 | 1.0649 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338207 3T.E.#7 115 | 1.0576 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338207 3T.E.#7 115 | 1.0663 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338207 3T.E.#7 115 | 1.0571 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338207 3T.E.#7 115 | 1.0633 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 338208 3WALNUT 115 | 1.0595 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338208 3WALNUT 115 | 1.0681 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
18S | 338208 3WALNUT 115 | 1.0505 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338208 3WALNUT 115 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338208 3WALNUT 115 | 1.0651 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338552 HARRISON-S1 69 | 1.0525 | BUS 338104 [5HARR-E 161.00] TO BUS 338105 [5OMAHA * 161.00] CKT 1 | Ozark Beach - Harrison East | 1.0528 | 9.4
10S | 338552 HARRISON-S1 69 | 1.0509 | BUS 338105 [5OMAHA * 161.00] TO BUS 547474 [OZD312 5 161.00] CKT 1 | Ozark Beach - Harrison East | 1.0528 | 9.4
14W | 338552 HARRISON-S1 69 | 1.0538 | BUS 338101 [5GR FOR 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 1.0526 | 0
14W | 338552 HARRISON-S1 69 | 1.0557 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 1.0526 | 0
14W | 338552 HARRISON-S1 69 | 1.0521 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | 1.0526 | 0
14W | 338552 HARRISON-S1 69 | 1.0539 | BUS 338104 [5HARR-E 161.00] TO BUS 338105 [5OMAHA * 161.00] CKT 1 | Ozark Beach - Harrison East | 1.0542 | 7.6
14W | 338552 HARRISON-S1 69 | 1.053 | BUS 338105 [5OMAHA * 161.00] TO BUS 547474 [OZD312 5 161.00] CKT 1 | Ozark Beach - Harrison East | 1.0542 | 7.6
14W | 338552 HARRISON-S1 69 | 1.0504 | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 1.0503 | 78.7
18S | 338570 BLACKROCK1 69 | 1.0658 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 1.0675 | 14
18S | 338570 BLACKROCK1 69 | 1.0661 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0675 | 14
18S | 338570 BLACKROCK1 69 | 1.0676 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0675 | 14
10W | 338570 BLACKROCK1 69 | 1.0508 | BUS 338144 [8ISXF 5 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA
14W | 338570 BLACKROCK1 69 | 1.0523 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 1.0519 | 9.6
14W | 338570 BLACKROCK1 69 | 1.0516 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0519 | 9.6
14W | 338570 BLACKROCK1 69 | 1.0519 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 1.0519 | 9.6
10W | 338578 OPPELO 69 | 1.0506 | BUS 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 OPPELO 69 | 1.0506 | BUS 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 OPPELO 69 | 1.05 | BUS 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 1.0511 | 21.4
10W | 338578 OPPELO 69 | 1.0501 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 OPPELO 69 | 1.0501 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 OPPELO 69 | 1.0501 | BUS 337940 [5HAMLET* 161.00] TO BUS 337941 [5HAMLT 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0535 | 140.8
10W | 338578 OPPELO 69 | 1.0512 | BUS 337826 [3LR-PIN 115.00] TO BUS 337829 [5LR-PIN 161.00] CKT 1 | Same | NA | NA
14S | 338581 DELUCE1 69 | 1.0548 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.055 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.056 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.0505 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.059 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.0562 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0603 | 25.8
14S | 338581 DELUCE1 69 | 1.0508 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | NA | NA
18S | 338581 DELUCE1 69 | 1.0536 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 38.9
18S | 338581 DELUCE1 69 | 1.0502 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 1.0551 | 38.9
18S | 338583 WARD1 69 | 0.87774 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338583 WARD1 69 | 0.87823 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14W | 338585 HEBERSP1 69 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 1.0544 | 78.7
14W | 338585 HEBERSP1 69 | 1.0544 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0544 | 78.7
14W | 338585 HEBERSP1 69 | 1.0536 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 1.0544 | 78.7
14W | 338585 HEBERSP1 69 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0545 | 164.1
14W | 338585 HEBERSP1 69 | 1.0532 | BUS 337939 [5GOLDCR* 161.00] TO BUS 337940 [5HAMLET* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0545 | 164.1
14W | 338585 HEBERSP1 69 | 1.0509 | BUS 337940 [5HAMLET* 161.00] TO BUS 337941 [5HAMLT 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0545 | 164.1
10S | 338585 HEBERSP1 69 | 1.0546 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 1.0547 | 188.3
18S | 337367 3ARCADIA 115 | 0.9 | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | * | 101
14S | 338585 HEBERSP1 69 | 1.0546 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14W | 338585 HEBERSP1 69 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14W | 338585 HEBERSP1 69 | 1.0545 | BUS 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14W | 338585 HEBERSP1 69 | 1.0547 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 102.2
14S | 338007 3BEEBE 115 | 0.91726 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 103.5
14S | 338756 3WARD # 115 | 0.90215 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 103.5
14S | 338704 3LIGHT # 115 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338704 3LIGHT # 115 | 1.0675 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338756 3WARD # 115 | 0.91799 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 103.5
10W | 338578 OPPELO 69 | 1.0503 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 111.9
14S | 337801 3BENT-S* 115 | 0.91347 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 113.9
14S | 337802 3BAUXIT 115 | 0.89482 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 113.9
10S | 338704 3LIGHT # 115 | 1.0583 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338704 3LIGHT # 115 | 1.0645 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14S | 337803 3BRYANT 115 | 0.89135 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 113.9
14S | 338757 3BRYNTS# 115 | 0.89223 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 113.9
18S | 338007 3BEEBE 115 | 0.89249 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 119
18S | 338008 3GARNER* 115 | 0.91172 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 119
18S | 338009 3T.E.MC 115 | 0.91159 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 119
18S | 338583 WARD1 69 | 0.89704 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 119
14S | 338710 3CRO-RG# 115 | 1.059 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
14W | 338710 3CRO-RG# 115 | 1.0676 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
18S | 338756 3WARD # 115 | 0.87462 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | * | 119
18S | 338160 5EBON S* 161 | 0.91853 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338410 5WM-DOV 161 | 0.91701 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338411 5WM-GAT 161 | 0.91723 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338413 5WM-LH2 161 | 0.91629 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338414 5WM-POK 161 | 0.9125 | BUS 338161 [5WM-EHV 161.00] TO BUS 338414 [5WM-POK 161.00] CKT 1 | Kuhn Road - West Memphis EHV | * | 119.1
18S | 338112 5HEBR-S 161 | 0.91077 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
18S | 338710 3CRO-RG# 115 | 1.0501 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10S | 338710 3CRO-RG# 115 | 1.0584 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
10W | 338710 3CRO-RG# 115 | 1.0644 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
18S | 338113 5HEBR-I 161 | 0.90869 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
18S | 338758 5HEBR-N# 161 | 0.90685 | BUS 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | * | 126.3
10S | 337802 3BAUXIT 115 | 0.90981 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
10S | 337803 3BRYANT 115 | 0.90691 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
10S | 338757 3BRYNTS# 115 | 0.90766 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 135
18S | 337136 3SNTOBI 115 | 0.85286 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
18S | 337137 3CLDWTR 115 | 0.82533 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
14S | 338756 3WARD # 115 | 0.90584 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
14S | 338756 3WARD # 115 | 0.90628 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 337138 3HRNADO 115 | 0.79518 | BUS 337138 [3HRNADO 115.00] TO BUS 337139 [3GETWEL 115.00] CKT 1 | Batesville - Getwell | * | 158.6
18S | 338756 3WARD # 115 | 0.8558 | BUS 338006 [3CABOT 115.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 338756 3WARD # 115 | 0.85627 | BUS 338015 [5HOLBT 161.00] TO BUS 338017 [3HOLBT-C 115.00] CKT 1 | Same | NA | NA
18S | 337800 3HASKEL 115 | 0.91912 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 337801 3BENT-S* 115 | 0.89738 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 337802 3BAUXIT 115 | 0.87571 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 337803 3BRYANT 115 | 0.87156 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 338757 3BRYNTS# 115 | 0.8726 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
18S | 338757 3BRYNTS# 115 | 0.91937 | BUS 337803 [3BRYANT 115.00] TO BUS 338757 [3BRYNTS# 115.00] CKT 1 | Mabelvale - Hot Springs EHV | * | 167.4
10S | 338552 HARRISON-S1 69 | 1.0523 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | * | 217.5
18S | 338420 5DONAGHE 161 | 0.90093 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338421 5CONW-S 161 | 0.90186 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338423 5CONIND 161 | 0.90324 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | * | 247
18S | 338880 3HELN-I 115 | 0.90693 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
18S | 37010 8WOLFCRK 500 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA

## LH Sys Int
Low Hydro System Intact
Thermal Overlads [%, MVA]
| From Bus |  |  | To Bus |  |  | Circuit | Model | 2010S |  | 2014S |  | 2018S
| No. | Name | kV | No. | Name | kV |  |  | Overload | Flow | Overload | Flow | Overload | Flow
| 335094 | 2MOSSVL | 69 | 335102 | 2CANAL-LA | 69 | 1 | Base+CP |  |  |  |  | 102 | 38
[8 empty] | Base+CP+ 50% SPA |  |  |  |  | 102 | 38
[8 empty] | Base+CP+BullSh off |  |  |  |  | 102 | 38
[8 empty] | Base+CP+GF off |  |  |  |  | 102 | 38
| 335346 | 2SCOTT | 69 | 503304 | RAYNE 2 | 69 | 1 | Base+CP |  |  |  |  | 105.3 | 21
[8 empty] | Base+CP+ 50% SPA |  |  |  |  | 105.3 | 21
[8 empty] | Base+CP+BullSh off |  |  |  |  | 105.3 | 21
[8 empty] | Base+CP+GF off |  |  |  |  | 105.3 | 21
| 335411 | 2HOLIDAY | 69 | 335412 | 2LAFAYET | 69 | 1 | Base+CP | 103.5 | 40 | 107.9 | 41 | 117.1 | 45
[8 empty] | Base+CP+ 50% SPA | 103.6 | 40 | 107.9 | 41 | 117.1 | 45
[8 empty] | Base+CP+BullSh off | 103.6 | 40 | 107.9 | 41 | 117.1 | 45
[8 empty] | Base+CP+GF off | 103.6 | 40 | 107.9 | 41 | 117.1 | 45
| 335781 | 2ZAC REA | 69 | 335782 | 2PTHUDSONA | 69 | 1 | Base+CP |  |  | 101.3 | 91 | 114 | 101
[8 empty] | Base+CP+ 50% SPA |  |  | 101.3 | 91 | 114 | 101
[8 empty] | Base+CP+BullSh off |  |  | 101.3 | 91 | 114 | 101
[8 empty] | Base+CP+GF off |  |  | 101.3 | 91 | 114 | 101
| 338130 | 5CALCR | 161 | 338131 | 5MELBRN | 161 | 1 | Base+CP
[8 empty] | Base+CP+ 50% SPA |  |  |  |  | 105 | 159
[8 empty] | Base+CP+BullSh off |  |  | 102.4 | 153 | 107.8 | 159
Base+CP+GF off
| 338130 | 5CALCR | 161 | 505448 | NORFORK5 | 161 | 1 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  |  |  | 104.4 | 151
Base+CP+GF off
| 338131 | 5MELBRN | 161 | 338132 | 5SAGE * | 161 | 1 | Base+CP
[8 empty] | Base+CP+ 50% SPA |  |  | 106.3 | 163 | 112.6 | 171
[8 empty] | Base+CP+BullSh off | 105.3 | 160 | 109.2 | 164 | 115.7 | 172
Base+CP+GF off
Voltage Overloads [pu]
[5 empty] | To Bus |  |  | Model | 2010S | 2014S | 2018S
[5 empty] | No. | Name | kV |  | Voltage | Voltage | Voltage
[5 empty] | 334000 | 2CALVERT | 69 | Base+CP | 0.9307 | 0.9179 | 0.9111
[8 empty] | Base+CP+ 50% SPA | 0.9307 | 0.918
[8 empty] | Base+CP+BullSh off | 0.9307 | 0.918 | 0.9111
[8 empty] | Base+CP+GF off | 0.9308 | 0.918 | 0.9111
[5 empty] | 334001 | 2SINHERN | 69 | Base+CP |  | 0.9428 | 0.9379
[8 empty] | Base+CP+ 50% SPA |  | 0.9428
[8 empty] | Base+CP+BullSh off |  | 0.9428 | 0.9379
[8 empty] | Base+CP+GF off |  | 0.9428 | 0.9379
[5 empty] | 334681 | 3NECHESO | 69 | Base+CP | 0.9445 | 0.94 | 0.9362
[8 empty] | Base+CP+ 50% SPA | 0.9445 | 0.94
[8 empty] | Base+CP+BullSh off | 0.9445 | 0.94 | 0.9362
[8 empty] | Base+CP+GF off | 0.9445 | 0.94 | 0.9362
[5 empty] | 335275 | 2LKARTHR | 69 | Base+CP |  | 0.946 | 0.9404
[8 empty] | Base+CP+ 50% SPA |  | 0.946
[8 empty] | Base+CP+BullSh off |  | 0.946 | 0.9404
[8 empty] | Base+CP+GF off |  | 0.946 | 0.9404
[5 empty] | 335276 | 2KLONDKE | 69 | Base+CP |  | 0.9491 | 0.9436
[8 empty] | Base+CP+ 50% SPA |  | 0.9491
[8 empty] | Base+CP+BullSh off |  | 0.9491 | 0.9436
[8 empty] | Base+CP+GF off |  | 0.9491 | 0.9436
[5 empty] | 335379 | 4SCOTT1 | 138 | Base+CP | 0.9499 | 0.9369
[8 empty] | Base+CP+ 50% SPA |  | 0.9369
[8 empty] | Base+CP+BullSh off | 0.9498 | 0.9369
[8 empty] | Base+CP+GF off | 0.9498 | 0.9369
[5 empty] | 335380 | 4MEAUX | 138 | Base+CP | 0.9342 | 0.9152 | 0.9358
[8 empty] | Base+CP+ 50% SPA | 0.9344 | 0.9152
[8 empty] | Base+CP+BullSh off | 0.9341 | 0.9152 | 0.9358
[8 empty] | Base+CP+GF off | 0.9341 | 0.9152 | 0.9358
[5 empty] | 335385 | 4LEROY | 138 | Base+CP | 0.9265 | 0.906 | 0.9255
[8 empty] | Base+CP+ 50% SPA | 0.9267 | 0.906
[8 empty] | Base+CP+BullSh off | 0.9264 | 0.906 | 0.9255
[8 empty] | Base+CP+GF off | 0.9264 | 0.906 | 0.9255
[5 empty] | 335386 | 4ABBVIL | 138 | Base+CP | 0.9429 | 0.9242 | 0.939
[8 empty] | Base+CP+ 50% SPA | 0.9431 | 0.9242
[8 empty] | Base+CP+BullSh off | 0.9429 | 0.9242 | 0.939
[8 empty] | Base+CP+GF off | 0.9429 | 0.9242 | 0.939
[5 empty] | 335387 | 4DELCAMB | 138 | Base+CP |  | 0.9338 | 0.9421
[8 empty] | Base+CP+ 50% SPA |  | 0.9338
[8 empty] | Base+CP+BullSh off |  | 0.9338 | 0.9421
[8 empty] | Base+CP+GF off |  | 0.9338 | 0.9421
[5 empty] | 335391 | 4CECELIA | 138 | Base+CP | 0.941 | 0.9297 | 0.9389
[8 empty] | Base+CP+ 50% SPA | 0.9412 | 0.9297
[8 empty] | Base+CP+BullSh off | 0.941 | 0.9297 | 0.9389
[8 empty] | Base+CP+GF off | 0.941 | 0.9297 | 0.9389
[5 empty] | 337181 | 5HN LAK | 161 | Base+CP | 1.0605 | 1.0596 | 1.0555
[8 empty] | Base+CP+ 50% SPA | 1.0605 | 1.0596
[8 empty] | Base+CP+BullSh off | 1.0605 | 1.0596 | 1.0555
[8 empty] | Base+CP+GF off | 1.0605 | 1.0595 | 1.0555
[5 empty] | 338112 | 5HEBR-S | 161 | Base+CP
Base+CP+ 50% SPA
Base+CP+BullSh off
[8 empty] | Base+CP+GF off |  |  | 0.9386
[5 empty] | 338113 | 5HEBR-I | 161 | Base+CP
Base+CP+ 50% SPA
Base+CP+BullSh off
[8 empty] | Base+CP+GF off |  |  | 0.9375
[5 empty] | 338123 | 5BULLSH* | 161 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9489
Base+CP+GF off
[5 empty] | 338124 | 5BULLSH | 161 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9488
Base+CP+GF off
[5 empty] | 338125 | 5MT HOM | 161 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.941
Base+CP+GF off
[5 empty] | 338581 | DELUCE1 | 69 | Base+CP | 1.0515
[8 empty] | Base+CP+ 50% SPA | 1.0515
[8 empty] | Base+CP+BullSh off | 1.0514
[8 empty] | Base+CP+GF off | 1.0515
[5 empty] | 338606 | MIDWAY-JD1 | 69 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9367
Base+CP+GF off
[5 empty] | 338608 | MIDWAY-JD2 | 69 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9367
Base+CP+GF off
[5 empty] | 338758 | 5HEBR-N# | 161 | Base+CP
Base+CP+ 50% SPA
Base+CP+BullSh off
[8 empty] | Base+CP+GF off |  |  | 0.9366
[5 empty] | 338813 | 5MIDWAY# | 161 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9367
Base+CP+GF off
[5 empty] | 338814 | 5SOLAND# | 161 | Base+CP
Base+CP+ 50% SPA
[8 empty] | Base+CP+BullSh off |  |  | 0.9434
Base+CP+GF off

## LH Thermal
Low Hydro Contingency Scan - Thermal Overloads
Approved 2009-2011 Construction Plan Projects Included
Model | MONITORED ELEMENT | To Bus | Contingency | Breaker to Breaker | Cload | Base | Base + 50% SPA |  | Base + BullSh off |  | Base + GF off |  | Worst
18S | 337705 3CHEETA* 115.00 | 337707 3HS-VIL 115.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  |  |  | 100.5% | 104MVA |  |  | x
10S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 25.1 |  | 101.2% | 223MVA
14S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 |  | 108.1% | 237MVA |  |  | 111.8% | 244MVA | x
10S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA |  | 101.2% | 223MVA |  |  | 103.6% | 227MVA | x
14S | 337925 5GREENB 161.00 | 337926 5QUITMN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 | [5 empty] | 102.3% | 223MVA
18S | 337925 5GREENB 161.00 | 337926 5QUITMN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 104.6% | 226MVA |  |  | 109.2% | 228MVA
14S | 337925 5GREENB 161.00 | 337926 5QUITMN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 102.8% | 226MVA |  |  | 108% | 230MVA | x
18S | 337925 5GREENB 161.00 | 337926 5QUITMN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 111.1% | 238MVA | 104.7% | 218MVA | 116.1% | 240MVA | x
14S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 | [5 empty] | 107.5% | 234MVA | x
18S | 337928 3CONW-W 115.00 | 337929 3LK CON 115.00 1 | 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 101.6% | 234MVA |  |  | 103.7% | 237MVA
18S | 337928 3CONW-W 115.00 | 337929 3LK CON 115.00 1 | 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 111.1% | 253MVA |  |  | 113.3% | 257MVA | x
18S | 337928 3CONW-W 115.00 | 337929 3LK CON 115.00 1 | 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 108.9% | 249MVA |  |  | 111.1% | 252MVA
18S | 337928 3CONW-W 115.00 | 338422 5CONW-W 161.00 1 | 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 104.5% | 234MVA | 102.2% | 229MVA | 106% | 237MVA
18S | 337928 3CONW-W 115.00 | 338422 5CONW-W 161.00 1 | 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 113.1% | 253MVA | 110.9% | 248MVA | 114.6% | 257MVA | x
18S | 337928 3CONW-W 115.00 | 338422 5CONW-W 161.00 1 | 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 39.9 |  | 111.2% | 249MVA | 108.9% | 244MVA | 112.7% | 252MVA
14S | 337929 3LK CON 115.00 | 337930 3MAYFL 115.00 1 | 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 36.8 | [5 empty] | 102.2% | 244MVA
14S | 337929 3LK CON 115.00 | 337930 3MAYFL 115.00 1 | 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 36.8 | [5 empty] | 110.8% | 263MVA | x
14S | 337929 3LK CON 115.00 | 337930 3MAYFL 115.00 1 | 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 36.8 | [5 empty] | 108.6% | 259MVA
14S | 337929 3LK CON 115.00 | 337930 3MAYFL 115.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 104% | 249MVA | 102.1% | 244MVA | 105.9% | 252MVA | x
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 | [5 empty] | 100.1% | 281MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 |  | 100.1% | 281MVA | 100% | 281MVA | 100.2% | 281MVA | x
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337936 [3SYLVN 115.00] TO BUS 338486 [3SHERWD 115.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  |  | 100% | 281MVA | 100.1% | 281MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337800 [3HASKEL 115.00] TO BUS 337801 [3BENT-S* 115.00] CKT 1 | Hot Springs EHV - Mabelvale | 167 |  | 100.1% | 282MVA |  |  | 100.2% | 282MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337648 [3WH BLF 115.00] TO BUS 337859 [3WRIGHTS 115.00] CKT 1 | Same | NA | [5 empty] | 100% | 281MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 337808 [8MABEL 500.00] TO BUS 337909 [8ANO 50 500.00] CKT 1 | Same | NA | [5 empty] | 100.1% | 281MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | [5 empty] | 100.1% | 281MVA
18S | 337930 3MAYFL 115.00 | 337931 3MORGAN 115.00 1 | 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 118.8 |  | 100% | 281MVA |  |  | 100.2% | 282MVA
18S | 337936 3SYLVN 115.00 | 337938 5SYLVN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 | [5 empty] | 100.1% | 140MVA
18S | 337936 3SYLVN 115.00 | 337938 5SYLVN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 106.8% | 149MVA | 102.4% | 143MVA | 112.3% | 157MVA | x
18S | 337938 5SYLVN 161.00 | 338748 5GRAVEL# 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 | [5 empty] | 104.6% | 137MVA
18S | 337938 5SYLVN 161.00 | 338748 5GRAVEL# 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 111.6% | 146MVA | 107.1% | 140MVA | 117.8% | 153MVA | x
18S | 337939 5GOLDCR* 161.00 | 337940 5HAMLET* 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  |  | 100.6% | 206MVA | 101.4% | 207MVA | x
18S | 338100 5BERRYV 161.00 | 338101 5GR FOR 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  |  | 101.9% | 166MVA |  |  | x
18S | 338101 5GR FOR 161.00 | 338103 5GRFORS 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  |  | 105% | 174MVA |  |  | x
18S | 338102 5HARR-W 161.00 | 338103 5GRFORS 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  |  | 112.4% | 187MVA |  |  | x
18S | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 101.9% | 156MVA | 108.9% | 151MVA |  |  | x
14S | 338108 5ST_JOE 161.00 | 338110 5HILLTOP 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  |  |  | 102.4% | 157MVA |  |  | x
18S | 338125 5MT HOM 161.00 | 338814 5SOLAND# 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  |  | 102.8% | 147MVA
18S | 338125 5MT HOM 161.00 | 338814 5SOLAND# 161.00 1 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156.8 |  | 101.2% | 155MVA | 105.3% | 155MVA | 100% | 155MVA | x
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 109.6% | 165MVA | 114.8% | 173MVA |  |  | x
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 108.2% | 162MVA | 113.7% | 171MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 105.3% | 159MVA | 110.3% | 166MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 104.9% | 158MVA | 109.9% | 166MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 104.3% | 157MVA | 109.2% | 165MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 50.2 |  |  |  | 109.1% | 164MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 103.7% | 157MVA | 108.7% | 164MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 103.2% | 156MVA | 108.5% | 164MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 103.1% | 156MVA | 108.3% | 163MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 102.7% | 155MVA | 107.9% | 163MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 102.3% | 155MVA | 107.6% | 163MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 107.5% | 162MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 50.2 |  |  |  | 107.3% | 162MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 106.8% | 161MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA |  | 101.1% | 153MVA | 106.6% | 161MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 101.3% | 153MVA | 106.1% | 160MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 106% | 160MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  |  |  | 106% | 160MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  |  |  | 105% | 159MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  |  |  | 104.8% | 158MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  |  |  | 104.7% | 157MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  |  |  | 104.4% | 158MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 103.9% | 157MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  |  |  | 103.8% | 157MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 103.7% | 157MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  |  |  | 103.5% | 157MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  |  |  | 103.1% | 156MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 27.5 |  |  |  | 102.9% | 156MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 102.8% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  |  |  | 102.7% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  |  |  | 102.7% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6.2 |  |  |  | 102.4% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 49.2 |  |  |  | 102.4% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 32.9 |  |  |  | 102.3% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6.2 |  |  |  | 102.3% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 27.5 |  |  |  | 102.3% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  |  |  | 102.2% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA |  |  |  | 102.2% | 155MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 27.5 |  |  |  | 102.1% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  |  |  | 102.1% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 32.9 |  |  |  | 101.9% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 40.9 |  |  |  | 101.9% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  |  |  | 101.9% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  |  |  | 101.8% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  |  |  | 101.8% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  |  |  | 101.7% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  |  |  | 101.7% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  |  |  | 101.7% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  |  |  | 101.6% | 154MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 6.6 |  |  |  | 101.4% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  |  |  | 101.4% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  |  |  | 101.4% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 49.2 |  |  |  | 101.3% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 7.9 |  |  |  | 101.3% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 6.6 |  |  |  | 101.3% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 40.9 |  |  |  | 101.3% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  |  |  | 101.3% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  |  |  | 101.2% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  |  |  | 101.2% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 0 |  |  |  | 101.1% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 7.9 |  |  |  | 101.1% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA |  |  |  | 101.1% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  |  |  | 100.9% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  |  |  | 100.9% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  |  |  | 100.9% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  |  |  | 100.9% | 153MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  |  |  | 100.7% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  |  | 100.7% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 98 |  |  |  | 100.7% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 25.1 |  |  |  | 100.6% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  |  |  | 100.6% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  |  |  | 100.5% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA |  |  |  | 100.5% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 98 |  |  |  | 100.5% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 25.1 |  |  |  | 100.4% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  |  |  | 100.4% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  |  |  | 100.4% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA |  |  |  | 100.4% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338100 [5BERRYV 161.00] TO BUS 338682 [5OSAGE # 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  |  |  | 100.3% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  |  |  | 100.2% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 2.4 |  |  |  | 100.2% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 2.4 |  |  |  | 100.2% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA |  |  |  | 100.2% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337686 [3ARKLA 115.00] TO BUS 337690 [3CATH4 115.00] CKT 1 | Same | NA |  |  |  | 100.2% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA |  |  |  | 100.1% | 151MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338191 [5BLYELM 161.00] TO BUS 338193 [5BLYINT 161.00] CKT 1 | Same | NA |  |  |  | 100.1% | 152MVA
10S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 23.7 |  |  |  | 100% | 151MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338020 [5BRNK-E 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley West - Moses SES | 25.7 |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337717 [3HS-S 1 115.00] TO BUS 337718 [3CARPE 115.00] CKT 1 | Carpenter Dam - Blakely SPA | 134.5 |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337345 [3DANVLL 115.00] TO BUS 337348 [6DANVLL 230.00] CKT 1 | Same | NA |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337348 [6DANVLL 230.00] TO BUS 337375 [6GRAMBL 230.00] CKT 1 | Same | NA |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337369 [6MTOLIV 230.00] TO BUS 337375 [6GRAMBL 230.00] CKT 1 | Same | NA |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337672 [4MURFRE 138.00] TO BUS 337673 [3MURF-S 115.00] CKT 1 | Same | NA |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337804 [3MABEL 115.00] TO BUS 337825 [3KANIS * 115.00] CKT 1 | Same | NA |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337818 [3LR-S 1 115.00] TO BUS 338749 [3IRNTON# 115.00] CKT 1 | Wrightsville EHV IPP - L. R. South | 9.4 |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337859 [3WRIGHTS 115.00] TO BUS 338749 [3IRNTON# 115.00] CKT 1 | Wrightsville EHV IPP - L. R. South | 9.4 |  | 100% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337996 [3BRNK-E 115.00] TO BUS 338001 [3DEVALL 115.00] CKT 1 | Brinkley East - Lynch | 59.1 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338001 [3DEVALL 115.00] TO BUS 338002 [3HAZEN 115.00] CKT 1 | Brinkley East - Lynch | 59.1 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337695 [3TIGRE * 115.00] TO BUS 337697 [3PANTH * 115.00] CKT 1 | Cheetah - Arklahoma | 22.2 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337697 [3PANTH * 115.00] TO BUS 337705 [3CHEETA* 115.00] CKT 1 | Cheetah - Arklahoma | 22.2 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337939 [5GOLDCR* 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337900 [3OLA 11 115.00] TO BUS 337901 [3DANVI 115.00] CKT 1 | Danville - Cheetah | 45.8 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337901 [3DANVI 115.00] TO BUS 337902 [5DANVI 161.00] CKT 1 | Danville - Cheetah | 45.8 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337801 [3BENT-S* 115.00] TO BUS 338431 [3BENT-S 115.00] CKT 1 | Hot Springs EHV - Mabelvale | 150 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337802 [3BAUXIT 115.00] TO BUS 338433 [3ALCOA 115.00] CKT 1 | Hot Springs EHV - Mabelvale | 150 |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337859 [3WRIGHTS 115.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338200 [5HAYTI 161.00] TO BUS 338202 [5JIMHL 161.00] CKT 1 | Same | NA |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338201 [5PRTGVL 161.00] TO BUS 345534 [1PORTGVIL 34.500] CKT 1 | Same | NA |  | 100.1% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 25.7 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337686 [3ARKLA 115.00] TO BUS 337695 [3TIGRE * 115.00] CKT 1 | Cheetah - Arklahoma | 22.2 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.2% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337707 [3HS-VIL 115.00] TO BUS 338743 [3HOLLIS# 115.00] CKT 1 | Danville - Cheetah | 45.8 |  | 100.2% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337900 [3OLA 11 115.00] TO BUS 338743 [3HOLLIS# 115.00] CKT 1 | Danville - Cheetah | 45.8 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338160 [5EBON S* 161.00] TO BUS 338410 [5WM-DOV 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 114.9 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338160 [5EBON S* 161.00] TO BUS 338411 [5WM-GAT 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 114.9 |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337515 [8MCNEIL 500.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338193 [5BLYINT 161.00] TO BUS 338200 [5HAYTI 161.00] CKT 1 | Same | NA |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338200 [5HAYTI 161.00] TO BUS 344720 [1HAYTI N 34.500] CKT 1 | Same | NA |  | 100.2% | 153MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 68.4 |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337808 [8MABEL 500.00] CKT 1 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69.000] CKT 1 | Vienna - Ruston | 74 |  | 100.3% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338100 [5BERRYV 161.00] TO BUS 338682 [5OSAGE # 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 100.5% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337686 [3ARKLA 115.00] TO BUS 337690 [3CATH4 115.00] CKT 1 | Same | NA |  | 100.5% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 33.3 |  | 100.6% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA |  | 100.6% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 2.3 |  | 100.6% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 100.7% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337705 [3CHEETA* 115.00] TO BUS 337707 [3HS-VIL 115.00] CKT 1 | Danville - Cheetah | 45.8 |  | 100.7% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 2.3 |  | 100.7% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 33.3 |  | 100.8% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 33.3 |  | 100.8% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 107.9 |  | 100.8% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 26 |  | 100.9% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  | 100.9% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA |  | 100.9% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  | 100.9% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 68.4 |  | 101% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 26 |  | 101.1% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 68.4 |  | 101.1% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 107.9 |  | 101.1% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 101.2% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA |  | 101.2% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 68.4 |  | 101.3% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 89.1 |  | 101.3% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 0 |  | 101.4% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 101.4% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337562 [7ELDEHV 345.00] TO BUS 337569 [ 7SAREPT 345.00] CKT 1 | Same | NA |  | 101.4% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 89.1 |  | 101.4% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 8.3 |  | 101.5% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 101.5% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  | 101.5% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 8.3 |  | 101.6% | 155MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 89.1 |  | 101.6% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 0 |  | 101.6% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 139.5 |  | 101.7% | 154MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 6.9 |  | 101.7% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  | 101.7% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48.6 |  | 101.8% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 6.9 |  | 101.8% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  | 101.8% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  | 101.8% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA |  | 101.8% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 |  | 101.9% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  | 101.9% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 102% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  | 102% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  | 102.1% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  | 102.1% | 156MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 30.4 |  | 102.3% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  | 102.3% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 33.8 |  | 102.4% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6 |  | 102.4% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6 |  | 102.5% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  | 102.5% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  | 102.5% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  | 102.5% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  | 102.6% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 30.4 |  | 102.6% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  | 102.7% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 33.8 |  | 102.8% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48.6 |  | 102.8% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 |  | 102.8% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 102.9% | 157MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 103% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  | 103.2% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 30.4 |  | 103.2% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 103.3% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  | 103.3% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  | 104.1% | 159MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  | 104.4% | 160MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 104.5% | 158MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  | 105% | 161MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  | 105.1% | 161MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 0 |  | 105.2% | 161MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 105.3% | 161MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  | 105.7% | 162MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 106.2% | 162MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 106.6% | 163MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  | 106.7% | 163MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  | 106.8% | 163MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA |  | 107.1% | 164MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 52.6 |  | 107.2% | 164MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 108.4% | 166MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 52.6 |  | 108.7% | 166MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 108.8% | 166MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 109.4% | 167MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 109.4% | 167MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 109.8% | 168MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 110.4% | 169MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 111.1% | 170MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 111.5% | 170MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 113.7% | 173MVA
14S | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 113.9% | 174MVA |  |  |  |  | x
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 102.1% | 154MVA | 109.9% | 163MVA |  |  | x
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 101% | 151MVA | 109.2% | 161MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  |  |  | 105.6% | 157MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  |  |  | 105.2% | 156MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  |  |  | 104.6% | 155MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  |  |  | 104% | 155MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  |  |  | 103.8% | 154MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  |  |  | 103.7% | 155MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  |  |  | 103.2% | 154MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  |  |  | 102.8% | 153MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  |  |  | 101.5% | 151MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  |  |  | 101.1% | 148MVA
10S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  |  |  | 100.3% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 107.9% | 162MVA | 112.2% | 163MVA |  |  | x
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 107.7% | 163MVA | 111.8% | 163MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 105.5% | 160MVA | 109.4% | 160MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 105.1% | 159MVA | 109% | 159MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 52.6 |  |  |  | 108.4% | 158MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 104.4% | 158MVA | 108.3% | 158MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 34 |  | 103.8% | 157MVA | 107.8% | 158MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 103.5% | 156MVA | 107.7% | 157MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 103.2% | 157MVA | 107.4% | 158MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 102.6% | 156MVA | 106.9% | 157MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 52.6 |  |  |  | 106.8% | 156MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 106.6% | 155MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 |  | 102.3% | 155MVA | 106.5% | 156MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 105.9% | 154MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  |  |  | 105.6% | 151MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  |  |  | 105.3% | 154MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 104.9% | 153MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 100.7% | 153MVA | 104.7% | 153MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  |  |  | 104.2% | 153MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  |  |  | 103.6% | 152MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  |  |  | 103.5% | 152MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 0 |  |  |  | 103.2% | 152MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  |  |  | 103% | 151MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 31.6 |  |  |  | 102.7% | 151MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 102.6% | 150MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 102.4% | 150MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  |  |  | 102% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  |  |  | 101.7% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  |  |  | 101.7% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 30.4 |  |  |  | 101.7% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  |  |  | 101.5% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48.6 |  |  |  | 101.4% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 101.4% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 |  |  |  | 101.4% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 33.8 |  |  |  | 101.3% | 149MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  |  |  | 101.2% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  |  |  | 101.2% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6 |  |  |  | 101.1% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 26.9 |  |  |  | 101.1% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 30.4 |  |  |  | 101.1% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  |  |  | 101% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  |  |  | 101% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 33.8 |  |  |  | 100.9% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6 |  |  |  | 100.9% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 30.4 |  |  |  | 100.9% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  |  |  | 100.8% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  |  |  | 100.8% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  |  |  | 100.6% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  |  |  | 100.5% | 148MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA |  |  |  | 100.5% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 6.9 |  |  |  | 100.4% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  |  |  | 100.4% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  |  |  | 100.4% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 60.1 |  |  |  | 100.4% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48.6 |  |  |  | 100.3% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 74.1 |  |  |  | 100.3% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 6.9 |  |  |  | 100.3% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  |  |  | 100.3% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 89.1 |  |  |  | 100.3% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  |  |  | 100.2% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 0 |  |  |  | 100.2% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 0 |  |  |  | 100.1% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  |  | 100.1% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337562 [7ELDEHV 345.00] TO BUS 337569 [ 7SAREPT 345.00] CKT 1 | Same | NA |  |  |  | 100.1% | 147MVA
14S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 137.4 |  |  |  | 100.1% | 147MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 100% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA |  | 100% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA |  | 100% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 100.1% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337939 [5GOLDCR* 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 100.1% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338100 [5BERRYV 161.00] TO BUS 338682 [5OSAGE # 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 100.1% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 100.1% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69.000] CKT 1 | Vienna - Ruston | 78 |  | 100.1% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA |  | 100.2% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337808 [8MABEL 500.00] CKT 1 | Same | NA |  | 100.2% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 100.3% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 100.3% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 34 |  | 100.4% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 71.7 |  | 100.4% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337686 [3ARKLA 115.00] TO BUS 337690 [3CATH4 115.00] CKT 1 | Same | NA |  | 100.4% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 2.3 |  | 100.5% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 2.3 |  | 100.5% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337562 [7ELDEHV 345.00] TO BUS 337569 [ 7SAREPT 345.00] CKT 1 | Same | NA |  | 100.5% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 118.8 |  | 100.5% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 0 |  | 100.6% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 100.6% | 150MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 34 |  | 100.6% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 34 |  | 100.7% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  | 100.7% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  | 100.8% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA |  | 100.8% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 118.8 |  | 100.8% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 27 |  | 100.9% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA |  | 100.9% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 71.7 |  | 101% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 98 |  | 101% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 98 |  | 101.1% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 0 |  | 101.1% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 27 |  | 101.2% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 71.7 |  | 101.2% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  | 101.2% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 154.6 |  | 101.2% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 101.3% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 8.8 |  | 101.3% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 71.7 |  | 101.4% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 101.4% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 101.4% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA |  | 101.4% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 98 |  | 101.4% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 8.8 |  | 101.5% | 151MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 7.1 |  | 101.5% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  | 101.5% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 7.1 |  | 101.6% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  | 101.6% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  | 101.6% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  | 101.6% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 5.8 |  | 101.7% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  | 101.7% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  | 101.7% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48 |  | 101.8% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  | 101.8% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 88.2 |  | 101.8% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  | 101.8% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 5.8 |  | 101.9% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 33.5 |  | 101.9% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 33.5 |  | 102.1% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 102.2% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  | 102.2% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 |  | 102.3% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 154.6 |  | 102.3% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 154.6 |  | 102.3% | 153MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 102.5% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 102.7% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 |  | 102.8% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 33.5 |  | 102.8% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48 |  | 102.9% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 102.9% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 102.9% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 103.1% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 103.3% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 88.2 |  | 103.3% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  | 103.3% | 154MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156.8 |  | 103.4% | 152MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 103.6% | 155MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 104% | 156MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  | 104.4% | 156MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 104.6% | 156MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 105.1% | 157MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 105.2% | 157MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 0 |  | 105.5% | 158MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 106.2% | 158MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 106.4% | 159MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 106.6% | 155MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  | 106.9% | 159MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 56.4 |  | 107.3% | 160MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 108.1% | 162MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 108.5% | 162MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 56.4 |  | 108.8% | 162MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 108.9% | 162MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 109.1% | 163MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 110.3% | 164MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 110.9% | 165MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 111.6% | 166MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 112.1% | 167MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 114.8% | 171MVA
18S | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 115.2% | 170MVA |  |  |  |  | x
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338160 [5EBON S* 161.00] TO BUS 338410 [5WM-DOV 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 111 |  | 100% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA |  | 100% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337808 [8MABEL 500.00] CKT 1 | Same | NA |  | 100% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337672 [4MURFRE 138.00] TO BUS 337673 [3MURF-S 115.00] CKT 1 | Same | NA |  | 100% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338011 [3GRIFTH 115.00] CKT 1 | Searcy Price - Brinkley East | 24.2 |  | 100% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 188.3 |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337515 [8MCNEIL 500.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA |  | 100.1% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 23.7 |  | 100.2% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69.000] CKT 1 | Vienna - Ruston | 72 |  | 100.2% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  | 100.3% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA |  | 100.3% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA |  | 100.3% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 188.3 |  | 100.4% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 2.4 |  | 100.4% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 2.4 |  | 100.4% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 123.4 |  | 100.4% | 150MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337686 [3ARKLA 115.00] TO BUS 337690 [3CATH4 115.00] CKT 1 | Same | NA |  | 100.4% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  | 100.5% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 25.1 |  | 100.6% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 32.6 |  | 100.6% | 152MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  | 100.6% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA |  | 100.6% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  | 100.7% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  | 100.7% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 98 |  | 100.7% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 25.1 |  | 100.8% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 188.3 |  | 100.8% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA |  | 100.8% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 64.9 |  | 100.9% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 98 |  | 100.9% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 188.3 |  | 101% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  | 101% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  | 101.1% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  | 101.1% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  | 101.1% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 0 |  | 101.1% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | 500 kV El Dorado EHV - 345 kV El Dorado EHV - Longwood | 0 |  | 101.2% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 7.9 |  | 101.2% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA |  | 101.2% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 7.9 |  | 101.3% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 101.3% | 153MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  | 101.4% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 80.9 |  | 101.4% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 49.2 |  | 101.5% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  | 101.6% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  | 101.6% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 40.9 |  | 101.6% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  | 101.7% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  | 101.8% | 154MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA |  | 101.9% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 121.4 |  | 102% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 32.9 |  | 102.1% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 40.9 |  | 102.2% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 27.5 |  | 102.3% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  | 102.4% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 102.4% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA |  | 102.4% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 32.9 |  | 102.5% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6.2 |  | 102.5% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 49.2 |  | 102.5% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 27.5 |  | 102.6% | 155MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 6.2 |  | 102.7% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  | 102.9% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 25.9 |  | 102.9% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 103% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 103.2% | 157MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 27.5 |  | 103.2% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  | 103.5% | 157MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  | 103.6% | 156MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  | 103.7% | 157MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  | 104.3% | 158MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 0 |  | 104.6% | 159MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  | 104.9% | 159MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 105% | 159MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  | 105.1% | 159MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 105.8% | 160MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 30.1 |  | 105.9% | 160MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 50.2 |  | 106.1% | 161MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 68.5 |  | 106.4% | 161MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA |  | 106.6% | 161MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 106.7% | 162MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 50.2 |  | 107.6% | 163MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 107.8% | 163MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 108.1% | 164MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 108.6% | 164MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 12.6 |  | 108.7% | 165MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 109.2% | 165MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 109.8% | 166MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 110.4% | 167MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 32.9 |  | 110.8% | 168MVA |  |  |  |  | x
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 106% | 329MVA | 106.5% | 330MVA |  |  | x
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 106.2% | 329MVA | 106.5% | 330MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 104.8% | 325MVA | 105% | 326MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 104.6% | 324MVA | 104.8% | 325MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 104.3% | 323MVA | 104.5% | 324MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 35.1 |  | 104% | 322MVA | 104.2% | 323MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 103.5% | 321MVA | 103.9% | 322MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 56.4 |  | 103.2% | 320MVA | 103.9% | 322MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 103.3% | 320MVA | 103.6% | 321MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA |  | 103.2% | 320MVA | 103.5% | 321MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 |  | 103.1% | 319MVA | 103.4% | 320MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 56.4 |  | 102.5% | 318MVA | 103.2% | 320MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 102.9% | 319MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA |  | 102.4% | 317MVA | 102.8% | 319MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 102.6% | 318MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 102.1% | 317MVA | 102.5% | 318MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 102.1% | 317MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 100.9% | 313MVA | 102% | 316MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 101.6% | 315MVA | 102% | 316MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 0 |  | 101.7% | 315MVA | 101.9% | 316MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 101.3% | 314MVA | 101.7% | 315MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA |  | 101.1% | 314MVA | 101.4% | 314MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 101% | 313MVA | 101.4% | 314MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 32.9 |  | 100.8% | 313MVA | 101.2% | 314MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 101.1% | 313MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 100.9% | 313MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA |  | 100.6% | 312MVA | 100.8% | 313MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA |  | 100.5% | 312MVA | 100.8% | 313MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48 |  |  |  | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA |  |  |  | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 100.4% | 311MVA | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 100.4% | 311MVA | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 33.5 |  | 100.4% | 311MVA | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  | 100.4% | 311MVA | 100.7% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 |  | 100.3% | 311MVA | 100.6% | 312MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 34.7 |  | 100.1% | 310MVA | 100.4% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 79.7 |  |  |  | 100.4% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 28 |  | 100.1% | 310MVA | 100.4% | 311MVA
14S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA |  | 100.3% | 311MVA | 100.4% | 311MVA |  |  | x
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA |  | 100.1% | 310MVA | 100.4% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 154.6 |  | 100.1% | 310MVA | 100.4% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 154.6 |  | 100.1% | 310MVA | 100.4% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 33.5 |  | 100% | 310MVA | 100.3% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 5.8 |  |  |  | 100.2% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 48 |  |  |  | 100.2% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA |  |  |  | 100.2% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 33.5 |  |  |  | 100.2% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA |  |  |  | 100.2% | 311MVA
14S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  | 100.1% | 310MVA | 100.2% | 311MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 5.8 |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 7.1 |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA |  |  |  | 100.1% | 310MVA
18S | 338138 5MORFLD 161.00 | 338142 5ISES 1 161.00 1 | 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 7.1 |  |  |  | 100% | 310MVA
10S | 338186 5MONETE 161.00 | 338204 5PARAG 161.00 1 | 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | [5 empty] | 101.1% | 150MVA | x
14S | 338422 5CONW-W 161.00 | 338424 5TYLER 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | [5 empty] | 101.1% | 218MVA | x
18S | 338814 5SOLAND# 161.00 | 505448 NORFORK5 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  |  | 109.3% | 157MVA |  |  | x
18S | 338814 5SOLAND# 161.00 | 505448 NORFORK5 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA |  |  |  | 104% | 156MVA

## LH > 5% Thermal
Low Hydro Contingency Scan - Thermal Overloads Impacted by More than 5%
Approved 2009-2011 Construction Plan Projects Included
Model | MONITORED ELEMENT - From Bus | To Bus | Contingency | Breaker to Breaker | Cload | Base+CP |  | Base+CP+ 50% SPA |  | Base+CP+BullSh off |  | Base+CP+GF off |  | Worst
18S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 27 | 132.9% | 283MVA | 138% | 293MVA |  |  |  |  | x
18S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 27 | 124.6% | 267MVA | 129.7% | 277MVA
18S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | 124.6% | 267MVA | 129.7% | 277MVA |  |  | 132.7% | 281MVA | x
18S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 88.2 | 115.6% | 251MVA | 122.2% | 264MVA
18S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 88.2 | 100.4% | 219MVA | 106.7% | 232MVA
14S | 337921 5MOR-E 161.00 | 337927 5GLEASN 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | 111% | 242MVA |  |  |  |  | 118.4% | 256MVA | x
18S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 27 | 120.3% | 258MVA | 125.4% | 267MVA
18S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 27 | 128.6% | 273MVA | 133.7% | 283MVA |  |  |  |  | x
18S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 88.2 | 111.4% | 241MVA | 117.9% | 254MVA
18S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | 120.3% | 258MVA | 125.4% | 267MVA |  |  | 128.4% | 272MVA | x
14S | 337927 5GLEASN 161.00 | 338424 5TYLER 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | 106.8% | 232MVA |  |  |  |  | 114.1% | 246MVA | x
18S | 337928 3CONW-W 115.00 | 337929 3LK CON 115.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | 101.9% | 235MVA | 107.1% | 246MVA |  |  | 108.6% | 247MVA | x
18S | 337928 3CONW-W 115.00 | 338422 5CONW-W 161.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | 104.7% | 235MVA |  |  |  |  | 110.4% | 247MVA | x
18S | 337929 3LK CON 115.00 | 337930 3MAYFL 115.00 1 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | 113.5% | 269MVA | 118.8% | 281MVA |  |  | 120.3% | 284MVA | x
14S | 338102 5HARR-W 161.00 | 338681 5HARR-S 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 | 106.2% | 228MVA |  |  | 115.5% | 228MVA |  |  | x
18S | 338102 5HARR-W 161.00 | 338681 5HARR-S 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 122.8% | 249MVA |  |  | 143.6% | 254MVA |  |  | x
10S | 338104 5HARR-E 161.00 | 338681 5HARR-S 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 | 101.1% | 225MVA |  |  | 107.3% | 226MVA |  |  | x
14S | 338104 5HARR-E 161.00 | 338681 5HARR-S 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 | 114.1% | 247MVA |  |  | 124.1% | 247MVA |  |  | x
18S | 338104 5HARR-E 161.00 | 338681 5HARR-S 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 132.1% | 270MVA |  |  | 154.1% | 277MVA |  |  | x
18S | 338108 5ST_JOE 161.00 | 338110 5HILLTOP 161.00 1 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 100.4% | 158MVA | 107.6% | 166MVA | 115.2% | 165MVA |  |  | x
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | 100.8% | 156MVA | 113.7% | 171MVA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | 101.7% | 157MVA | 115.1% | 174MVA |  |  |  |  | x
18S | 338422 5CONW-W 161.00 | 338424 5TYLER 161.00 1 | 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | 105.8% | 226MVA | 110.8% | 236MVA |  |  | 113.6% | 240MVA | x
18S | 338814 5SOLAND# 161.00 | 505448 NORFORK5 161.00 1 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156.8 | 106% | 165MVA |  |  | 111.7% | 165MVA |  |  | x

## LH Voltage
Low Hydro Contingency Scan - Voltages
Approved 2009-2011 Construction Plan Projects Included
Model | BUS | Contingency | Breaker to Breaker | Cload | 10S+CP+ 50% SPA | 10S+CP+BullSh off | 10S+CP+GF off | Worst
18S | 337939 5GOLDCR* 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.91386 | x
18S | 337940 5HAMLET* 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.9132 | x
18S | 337941 5HAMLT 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.91317 | x
14S | 338100 5BERRYV 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 | 0.91637 | 0.84695 |  | x
10S | 338100 5BERRYV 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  | 0.90703 |  | x
14S | 338101 5GR FOR 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.85702 |  | x
10S | 338101 5GR FOR 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  | 0.91527 |  | x
14S | 338102 5HARR-W 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.88426 |  | x
14S | 338103 5GRFORS 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.85865 |  | x
10S | 338103 5GRFORS 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  | 0.91611 |  | x
18S | 338104 5HARR-E 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 0.91051 | 0.83087 |  | x
14S | 338104 5HARR-E 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.90358 |  | x
18S | 338105 5OMAHA * 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.8701 |  | x
18S | 338106 5OMAHA 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.87009 |  | x
18S | 338107 5EVRTON 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 0.91603 | 0.84204 |  | x
14S | 338107 5EVRTON 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.9084 |  | x
18S | 338108 5ST_JOE 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.85671 |  | x
14S | 338108 5ST_JOE 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.91593 |  | x
18S | 338109 5MARSHL 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.88191 |  | x
18S | 338110 5HILLTOP 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.87649 |  | x
18S | 338112 5HEBR-S 161.00 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  |  | 0.91607
14S | 338112 5HEBR-S 161.00 | 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.77158 | x
18S | 338112 5HEBR-S 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.91307 | x
18S | 338112 5HEBR-S 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.90389
14S | 338113 5HEBR-I 161.00 | 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.77169
14S | 338113 5HEBR-I 161.00 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.80224 | x
14S | 338113 5HEBR-I 161.00 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  | 0.91986 |  | x
18S | 338113 5HEBR-I 161.00 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  |  | 0.91512
18S | 338113 5HEBR-I 161.00 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  |  | 0.63526
18S | 338113 5HEBR-I 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.91217 | x
18S | 338113 5HEBR-I 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.90307
18S | 338120 5LEAD HL 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.90699 |  | x
18S | 338121 5SUMMIT 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.86565 |  | x
18S | 338122 5FLIPN 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.8786 |  | x
18S | 338123 5BULLSH* 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.88641 |  | x
18S | 338124 5BULLSH 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.88635 |  | x
18S | 338125 5MT HOM 161.00 | 338125 [5MT HOM 161.00] TO BUS 338814 [5SOLAND# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.90074
18S | 338125 5MT HOM 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.886
18S | 338125 5MT HOM 161.00 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.90988 |  | x
18S | 338125 5MT HOM 161.00 | 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89497
10S | 338161 5WM-EHV 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91979 | x
10S | 338410 5WM-DOV 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.9191 | x
18S | 338410 5WM-DOV 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91958 | x
10S | 338411 5WM-GAT 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91913 | x
18S | 338411 5WM-GAT 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.9198 | x
10S | 338413 5WM-LH2 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91945 | x
10S | 338414 5WM-POK 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91865 | x
18S | 338414 5WM-POK 161.00 | 338161 [5WM-EHV 161.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA |  |  | 0.91935 | x
14S | 338420 5DONAGHE 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 | 0.91954 | 0.91295 | 0.9052 | x
14S | 338421 5CONW-S 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 0.91377 | 0.90602 | x
14S | 338423 5CONIND 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 218.5 |  | 0.91499 | 0.90726 | x
18S | 338552 HARRISON-S1 69.000 | 338100 [5BERRYV 161.00] TO BUS 338101 [5GR FOR 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  |  | 1.0508 | x
18S | 338552 HARRISON-S1 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 | 0.91758 | 0.8277 |  | x
14S | 338552 HARRISON-S1 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.91359 |  | x
14S | 338554 OSAGE-CR1 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.86455 |  | x
14S | 338556 OSAGE-CR2 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.86455 |  | x
14S | 338570 BLACKROCK1 69.000 | 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 13.3 | 1.0692 |  |  | x
18S | 338585 HEBERSP1 69.000 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  |  | 0.65189
18S | 338585 HEBERSP1 69.000 | 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  |  | 0.78177 | x
18S | 338585 HEBERSP1 69.000 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  | 0.90858 |  | x
14S | 338585 HEBERSP1 69.000 | 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.79185
14S | 338585 HEBERSP1 69.000 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.82306
14S | 338585 HEBERSP1 69.000 | 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.86757 | x
10S | 338585 HEBERSP1 69.000 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 95.4 |  |  | 0.87571 | x
18S | 338606 MIDWAY-JD1 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.87872
18S | 338606 MIDWAY-JD1 69.000 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89906
18S | 338606 MIDWAY-JD1 69.000 | 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89906
18S | 338606 MIDWAY-JD1 69.000 | 338125 [5MT HOM 161.00] TO BUS 338814 [5SOLAND# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.90388
18S | 338606 MIDWAY-JD1 69.000 | 338130 [5CALCR 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91837
18S | 338606 MIDWAY-JD1 69.000 | 338125 [5MT HOM 161.00] TO BUS 338813 [5MIDWAY# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91961 |  | x
18S | 338608 MIDWAY-JD2 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.87872
18S | 338608 MIDWAY-JD2 69.000 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89906
18S | 338608 MIDWAY-JD2 69.000 | 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 157 |  | 0.89906
18S | 338608 MIDWAY-JD2 69.000 | 338125 [5MT HOM 161.00] TO BUS 338814 [5SOLAND# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.90388
18S | 338608 MIDWAY-JD2 69.000 | 338130 [5CALCR 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91837
18S | 338608 MIDWAY-JD2 69.000 | 338125 [5MT HOM 161.00] TO BUS 338813 [5MIDWAY# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91961 |  | x
18S | 338618 CLINTON-W1 69.000 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.9058 |  | x
14S | 338681 5HARR-S 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 |  | 0.89075 |  | x
14S | 338682 5OSAGE # 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 238.1 | 0.91269 | 0.84294 |  | x
10S | 338682 5OSAGE # 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 |  | 0.90374 |  | x
14S | 338758 5HEBR-N# 161.00 | 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.77206
14S | 338758 5HEBR-N# 161.00 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.80249
14S | 338758 5HEBR-N# 161.00 | 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  |  | 0.84588 | x
14S | 338758 5HEBR-N# 161.00 | 338758 [5HEBR-N# 161.00] TO BUS 505422 [GREERSF5 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 |  | 0.9183 |  | x
18S | 338758 5HEBR-N# 161.00 | 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA |  |  | 0.9144 | x
18S | 338758 5HEBR-N# 161.00 | 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  |  | 0.63559
18S | 338758 5HEBR-N# 161.00 | 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 126.3 |  |  | 0.76223
18S | 338758 5HEBR-N# 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.91151 | x
18S | 338758 5HEBR-N# 161.00 | 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 247 |  |  | 0.90249
18S | 338813 5MIDWAY# 161.00 | 338125 [5MT HOM 161.00] TO BUS 338813 [5MIDWAY# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91961 |  | x
18S | 338813 5MIDWAY# 161.00 | 338125 [5MT HOM 161.00] TO BUS 338814 [5SOLAND# 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.90388
18S | 338813 5MIDWAY# 161.00 | 338130 [5CALCR 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91837
18S | 338813 5MIDWAY# 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.87872
18S | 338813 5MIDWAY# 161.00 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89906
18S | 338813 5MIDWAY# 161.00 | 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.89906
18S | 338814 5SOLAND# 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.88933
18S | 338814 5SOLAND# 161.00 | 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 156 |  | 0.91428 |  | x
18S | 338814 5SOLAND# 161.00 | 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | 157 |  | 0.89468
18S | 338832 5CLIN-W# 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.9058 |  | x
18S | 338833 5CLINTON 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.91629 |  | x
18S | 338834 5BOTKIN# 161.00 | 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | 259.9 |  | 0.89908 |  | x

## Thermal Rev2
Contingency Scan - Thermal Overloads
Draft 2010-2012 Construction Plan Revision 2 Approved and Proposed Projects Included
Season | From Bus | To Bus | Monitored Element | % Overloads | MVA Overloads | Bus to Bus Contingency | Breaker to Breaker | rating | flow | % | cload
14W | 303221 6TALISK 230.00 | 335845 6BOGCHTA 230.00 1 | 303221 6TALISK 230.00 - 335845 6BOGCHTA 230.00 1 | 107.8% | 684MVA | BUS 500510 [MADISON6 230.00] TO BUS 500520 [MANDEV 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 303221 6TALISK 230.00 | 335845 6BOGCHTA 230.00 1 | 303221 6TALISK 230.00 - 335845 6BOGCHTA 230.00 1 | 121.9% | 779MVA | BUS 335845 [6BOGCHTA 230.00] TO BUS 500750 [RAMSAY 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 303221 6TALISK 230.00 | 335845 6BOGCHTA 230.00 1 | 303221 6TALISK 230.00 - 335845 6BOGCHTA 230.00 1 | 113.6% | 726MVA | BUS 500510 [MADISON6 230.00] TO BUS 500750 [RAMSAY 6 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 303221 6TALISK 230.00 | 500640 NSLID 6 230.00 1 | 303221 6TALISK 230.00 - 500640 NSLID 6 230.00 1 | 102.2% | 698MVA | BUS 335845 [6BOGCHTA 230.00] TO BUS 500750 [RAMSAY 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 334043 4TUBULAR 138.00 | 334044 4DOBBIN 138.00 1 | 334043 4TUBULAR 138.00 - 334044 4DOBBIN 138.00 1 | 133.2% | 139MVA | BUS 334073 [4EGYPT 138.00] TO BUS 334074 [4PANORAM 138.00] CKT 1 | Lewis Creek - Longmire | 112 | 136.76 | 123.64 | 44.7
18S | 334043 4TUBULAR 138.00 | 334044 4DOBBIN 138.00 1 | 334043 4TUBULAR 138.00 - 334044 4DOBBIN 138.00 1 | 123.7% | 137MVA | BUS 334074 [4PANORAM 138.00] TO BUS 334075 [4LONGMIR 138.00] CKT 1 | Lewis Creek - Longmire | 112 | 136.76 | 123.64 | 44.7
10S | 334045 4FISHCRK 138.00 | 334075 4LONGMIR 138.00 1 | 334045 4FISHCRK 138.00 - 334075 4LONGMIR 138.00 1 | 104% | 114MVA | BUS 334023 [4NAVSOTA 138.00] TO BUS 334024 [4SOTA 1 138.00] CKT 1 | Grimes - Navasota | 112 | 113.78 | 104.16 | 10.1
10S | 334045 4FISHCRK 138.00 | 334075 4LONGMIR 138.00 1 | 334045 4FISHCRK 138.00 - 334075 4LONGMIR 138.00 1 | 113% | 123MVA | BUS 334024 [4SOTA 1 138.00] TO BUS 334025 [4MAG AND 138.00] CKT 1 | Grimes - Navasota | 112 | 113.78 | 104.16 | 10.1
10S | 334045 4FISHCRK 138.00 | 334075 4LONGMIR 138.00 1 | 334045 4FISHCRK 138.00 - 334075 4LONGMIR 138.00 1 | 113.7% | 124MVA | BUS 334025 [4MAG AND 138.00] TO BUS 334026 [4GRIMES 138.00] CKT 1 | Grimes - Navasota | 112 | 113.78 | 104.16 | 10.1
18S | 334120 4NU LJON 138.00 | 334211 4BDAYTON 138.00 1 | 334120 4NU LJON 138.00 - 334211 4BDAYTON 138.00 1 | 106.4% | 101MVA | BUS 334084 [4CLVELND 138.00] TO BUS 334208 [4JACINTO 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 334413 4PNEC BK 138.00 | 334430 4SABINE 138.00 1 | 334413 4PNEC BK 138.00 - 334430 4SABINE 138.00 1 | 100.2% | 289MVA | BUS 334413 [4PNEC BK 138.00] TO BUS 334414 [4LINDE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 293.99 | 102.08 | 25.4
14S | 334413 4PNEC BK 138.00 | 334430 4SABINE 138.00 1 | 334413 4PNEC BK 138.00 - 334430 4SABINE 138.00 1 | 104.9% | 302MVA | BUS 334414 [4LINDE 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 293.99 | 102.08 | 25.4
18S | 334413 4PNEC BK 138.00 | 334430 4SABINE 138.00 1 | 334413 4PNEC BK 138.00 - 334430 4SABINE 138.00 1 | 103.7% | 299MVA | BUS 334413 [4PNEC BK 138.00] TO BUS 334414 [4LINDE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 304.38 | 105.69 | 27.3
18S | 334413 4PNEC BK 138.00 | 334430 4SABINE 138.00 1 | 334413 4PNEC BK 138.00 - 334430 4SABINE 138.00 1 | 108.8% | 313MVA | BUS 334414 [4LINDE 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Sabine - Port Neches (via Linde) | 288 | 304.38 | 105.69 | 27.3
14S | 334414 4LINDE 138.00 | 334430 4SABINE 138.00 1 | 334414 4LINDE 138.00 - 334430 4SABINE 138.00 1 | 101% | 291MVA | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 334414 4LINDE 138.00 | 334430 4SABINE 138.00 1 | 334414 4LINDE 138.00 - 334430 4SABINE 138.00 1 | 104.8% | 302MVA | BUS 334413 [4PNEC BK 138.00] TO BUS 334430 [4SABINE 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 334600 2KOLBS 69.000 | 334620 2LAKEVEW 69.000 1 | 334600 2KOLBS 69.000 - 334620 2LAKEVEW 69.000 1 | 100.7% | 51MVA | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
14W | 334600 2KOLBS 69.000 | 334620 2LAKEVEW 69.000 1 | 334600 2KOLBS 69.000 - 334620 2LAKEVEW 69.000 1 | 101.5% | 51MVA | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 334600 2KOLBS 69.000 | 334620 2LAKEVEW 69.000 1 | 334600 2KOLBS 69.000 - 334620 2LAKEVEW 69.000 1 | 102.1% | 52MVA | BUS 334624 [2ATLANTI 69.000] TO BUS 334627 [PNECBK2B 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335094 2MOSSVL 69.000 | 335107 2ALFOL 69.000 1 | 335094 2MOSSVL 69.000 - 335107 2ALFOL 69.000 1 | 106.8% | 42MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335094 2MOSSVL 69.000 | 335107 2ALFOL 69.000 1 | 335094 2MOSSVL 69.000 - 335107 2ALFOL 69.000 1 | 104.9% | 41MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335094 2MOSSVL 69.000 | 335107 2ALFOL 69.000 1 | 335094 2MOSSVL 69.000 - 335107 2ALFOL 69.000 1 | 106.1% | 41MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335108 [2L253ATP 69.000] CKT 1 | Same | NA | NA | NA | NA
14S | 335094 2MOSSVL 69.000 | 335108 2L253ATP 69.000 1 | 335094 2MOSSVL 69.000 - 335108 2L253ATP 69.000 1 | 104.8% | 41MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335094 2MOSSVL 69.000 | 335108 2L253ATP 69.000 1 | 335094 2MOSSVL 69.000 - 335108 2L253ATP 69.000 1 | 102.9% | 40MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335094 2MOSSVL 69.000 | 335108 2L253ATP 69.000 1 | 335094 2MOSSVL 69.000 - 335108 2L253ATP 69.000 1 | 104.1% | 40MVA | BUS 335094 [2MOSSVL 69.000] TO BUS 335107 [2ALFOL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335217 2CHLOMAL 69.000 | 335253 2LACASNE 69.000 1 | 335217 2CHLOMAL 69.000 - 335253 2LACASNE 69.000 1 | 100.4% | 33MVA | BUS 335211 [2LC BULK 69.000] TO BUS 335217 [2CHLOMAL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 100.2% | 20MVA | BUS 335435 [2CARNCRO 69.000] TO BUS 335436 [2INTSTPL 69.000] CKT 1 | Carencro - Sunset | 20 | 20.1 | 100.3 | 0.4
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 103.6% | 21MVA | BUS 335427 [2L625ATP 69.000] TO BUS 335428 [2L625OP 69.000] CKT NO | Cecelia - New Iberia | 20 | 21.16 | 105.7 | 61
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 103.6% | 21MVA | BUS 335428 [2L625OP 69.000] TO BUS 500490 [LONGFL 2 69.000] CKT 1 | Cecelia - New Iberia | 20 | 21.16 | 105.7 | 61
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 105.3% | 21MVA | BUS 335379 [4SCOTT1 138.00] TO BUS 303133 [4VATCAN 138.00] CKT 1 | Scott - East Opelousas | 20 | 21.17 | 105.28 | 114.4
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 105.7% | 21MVA | BUS 335346 [2SCOTT 69.000] TO BUS 335435 [2CARNCRO 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 100.8% | 20MVA | BUS 500440 [IVANHOE4 138.00] TO BUS 500460 [JULTAP 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 100.7% | 20MVA | BUS 500460 [JULTAP 4 138.00] TO BUS 500820 [TECHE 4 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 101.1% | 20MVA | BUS 335335 [2DUHON 69.000] TO BUS 335336 [2HUNTER 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 101.3% | 20MVA | BUS 335342 [2AVER TP 69.000] TO BUS 335343 [2AVERICO 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 105.8% | 21MVA | BUS 335346 [2SCOTT 69.000] TO BUS 335347 [2DUSON 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335346 2SCOTT 69.000 | 503304 RAYNE 2 69.000 1 | 335346 2SCOTT 69.000 - 503304 RAYNE 2 69.000 1 | 102% | 20MVA | BUS 335347 [2DUSON 69.000] TO BUS 335348 [2FROG 6 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335378 4SCOTT2 138.00 | 303152 4SEMERE 138.00 1 | 335378 4SCOTT2 138.00 - 303152 4SEMERE 138.00 1 | 101.8% | 125MVA | BUS 500940 [WELLS 6 230.00] TO BUS 502410 [PMOUTON6 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335378 4SCOTT2 138.00 | 303152 4SEMERE 138.00 1 | 335378 4SCOTT2 138.00 - 303152 4SEMERE 138.00 1 | 108.3% | 132MVA | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335379 4SCOTT1 138.00 | 303130 4NCROWL 138.00 1 | 335379 4SCOTT1 138.00 - 303130 4NCROWL 138.00 1 | 104.7% | 208MVA | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335379 4SCOTT1 138.00 | 303132 4JUDICE 138.00 1 | 335379 4SCOTT1 138.00 - 303132 4JUDICE 138.00 1 | 109.1% | 242MVA | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 241 | 241.7 | 108.83 | 9.4
10W | 335379 4SCOTT1 138.00 | 303132 4JUDICE 138.00 1 | 335379 4SCOTT1 138.00 - 303132 4JUDICE 138.00 1 | 113.6% | 251MVA | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 241.7 | 108.83 | 9.4
10S | 335379 4SCOTT1 138.00 | 303132 4JUDICE 138.00 1 | 335379 4SCOTT1 138.00 - 303132 4JUDICE 138.00 1 | 117.4% | 255MVA | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 241 | 239.11 | 109.29 | 22.6
10S | 335379 4SCOTT1 138.00 | 303132 4JUDICE 138.00 1 | 335379 4SCOTT1 138.00 - 303132 4JUDICE 138.00 1 | 107.6% | 237MVA | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 241 | 239.11 | 109.29 | 22.6
10S | 335379 4SCOTT1 138.00 | 502404 BONIN 4 138.00 1 | 335379 4SCOTT1 138.00 - 502404 BONIN 4 138.00 1 | 100.8% | 208MVA | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335380 4MEAUX 138.00 | 303132 4JUDICE 138.00 1 | 335380 4MEAUX 138.00 - 303132 4JUDICE 138.00 1 | 111.8% | 182MVA | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 185 | 166.07 | 101.45 | 22.6
10S | 335387 4DELCAMB 138.00 | 335388 4MORIL 138.00 1 | 335387 4DELCAMB 138.00 - 335388 4MORIL 138.00 1 | 101.2% | 238MVA | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335389 4DUBOIN 138.00 | 335390 4BUWHSE 138.00 1 | 335389 4DUBOIN 138.00 - 335390 4BUWHSE 138.00 1 | 126.4% | 131MVA | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
10S | 335390 4BUWHSE 138.00 | 500440 IVANHOE4 138.00 1 | 335390 4BUWHSE 138.00 - 500440 IVANHOE4 138.00 1 | 101.5% | 143MVA | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335391 4CECELIA 138.00 | 303152 4SEMERE 138.00 1 | 335391 4CECELIA 138.00 - 303152 4SEMERE 138.00 1 | 103.7% | 131MVA | BUS 335366 [4RICHARD 138.00] TO BUS 335375 [4COLACDY 138.00] CKT 1 | Same | NA | NA | NA | NA
14S | 335400 2FIVEPTS 69.000 | 335401 2TIGRE 69.000 1 | 335400 2FIVEPTS 69.000 - 335401 2TIGRE 69.000 1 | 105.6% | 40MVA | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335400 2FIVEPTS 69.000 | 335401 2TIGRE 69.000 1 | 335400 2FIVEPTS 69.000 - 335401 2TIGRE 69.000 1 | 113.8% | 43MVA | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335401 2TIGRE 69.000 | 335403 2L-247TP 69.000 1 | 335401 2TIGRE 69.000 - 335403 2L-247TP 69.000 1 | 104.2% | 40MVA | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335411 2HOLIDAY 69.000 | 335412 2LAFAYET 69.000 1 | 335411 2HOLIDAY 69.000 - 335412 2LAFAYET 69.000 1 | 117% | 45MVA | BUS 335388 [4MORIL 138.00] TO BUS 335405 [2MORIL 69.000] CKT 1 | Same | NA | NA | NA | NA
10S | 335411 2HOLIDAY 69.000 | 335412 2LAFAYET 69.000 1 | 335411 2HOLIDAY 69.000 - 335412 2LAFAYET 69.000 1 | 117.3% | 44MVA | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA | NA | NA
18S | 335411 2HOLIDAY 69.000 | 335412 2LAFAYET 69.000 1 | 335411 2HOLIDAY 69.000 - 335412 2LAFAYET 69.000 1 | 102% | 39MVA | BUS 335405 [2MORIL 69.000] TO BUS 335408 [2NEWIBER 69.000] CKT 1 | Same | NA | NA | NA | NA
10W | 335593 4MONOCM1 138.00 | 335595 4ALCHEM 138.00 1 | 335593 4MONOCM1 138.00 - 335595 4ALCHEM 138.00 1 | 102.4% | 223MVA | BUS 335569 [6POLSCAR 230.00] TO BUS 335573 [6A.A.C. 230.00] CKT 1 | Belle Helene - St. Gabriel | 225 | 219.94 | 100.87 | 19.2
10W | 335593 4MONOCM1 138.00 | 335595 4ALCHEM 138.00 1 | 335593 4MONOCM1 138.00 - 335595 4ALCHEM 138.00 1 | 101.9% | 222MVA | BUS 335573 [6A.A.C. 230.00] TO BUS 335574 [6LICAR 230.00] CKT 1 | Belle Helene - St. Gabriel | 225 | 219.94 | 100.87 | 19.2
10W | 335593 4MONOCM1 138.00 | 335595 4ALCHEM 138.00 1 | 335593 4MONOCM1 138.00 - 335595 4ALCHEM 138.00 1 | 100.5% | 219MVA | BUS 335574 [6LICAR 230.00] TO BUS 335575 [6BELL HE 230.00] CKT 1 | Belle Helene - St. Gabriel | 225 | 219.94 | 100.87 | 19.2
10W | 335593 4MONOCM1 138.00 | 335595 4ALCHEM 138.00 1 | 335593 4MONOCM1 138.00 - 335595 4ALCHEM 138.00 1 | 100.9% | 220MVA | BUS 335568 [6WGLEN 230.00] TO BUS 335569 [6POLSCAR 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335595 4ALCHEM 138.00 | 335601 4WGLEN-2 138.00 1 | 335595 4ALCHEM 138.00 - 335601 4WGLEN-2 138.00 1 | 100.3% | 269MVA | BUS 335599 [4GEIGY 138.00] TO BUS 335600 [4AIRPROD 138.00] CKT 1 | Same | NA | NA | NA | NA
10W | 335595 4ALCHEM 138.00 | 335601 4WGLEN-2 138.00 1 | 335595 4ALCHEM 138.00 - 335601 4WGLEN-2 138.00 1 | 101% | 271MVA | BUS 335600 [4AIRPROD 138.00] TO BUS 335601 [4WGLEN-2 138.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335625 4GONZL 138.00 | 336050 4SORXFM 138.00 1 | 335625 4GONZL 138.00 - 336050 4SORXFM 138.00 1 | 139.5% | 181MVA | BUS 335610 [4WGLEN 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | CL Issue | CL Issue | CL Issue | 120.3
18S | 335625 4GONZL 138.00 | 336050 4SORXFM 138.00 1 | 335625 4GONZL 138.00 - 336050 4SORXFM 138.00 1 | 139.6% | 182MVA | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | CL Issue | CL Issue | CL Issue | 120.3
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 102.3% | 719MVA | BUS 336121 [3FRANKLN 115.00] TO BUS 336122 [3BOGLSA 115.00] CKT 1 | Bogalusa - Amite | 704 | 708.31 | 100.58 | 98
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 101.5% | 713MVA | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 116.3% | 815MVA | BUS 335836 [8MCKNT 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 111.1% | 776MVA | BUS 335836 [8MCKNT 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 101.5% | 714MVA | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 101.7% | 714MVA | BUS 335500 [8WEBRE 500.00] TO BUS 303005 [8CAJUN2 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 101.9% | 715MVA | BUS 335500 [8WEBRE 500.00] TO BUS 335618 [8WGLEN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 100.9% | 710MVA | BUS 335618 [8WGLEN 500.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 103.1% | 725MVA | BUS 335618 [8WGLEN 500.00] TO BUS 336150 [8WATERFO 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 107.1% | 752MVA | BUS 335771 [6COLY 2 230.00] TO BUS 335837 [8COLY 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 105.1% | 738MVA | BUS 335771 [6COLY 2 230.00] TO BUS 336140 [6HAMMND 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 103.4% | 720MVA | BUS 335836 [8MCKNT 500.00] TO BUS 335844 [8BOGCHTA 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 103% | 724MVA | BUS 336150 [8WATERFO 500.00] TO BUS 336154 [6WATFRD 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 100.1% | 704MVA | BUS 335536 [6ADDIS 230.00] TO BUS 303000 [6CAJUN1 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 100.4% | 706MVA | BUS 335771 [6COLY 2 230.00] TO BUS 303200 [6VIGNES 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 100.3% | 706MVA | BUS 336060 [6SORR 2 230.00] TO BUS 303200 [6VIGNES 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 100.1% | 704MVA | BUS 336060 [6SORR 2 230.00] TO BUS 303204 [6FRNSTL 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 103% | 727MVA | BUS 336131 [6ADMSCRK 230.00] TO BUS 303222 [6ANGIE 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 136.4% | 964MVA | BUS 303221 [6TALISK 230.00] TO BUS 335845 [6BOGCHTA 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 131.6% | 930MVA | BUS 303221 [6TALISK 230.00] TO BUS 500640 [NSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 106.4% | 753MVA | BUS 303221 [6TALISK 230.00] TO BUS 335845 [6BOGCHTA 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 335845 6BOGCHTA 230.00 | 500750 RAMSAY 6 230.00 1 | 335845 6BOGCHTA 230.00 - 500750 RAMSAY 6 230.00 1 | 102.3% | 724MVA | BUS 303221 [6TALISK 230.00] TO BUS 500640 [NSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336050 4SORXFM 138.00 | 336051 3SORNTO 115.00 1 | 336050 4SORXFM 138.00 - 336051 3SORNTO 115.00 1 | 132.3% | 185MVA | BUS 335610 [4WGLEN 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | CL Issue | CL Issue | CL Issue | 120.3
18S | 336050 4SORXFM 138.00 | 336051 3SORNTO 115.00 1 | 336050 4SORXFM 138.00 - 336051 3SORNTO 115.00 1 | 132.3% | 185MVA | BUS 335627 [4OAKGROV 138.00] TO BUS 335628 [T300/331 138.00] CKT 1 | Willow Glen - Gonzales | CL Issue | CL Issue | CL Issue | 120.3
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 103.6% | 521MVA | BUS 335569 [6POLSCAR 230.00] TO BUS 335573 [6A.A.C. 230.00] CKT 1 | Belle Helene - St. Gabriel | 520 | 517.22 | 102.68 | 19.2
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 103.4% | 520MVA | BUS 335573 [6A.A.C. 230.00] TO BUS 335574 [6LICAR 230.00] CKT 1 | Belle Helene - St. Gabriel | 520 | 517.22 | 102.68 | 19.2
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 102.6% | 517MVA | BUS 335574 [6LICAR 230.00] TO BUS 335575 [6BELL HE 230.00] CKT 1 | Belle Helene - St. Gabriel | 520 | 517.22 | 102.68 | 19.2
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 102.8% | 518MVA | BUS 335568 [6WGLEN 230.00] TO BUS 335569 [6POLSCAR 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 100% | 505MVA | BUS 335575 [6BELL HE 230.00] TO BUS 335576 [6WOODSTK 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336060 6SORR 2 230.00 | 303200 6VIGNES 230.00 1 | 336060 6SORR 2 230.00 - 303200 6VIGNES 230.00 1 | 100.1% | 504MVA | BUS 335576 [6WOODSTK 230.00] TO BUS 335579 [6VULCHLR 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 336092 3CARLSL 115.00 | 336293 3PTNICK 115.00 1 | 336092 3CARLSL 115.00 - 336293 3PTNICK 115.00 1 | 124.4% | 114MVA | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336092 3CARLSL 115.00 | 336293 3PTNICK 115.00 1 | 336092 3CARLSL 115.00 - 336293 3PTNICK 115.00 1 | 122% | 113MVA | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336111 3AMITE 115.00 | 336517 3GILBR* 115.00 1 | 336111 3AMITE 115.00 - 336517 3GILBR* 115.00 1 | 105% | 109MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 108 | 108.67 | 104.89 | 0
10W | 336111 3AMITE 115.00 | 336517 3GILBR* 115.00 1 | 336111 3AMITE 115.00 - 336517 3GILBR* 115.00 1 | 104.9% | 109MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 108 | 108.67 | 104.89 | 0
18S | 336220 3GYPSY 115.00 | 336230 3CLAYTN 115.00 1 | 336220 3GYPSY 115.00 - 336230 3CLAYTN 115.00 1 | 100.9% | 318MVA | BUS 336190 [6GYPSY 230.00] TO BUS 336220 [3GYPSY 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336220 3GYPSY 115.00 | 336230 3CLAYTN 115.00 1 | 336220 3GYPSY 115.00 - 336230 3CLAYTN 115.00 1 | 100% | 314MVA | BUS 336194 [6SNFARM 230.00] TO BUS 336233 [3SNFARM 115.00] CKT 1 | Same | NA | NA | NA | NA
10S | 336232 3KENNER 115.00 | 336233 3SNFARM 115.00 1 | 336232 3KENNER 115.00 - 336233 3SNFARM 115.00 1 | 100.3% | 266MVA | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336232 3KENNER 115.00 | 336233 3SNFARM 115.00 1 | 336232 3KENNER 115.00 - 336233 3SNFARM 115.00 1 | 100.4% | 310MVA | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 336515 3LIBRTY 115.00 | 336517 3GILBR* 115.00 1 | 336515 3LIBRTY 115.00 - 336517 3GILBR* 115.00 1 | 102.3% | 118MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 115 | 117.2 | 102.19 | 0
10W | 336515 3LIBRTY 115.00 | 336517 3GILBR* 115.00 1 | 336515 3LIBRTY 115.00 - 336517 3GILBR* 115.00 1 | 102.2% | 117MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 115 | 117.2 | 102.19 | 0
10W | 336552 3NORFLD 115.00 | 336553 3MALIL* 115.00 1 | 336552 3NORFLD 115.00 - 336553 3MALIL* 115.00 1 | 104.1% | 204MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 199 | 202.4 | 103.98 | 0
10W | 336552 3NORFLD 115.00 | 336553 3MALIL* 115.00 1 | 336552 3NORFLD 115.00 - 336553 3MALIL* 115.00 1 | 104% | 202MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 199 | 202.4 | 103.98 | 0
10W | 336553 3MALIL* 115.00 | 336554 3BROKHV 115.00 1 | 336553 3MALIL* 115.00 - 336554 3BROKHV 115.00 1 | 108.3% | 212MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 199 | 210.75 | 108.27 | 0
10W | 336553 3MALIL* 115.00 | 336554 3BROKHV 115.00 1 | 336553 3MALIL* 115.00 - 336554 3BROKHV 115.00 1 | 108.3% | 211MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 199 | 210.75 | 108.27 | 0
10S | 336554 3BROKHV 115.00 | 336770 3WESSON 115.00 1 | 336554 3BROKHV 115.00 - 336770 3WESSON 115.00 1 | 103.1% | 156MVA | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 155.67 | 103.06 | 8.8
10S | 336554 3BROKHV 115.00 | 336770 3WESSON 115.00 1 | 336554 3BROKHV 115.00 - 336770 3WESSON 115.00 1 | 113.5% | 168MVA | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 161 | 155.67 | 103.06 | 8.8
10S | 336771 3JAM RD* 115.00 | 336772 3HZLHST 115.00 1 | 336771 3JAM RD* 115.00 - 336772 3HZLHST 115.00 1 | 125.2% | 138MVA | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 137.8 | 125.22 | 8.8
10S | 336771 3JAM RD* 115.00 | 336772 3HZLHST 115.00 1 | 336771 3JAM RD* 115.00 - 336772 3HZLHST 115.00 1 | 138.6% | 148MVA | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 137.8 | 125.22 | 8.8
10S | 336772 3HZLHST 115.00 | 336773 3COPHSW* 115.00 1 | 336772 3HZLHST 115.00 - 336773 3COPHSW* 115.00 1 | 109.1% | 120MVA | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 119.85 | 109.12 | 8.8
10S | 336772 3HZLHST 115.00 | 336773 3COPHSW* 115.00 1 | 336772 3HZLHST 115.00 - 336773 3COPHSW* 115.00 1 | 122.8% | 131MVA | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 120 | 119.85 | 109.12 | 8.8
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 102.5% | 240MVA | BUS 336906 [3JX-MON 115.00] TO BUS 336907 [3JX-MIA 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 239.95 | 102.55 | 11.7
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 103.4% | 242MVA | BUS 336907 [3JX-MIA 115.00] TO BUS 336940 [3RX BRN 115.00] CKT 1 | Monument - Rex Brown Jackson | 230 | 239.95 | 102.55 | 11.7
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 104.9% | 245MVA | BUS 336554 [3BROKHV 115.00] TO BUS 336770 [3WESSON 115.00] CKT 1 | Brookhaven - Byram | CL Issue | CL Issue | CL Issue | 102.8
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 102.7% | 240MVA | BUS 336770 [3WESSON 115.00] TO BUS 336771 [3JAM RD* 115.00] CKT 1 | Brookhaven - Byram | CL Issue | CL Issue | CL Issue | 102.8
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 100.6% | 236MVA | BUS 336771 [3JAM RD* 115.00] TO BUS 336772 [3HZLHST 115.00] CKT 1 | Brookhaven - Byram | CL Issue | CL Issue | CL Issue | 102.8
10S | 336871 3JAX-FH 115.00 | 336880 3R.BRAS 115.00 1 | 336871 3JAX-FH 115.00 - 336880 3R.BRAS 115.00 1 | 108% | 252MVA | BUS 336842 [6JAX-S 230.00] TO BUS 336890 [3JAX-S 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 336890 3JAX-S 115.00 | 336911 3JAX-E 115.00 1 | 336890 3JAX-S 115.00 - 336911 3JAX-E 115.00 1 | 103.2% | 165MVA | BUS 336906 [3JX-MON 115.00] TO BUS 336908 [3JX-FON 115.00] CKT 1 | Monument St. - East Jackson | CL Issue | CL Issue | CL Issue | 103.6
18S | 337040 6ANDRUS 230.00 | 337042 3ANDRUS 115.00 1 | 337040 6ANDRUS 230.00 - 337042 3ANDRUS 115.00 1 | 103% | 404MVA | BUS 337040 [6ANDRUS 230.00] TO BUS 337050 [6INDOLA 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337060 3WINONA 115.00 | 337061 3SAWYR* 115.00 1 | 337060 3WINONA 115.00 - 337061 3SAWYR* 115.00 1 | 100% | 105MVA | BUS 337065 [3TILTOB 115.00] TO BUS 337120 [6TILTOB 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337098 3CLARKD 115.00 | 337100 6MEPSCLK 230.00 1 | 337098 3CLARKD 115.00 - 337100 6MEPSCLK 230.00 1 | 120.5% | 301MVA | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337098 3CLARKD 115.00 | 337100 6MEPSCLK 230.00 1 | 337098 3CLARKD 115.00 - 337100 6MEPSCLK 230.00 1 | 120.5% | 301MVA | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337098 3CLARKD 115.00 | 337100 6MEPSCLK 230.00 1 | 337098 3CLARKD 115.00 - 337100 6MEPSCLK 230.00 1 | 120.6% | 302MVA | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 337098 3CLARKD 115.00 | 337100 6MEPSCLK 230.00 1 | 337098 3CLARKD 115.00 - 337100 6MEPSCLK 230.00 1 | 120.1% | 300MVA | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337098 3CLARKD 115.00 | 337100 6MEPSCLK 230.00 1 | 337098 3CLARKD 115.00 - 337100 6MEPSCLK 230.00 1 | 120.7% | 302MVA | BUS 337100 [6MEPSCLK 230.00] TO BUS 337107 [6MOONLAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337139 3GETWEL 115.00 | 337141 3NESBT* 115.00 1 | 337139 3GETWEL 115.00 - 337141 3NESBT* 115.00 1 | 102.1% | 233MVA | BUS 337144 [3GRNBRK 115.00] TO BUS 337150 [3HN LAK 115.00] CKT 1 | Horn Lake - Getwell | CL Issue | CL Issue | CL Issue | 217.3
18S | 337143 3PLUM PT 115.00 | 337144 3GRNBRK 115.00 1 | 337143 3PLUM PT 115.00 - 337144 3GRNBRK 115.00 1 | 119.6% | 272MVA | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
14S | 337144 3GRNBRK 115.00 | 337150 3HN LAK 115.00 1 | 337144 3GRNBRK 115.00 - 337150 3HN LAK 115.00 1 | 120.1% | 284MVA | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337144 3GRNBRK 115.00 | 337150 3HN LAK 115.00 1 | 337144 3GRNBRK 115.00 - 337150 3HN LAK 115.00 1 | 158.9% | 368MVA | BUS 337140 [6GETWELL 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 337361 3MINDEN 115.00 | 303302 3MNDENLG 115.00 1 | 337361 3MINDEN 115.00 - 303302 3MNDENLG 115.00 1 | 103.5% | 80MVA | BUS 337367 [3ARCADIA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | CL Issue | CL Issue | CL Issue | 101.6
18S | 337361 3MINDEN 115.00 | 303302 3MNDENLG 115.00 1 | 337361 3MINDEN 115.00 - 303302 3MNDENLG 115.00 1 | 142.7% | 106MVA | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | CL Issue | CL Issue | CL Issue | 101.6
10W | 337415 3STERL 115.00 | 337420 8STERL 500.00 2 | 337415 3STERL 115.00 - 337420 8STERL 500.00 2 | 100.6% | 603MVA | BUS 337415 [3STERL 115.00] TO BUS 337420 [8STERL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337674 3AMITY * 115.00 | 338850 3ALPINE# 115.00 1 | 337674 3AMITY * 115.00 - 338850 3ALPINE# 115.00 1 | 102.3% | 97MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337674 3AMITY * 115.00 | 338850 3ALPINE# 115.00 1 | 337674 3AMITY * 115.00 - 338850 3ALPINE# 115.00 1 | 102.3% | 97MVA | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 101.9% | 100MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 102.8% | 101MVA | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 100.9% | 100MVA | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 113% | 111MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 101.6% | 100MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 113% | 111MVA | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 107.7% | 106MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 101% | 100MVA | BUS 508072 [NWTXARK7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 337685 3HSEHVW 115.00 1 | 337678 3BISMRK 115.00 - 337685 3HSEHVW 115.00 1 | 101.4% | 100MVA | BUS 510907 [PITTSB-7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 338850 3ALPINE# 115.00 1 | 337678 3BISMRK 115.00 - 338850 3ALPINE# 115.00 1 | 106.4% | 102MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 338850 3ALPINE# 115.00 1 | 337678 3BISMRK 115.00 - 338850 3ALPINE# 115.00 1 | 106.4% | 102MVA | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 337678 3BISMRK 115.00 | 338850 3ALPINE# 115.00 1 | 337678 3BISMRK 115.00 - 338850 3ALPINE# 115.00 1 | 101.1% | 97MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10S | 337952 3LYNCH 115.00 | 338481 3MCALMT 115.00 1 | 337952 3LYNCH 115.00 - 338481 3MCALMT 115.00 1 | 109.9% | 173MVA | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 117.4% | 130MVA | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 127.23 | 115.32 | 0
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 131.9% | 146MVA | BUS 338160 [5EBON S* 161.00] TO BUS 338164 [5MARION-AR 161.00] CKT 1 | Marked Tree - Ebony | 112 | 128.2 | 118.6 | 23.8
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 115.3% | 127MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 122.76 | 111.3 | 35.1
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 110.4% | 122MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 112 | 122.76 | 111.3 | 35.1
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 112.1% | 123MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 112 | 122.76 | 111.3 | 35.1
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 114% | 126MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 122.76 | 111.3 | 35.1
18S | 338033 5PARKIN 161.00 | 338041 5TWIST 161.00 1 | 338033 5PARKIN 161.00 - 338041 5TWIST 161.00 1 | 103.7% | 114MVA | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 115.1% | 127MVA | BUS 338164 [5MARION-AR 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Marked Tree - West EHV | 112 | 123.91 | 112.97 | 0
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 113.1% | 124MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 119.65 | 109.13 | 35.1
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 108.2% | 119MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 112 | 119.65 | 109.13 | 35.1
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 109.9% | 120MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 112 | 119.65 | 109.13 | 35.1
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 111.8% | 122MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 112 | 119.65 | 109.13 | 35.1
18S | 338041 5TWIST 161.00 | 338165 5MTREE 161.00 1 | 338041 5TWIST 161.00 - 338165 5MTREE 161.00 1 | 101.6% | 111MVA | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338104 5HARR-E 161.00 - 338107 5EVRTON 161.00 1 | 106.5% | 182MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338121 [5SUMMIT 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 182.64 | 107 | 22.7
10W | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338104 5HARR-E 161.00 - 338107 5EVRTON 161.00 1 | 109.8% | 187MVA | BUS 338121 [5SUMMIT 161.00] TO BUS 338122 [5FLIPN 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 182.64 | 107 | 22.7
10W | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338104 5HARR-E 161.00 - 338107 5EVRTON 161.00 1 | 112.7% | 192MVA | BUS 338122 [5FLIPN 161.00] TO BUS 338123 [5BULLSH* 161.00] CKT 1 | Harrison E. - Bull Shoals C. O. | 167 | 182.64 | 107 | 22.7
10W | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338104 5HARR-E 161.00 - 338107 5EVRTON 161.00 1 | 113.9% | 194MVA | BUS 338123 [5BULLSH* 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals Dam - Harrison East | 167 | 182.79 | 107.09 | 27.2
10W | 338104 5HARR-E 161.00 | 338107 5EVRTON 161.00 1 | 338104 5HARR-E 161.00 - 338107 5EVRTON 161.00 1 | 104.7% | 177MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10S | 338104 5HARR-E 161.00 | 338681 5HARR-S 161.00 1 | 338104 5HARR-E 161.00 - 338681 5HARR-S 161.00 1 | 100.9% | 225MVA | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | CL Issue | CL Issue | CL Issue | 217.5
14S | 338123 5BULLSH* 161.00 | 505460 BULL SH5 161.00 1 | 338123 5BULLSH* 161.00 - 505460 BULL SH5 161.00 1 | 101.9% | 175MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 167 | 175.92 | 102.27 | 8.3
14S | 338123 5BULLSH* 161.00 | 505460 BULL SH5 161.00 1 | 338123 5BULLSH* 161.00 - 505460 BULL SH5 161.00 1 | 104.3% | 179MVA | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 167 | 175.92 | 102.27 | 8.3
18S | 338123 5BULLSH* 161.00 | 505460 BULL SH5 161.00 1 | 338123 5BULLSH* 161.00 - 505460 BULL SH5 161.00 1 | 107% | 182MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 167 | 182.71 | 107.41 | 8.8
18S | 338123 5BULLSH* 161.00 | 505460 BULL SH5 161.00 1 | 338123 5BULLSH* 161.00 - 505460 BULL SH5 161.00 1 | 109.6% | 186MVA | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 167 | 182.71 | 107.41 | 8.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336131 [6ADMSCRK 230.00] CKT 1 | Adams Creek - Franklin | 148 | 153.78 | 100.38 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 336130 [8BOGALUS 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Adams Creek - Franklin | 148 | 153.78 | 100.38 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 334200 [6PORTER 230.00] TO BUS 334202 [6CHPTSR2 230.00] CKT 1 | China - Porter | 148 | 153.31 | 100.06 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 334202 [6CHPTSR2 230.00] TO BUS 334203 [6CHPTSR1 230.00] CKT 2 | China - Porter | 148 | 153.31 | 100.06 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 334203 [6CHPTSR1 230.00] TO BUS 334204 [6CHINA 230.00] CKT 1 | China - Porter | 148 | 153.31 | 100.06 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.1% | 161MVA | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 148 | 168.83 | 110.34 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.3% | 156MVA | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 148 | 166.13 | 108.8 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 338217 [2THAY-N 69.000] TO BUS 301101 [2COUCH 69.000] CKT 1 | Thayer South - West Plains | 148 | 166.13 | 108.8 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337304 [6MONTGY 230.00] TO BUS 500200 [COLFAX 6 230.00] CKT 1 | Same | NA | NA | NA | 0
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.9% | 158MVA | BUS 338170 [5JONES 161.00] TO BUS 505418 [JONESBO5 161.00] CKT 1 | Hergett to Newport | 148 | 167.59 | 109.99 | 0
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.6% | 155MVA | BUS 338215 [5THAY-S 161.00] TO BUS 301124 [5COXCRK 161.00] CKT 1 | Thayer South - West Plains | 148 | 163.51 | 107.49 | 0
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 338033 [5PARKIN 161.00] TO BUS 338041 [5TWIST 161.00] CKT 1 | Parkin - Marked Tree | 148 | 153.8 | 100.4 | 1.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 338041 [5TWIST 161.00] TO BUS 338165 [5MTREE 161.00] CKT 1 | Parkin - Marked Tree | 148 | 153.8 | 100.4 | 1.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 156MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338734 [5SHOFNR 161.00] CKT 1 | Bailey SES AECC - Newport | 148 | 155.72 | 101.75 | 2.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.6% | 156MVA | BUS 338734 [5SHOFNR 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Newport | 148 | 155.72 | 101.75 | 2.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 155MVA | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 155.18 | 101.35 | 4.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 155.18 | 101.35 | 4.6
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 154MVA | BUS 338022 [5MOSES 161.00] TO BUS 338044 [5MCRORY 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 154.47 | 101.33 | 4.6
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 154MVA | BUS 338044 [5MCRORY 161.00] TO BUS 338879 [5BAILEY# 161.00] CKT 1 | Bailey SES AECC - Moses SES | 148 | 154.47 | 101.33 | 4.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.6% | 155MVA | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 148 | 155.87 | 101.96 | 4.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.5% | 155MVA | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 148 | 155.87 | 101.96 | 4.9
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 338142 [5ISES 1 161.00] TO BUS 338147 [5NEWRK 161.00] CKT 1 | Independence SES - Rutherford | 148 | 153.28 | 100.52 | 5.2
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 338147 [5NEWRK 161.00] TO BUS 338148 [5RUTHFR 161.00] CKT 1 | Independence SES - Rutherford | 148 | 153.28 | 100.52 | 5.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.1% | 156MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 148 | 155.89 | 101.78 | 5.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 148 | 155.89 | 101.78 | 5.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 154MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 148 | 153.66 | 100.68 | 6.3
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 154MVA | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 148 | 153.66 | 100.68 | 6.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.7% | 166MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 165.26 | 108.41 | 9.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.3% | 165MVA | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 165.26 | 108.41 | 9.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.1% | 165MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 165.26 | 108.41 | 9.1
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.6% | 165MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 164.95 | 108.3 | 9.6
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.1% | 165MVA | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 164.95 | 108.3 | 9.6
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 107.9% | 164MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 164.95 | 108.3 | 9.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 338010 [3PRICE 115.00] TO BUS 338011 [3GRIFTH 115.00] CKT 1 | Searcy Price - Brinkley East | 148 | 153.52 | 100.19 | 17.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 338011 [3GRIFTH 115.00] TO BUS 338012 [3DESARC 115.00] CKT 1 | Searcy Price - Brinkley East | 148 | 153.52 | 100.19 | 17.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 337928 [3CONW-W 115.00] TO BUS 337929 [3LK CON 115.00] CKT 1 | Conway West - Mayflower | 148 | 153.91 | 100.46 | 18.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 337929 [3LK CON 115.00] TO BUS 337930 [3MAYFL 115.00] CKT 1 | Conway West - Mayflower | 148 | 153.91 | 100.46 | 18.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 337672 [4MURFRE 138.00] TO BUS 507434 [SNASHVL4 138.00] CKT 1 | Patterson - Murfreesboro South | 148 | 153.45 | 100.15 | 19.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 157.62 | 103.04 | 19.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.6% | 157MVA | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 157.62 | 103.04 | 19.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.6% | 157MVA | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 157.62 | 103.04 | 19.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 337369 [6MTOLIV 230.00] TO BUS 337375 [6GRAMBL 230.00] CKT 1 | Danville - Mt. Olive | 148 | 146.6 | 100 | 20.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 157.38 | 102.86 | 20.7
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.8% | 157MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 148 | 157.38 | 102.86 | 20.7
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.3% | 157MVA | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 157.38 | 102.86 | 20.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 153MVA | BUS 338045 [5PRICE 161.00] TO BUS 338048 [5BALNOB 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 154.41 | 101.27 | 20.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 338048 [5BALNOB 161.00] TO BUS 338049 [5T.E.#6 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 154.41 | 101.27 | 20.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 154MVA | BUS 338049 [5T.E.#6 161.00] TO BUS 338142 [5ISES 1 161.00] CKT 1 | Independence SES - Searcy Price | 148 | 154.41 | 101.27 | 20.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338022 [5MOSES 161.00] TO BUS 338882 [5PALSTN 161.00] CKT 1 | Brinkley East - Moses SES | 148 | 153.44 | 100.1 | 22.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 338185 [5DELL 1 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 153.86 | 100.47 | 23
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 338186 [5MONETE 161.00] TO BUS 338204 [5PARAG 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 153.86 | 100.47 | 23
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 338186 [5MONETE 161.00] TO BUS 338806 [5MNILA# 161.00] CKT 1 | Dell 500 kV - Paragould | 148 | 153.86 | 100.47 | 23
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.9% | 163MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.25 | 105.51 | 23.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.7% | 161MVA | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.25 | 105.51 | 23.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.2% | 161MVA | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.25 | 105.51 | 23.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105% | 160MVA | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.25 | 105.51 | 23.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.2% | 162MVA | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 161.25 | 105.51 | 23.2
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 154MVA | BUS 338033 [5PARKIN 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 155.17 | 101.75 | 23.2
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 155MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338154 [5FISHER 161.00] CKT 1 | Newport - Parkin | 148 | 155.17 | 101.75 | 23.2
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 154MVA | BUS 338154 [5FISHER 161.00] TO BUS 338155 [5CHERRY 161.00] CKT 1 | Newport - Parkin | 148 | 155.17 | 101.75 | 23.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102% | 156MVA | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 156.05 | 101.89 | 24.4
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.3% | 157MVA | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 156.05 | 101.89 | 24.4
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.4% | 162MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338708 [5BLKRK# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 160.2 | 104.96 | 24.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.1% | 160MVA | BUS 338214 [5HRDY-N 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 160.2 | 104.96 | 24.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.7% | 160MVA | BUS 338214 [5HRDY-N 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 160.2 | 104.96 | 24.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.4% | 159MVA | BUS 338215 [5THAY-S 161.00] TO BUS 338815 [5MAMSPR# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 160.2 | 104.96 | 24.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.7% | 161MVA | BUS 338708 [5BLKRK# 161.00] TO BUS 338812 [5HRDY-E# 161.00] CKT 1 | Thayer South - Walnut Ridge | 148 | 160.2 | 104.96 | 24.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.7% | 154MVA | BUS 337905 [5RUSL-E 161.00] TO BUS 337906 [5RUSL-N 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 153.49 | 100.57 | 25.5
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 154MVA | BUS 337906 [5RUSL-N 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Russellville East | 148 | 153.49 | 100.57 | 25.5
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 110.3% | 169MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.22 | 109.89 | 26.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 109% | 167MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.22 | 109.89 | 26.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 109.4% | 167MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.22 | 109.89 | 26.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 109.9% | 168MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 168.22 | 109.89 | 26.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 110% | 168MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.91 | 109.49 | 27.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.6% | 165MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.91 | 109.49 | 27.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 109% | 166MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.91 | 109.49 | 27.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 109.5% | 167MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 166.91 | 109.49 | 27.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.9% | 156MVA | BUS 337923 [5P HILL 161.00] TO BUS 337925 [5GREENB 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 155.13 | 101.29 | 30.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.5% | 155MVA | BUS 337925 [5GREENB 161.00] TO BUS 337926 [5QUITMN 161.00] CKT 1 | Pleasant Hill - Quitman | 148 | 155.13 | 101.29 | 30.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.2% | 158MVA | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 156.51 | 102.19 | 36.4
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.4% | 157MVA | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 156.51 | 102.19 | 36.4
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102% | 156MVA | BUS 337904 [5RUSL-S 161.00] TO BUS 337905 [5RUSL-E 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 154.11 | 100.97 | 36.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 154MVA | BUS 337904 [5RUSL-S 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Dardanlle Dam SPA - Russellville East | 148 | 154.11 | 100.97 | 36.7
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 337673 [3MURF-S 115.00] TO BUS 338849 [3MURF-E# 115.00] CKT 1 | Hot Springs EHV - Murfreesboro S. SW STA | 148 | 153.45 | 100.15 | 39.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 337674 [3AMITY * 115.00] TO BUS 338849 [3MURF-E# 115.00] CKT 1 | Hot Springs EHV - Murfreesboro S. SW STA | 148 | 153.45 | 100.15 | 39.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 337674 [3AMITY * 115.00] TO BUS 338850 [3ALPINE# 115.00] CKT 1 | Hot Springs EHV - Murfreesboro S. SW STA | 148 | 153.45 | 100.15 | 39.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 337678 [3BISMRK 115.00] TO BUS 337685 [3HSEHVW 115.00] CKT 1 | Hot Springs EHV - Murfreesboro S. SW STA | 148 | 153.45 | 100.15 | 39.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 337678 [3BISMRK 115.00] TO BUS 338850 [3ALPINE# 115.00] CKT 1 | Hot Springs EHV - Murfreesboro S. SW STA | 148 | 153.45 | 100.15 | 39.6
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337372 [3RUSTON 115.00] TO BUS 338470 [2RUSTON 69.000] CKT 1 | Vienna - Ruston | 148 | 153.31 | 100.06 | 41.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.5% | 161MVA | BUS 338220 [5HIGHLND 161.00] TO BUS 504080 [GLENCOE 5 161.00] CKT 1 | Water Valley SPA - Norfork | 148 | 153.94 | 100.22 | 52.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.7% | 163MVA | BUS 338220 [5HIGHLND 161.00] TO BUS 505442 [WATER V5 161.00] CKT 1 | Water Valley SPA - Norfork | 148 | 153.94 | 100.22 | 52.2
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 155MVA | BUS 338165 [5MTREE 161.00] TO BUS 338167 [5HRSBRG* 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 154.2 | 100.63 | 56.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 154MVA | BUS 338167 [5HRSBRG* 161.00] TO BUS 338169 [5TRUMAN 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 154.2 | 100.63 | 56.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 338169 [5TRUMAN 161.00] TO BUS 338707 [5TRUM-W# 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 154.2 | 100.63 | 56.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 338707 [5TRUM-W# 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Hergett JCWL - Marked Tree | 148 | 154.2 | 100.63 | 56.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 155MVA | BUS 338047 [5PANGBR 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 157.19 | 102.57 | 70.5
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 338148 [5RUTHFR 161.00] TO BUS 338149 [5SOUTHS 161.00] CKT 1 | Searcy Price - Southside | 148 | 157.19 | 102.57 | 70.5
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 155MVA | BUS 338149 [5SOUTHS 161.00] TO BUS 338150 [5CEDAR 161.00] CKT 1 | Searcy Price - Southside | 148 | 157.19 | 102.57 | 70.5
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.4% | 166MVA | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.2% | 158MVA | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.3% | 160MVA | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 107.7% | 165MVA | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.9% | 164MVA | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.5% | 160MVA | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 157.7 | 102.96 | 72.8
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.5% | 165MVA | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 154MVA | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.7% | 157MVA | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.8% | 158MVA | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 107.7% | 164MVA | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.8% | 163MVA | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.1% | 159MVA | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 148 | 156.5 | 102.55 | 78.7
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 338046 [5SRCY-S 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 148 | 157.94 | 103.06 | 83.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 338047 [5PANGBR 161.00] TO BUS 338751 [5COP SP# 161.00] CKT 1 | Searcy Price - Rutherford | 148 | 157.94 | 103.06 | 83.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338160 [5EBON S* 161.00] TO BUS 338410 [5WM-DOV 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 148 | 154.21 | 100.62 | 91
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338160 [5EBON S* 161.00] TO BUS 338411 [5WM-GAT 161.00] CKT 1 | Kuhn Road - West Memphis EHV | 148 | 154.21 | 100.62 | 91
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 156MVA | BUS 338007 [3BEEBE 115.00] TO BUS 338008 [3GARNER* 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 155.53 | 101.4 | 111.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 338007 [3BEEBE 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 155.53 | 101.4 | 111.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.8% | 156MVA | BUS 338008 [3GARNER* 115.00] TO BUS 338010 [3PRICE 115.00] CKT 1 | Searcy Price - Jacksonville North | 148 | 155.53 | 101.4 | 111.9
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102% | 154MVA | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | CL Issue | CL Issue | CL Issue | 116.2
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 151MVA | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | CL Issue | CL Issue | CL Issue | 132.3
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 155MVA | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 148 | 153.96 | 100.5 | 140.8
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 157MVA | BUS 338682 [5OSAGE # 161.00] TO BUS 506932 [EUREKA 5 161.00] CKT 1 | Eureka Springs - Harrison East | CL Issue | CL Issue | CL Issue | 186.1
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 300035 [8NEWMAD 500.00] TO BUS 300046 [7NEWMAD 345.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.1% | 156MVA | BUS 300038 [7ESSEX 345.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 154MVA | BUS 300038 [7ESSEX 345.00] TO BUS 344974 [7LUTESVIL 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 300040 [7FLETCH 345.00] TO BUS 300047 [7SALEM 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104% | 159MVA | BUS 300040 [7FLETCH 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.2% | 158MVA | BUS 300041 [7FRANKS 345.00] TO BUS 300042 [7HUBEN 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 300041 [7FRANKS 345.00] TO BUS 344154 [7BLAND 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 300041 [7FRANKS 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 300045 [7MORGAN 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 107.5% | 164MVA | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 110.1% | 168MVA | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7CHOTEAU 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.6% | 156MVA | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 334204 [6CHINA 230.00] TO BUS 334327 [6AMELIA 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 334320 [8CYPRESS 500.00] TO BUS 334325 [8HARTBRG 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 334325 [8HARTBRG 500.00] TO BUS 334370 [8COTNWD1 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.7% | 154MVA | BUS 334325 [8HARTBRG 500.00] TO BUS 337368 [8MTOLIV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 334370 [8COTNWD1 500.00] TO BUS 334372 [XMFRINT1 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 335642 [6ESSO 2 230.00] TO BUS 335643 [6G5EXXON 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 335836 [8MCKNT 500.00] TO BUS 336562 [8FRKLIN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 336562 [8FRKLIN 500.00] TO BUS 336820 [8G.GULF 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 336830 [8B.WLSN 500.00] TO BUS 336839 [8R.BRAS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 336830 [8B.WLSN 500.00] TO BUS 337427 [8PERYVIL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 156MVA | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 337107 [6MOONLAK 230.00] TO BUS 337123 [6BATESV 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337304 [6MONTGY 230.00] TO BUS 500170 [CLARN 6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 337368 [8MTOLIV 500.00] TO BUS 337369 [6MTOLIV 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 155MVA | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337502 [3COUCH 115.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 337515 [8MCNEIL 500.00] TO BUS 337516 [3MCNEIL 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 337515 [8MCNEIL 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.8% | 157MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.5% | 155MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337643 [8SHERID 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.9% | 157MVA | BUS 337562 [7ELDEHV 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.2% | 158MVA | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 337643 [8SHERID 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 337650 [WBLFXF 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 337672 [4MURFRE 138.00] TO BUS 337673 [3MURF-S 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 337753 [8HSEHV 500.00] TO BUS 337754 [8ETTA 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 337753 [8HSEHV 500.00] TO BUS 337763 [8MAGCOVE 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.5% | 157MVA | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 155MVA | BUS 337808 [8MABEL 500.00] TO BUS 337937 [8MAYFL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 155MVA | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 115.9% | 177MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 337921 [5MOR-E 161.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102% | 156MVA | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 337928 [3CONW-W 115.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.5% | 166MVA | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 337957 [8KEO 50 500.00] TO BUS 338162 [8WM-EHV 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 104.5% | 160MVA | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 338110 [5HILLTOP 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.5% | 163MVA | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.1% | 156MVA | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 115.4% | 176MVA | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.9% | 156MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.9% | 156MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 338162 [8WM-EHV 500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 338185 [5DELL 1 161.00] TO BUS 338187 [8DELL 5 500.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.7% | 163MVA | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 338187 [8DELL 5 500.00] TO BUS 338188 [8SANSOUCI 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.8% | 163MVA | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 338191 [5BLYELM 161.00] TO BUS 338193 [5BLYINT 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 338193 [5BLYINT 161.00] TO BUS 338200 [5HAYTI 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 338200 [5HAYTI 161.00] TO BUS 338202 [5JIMHL 161.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338200 [5HAYTI 161.00] TO BUS 344720 [1HAYTI N 34.500] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338200 [5HAYTI 161.00] TO BUS 344722 [1HAYTI S 34.500] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 338201 [5PRTGVL 161.00] TO BUS 345534 [1PORTGVIL 34.500] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 338202 [5JIMHL 161.00] TO BUS 338230 [3JIMHL 115.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 344088 [7BAILEY 345.00] TO BUS 345669 [7RUSH 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 344088 [7BAILEY 345.00] TO BUS 345859 [7TYSON 2 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 344102 [7BELLEAU 345.00] TO BUS 345747 [7SIOUX 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 155MVA | BUS 344154 [7BLAND 345.00] TO BUS 344886 [7LABADIE 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102% | 156MVA | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 344886 [7LABADIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 344974 [7LUTESVIL 345.00] TO BUS 345773 [7ST FRANC 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 345088 [7MCCREDIE 345.00] TO BUS 345230 [7MONTGMRY 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 345088 [7MCCREDIE 345.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 345669 [7RUSH 345.00] TO BUS 345858 [7TYSON 1 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360010 [8RUTHERFORD 500.00] TO BUS 360050 [8MAURY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.7% | 157MVA | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 103.3% | 158MVA | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 360023 [8FREEPORT TN500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.7% | 154MVA | BUS 360023 [8FREEPORT TN500.00] TO BUS 360075 [8BHAM STEEL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 360033 [8UNION MS 500.00] TO BUS 360541 [8PLEASANT HL500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.7% | 154MVA | BUS 360035 [8WEST POINT 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101% | 155MVA | BUS 360037 [8JVILLE FP 500.00] TO BUS 360048 [8DAVIDSON TN500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.3% | 157MVA | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 360042 [8PARADISE FP500.00] TO BUS 360044 [8MONTGOMERY 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 360048 [8DAVIDSON TN500.00] TO BUS 360581 [8PIN HOOK TN500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 155MVA | BUS 360050 [8MAURY TN 500.00] TO BUS 360052 [8BR FERRY NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360050 [8MAURY TN 500.00] TO BUS 360069 [8FRANKLIN TN500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 360052 [8BR FERRY NP500.00] TO BUS 360060 [8MADISON AL 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 360052 [8BR FERRY NP500.00] TO BUS 360088 [8LIMESTONE 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 360060 [8MADISON AL 500.00] TO BUS 360065 [8WID CRK FP 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 154MVA | BUS 360065 [8WID CRK FP 500.00] TO BUS 360079 [8RACCOON MTN500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 360071 [8WILSON TN 500.00] TO BUS 360090 [8ROANE TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360085 [8WBNP #1 500.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360086 [8WBNP #2 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 360081 [8SEQUOYAH NP500.00] TO BUS 360662 [8BRADLEY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360085 [8WBNP #1 500.00] TO BUS 360090 [8ROANE TN 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 360086 [8WBNP #2 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 360086 [8WBNP #2 500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 360090 [8ROANE TN 500.00] TO BUS 360093 [8BULL RUN FP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 155MVA | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.6% | 157MVA | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 360541 [8PLEASANT HL500.00] TO BUS 360612 [8BENTON MS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 360662 [8BRADLEY TN 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 380004 [8BULLSLUI 500.00] TO BUS 380019 [8BIG SHANTY 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 380021 [8MOSTELLE 500.00] TO BUS 383045 [8CONASAUG 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 382500 [8RACOONCK 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 99 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 384157 [8MILLER8 500.00] TO BUS 384375 [8S.BESS 8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 384157 [8MILLER8 500.00] TO BUS 385312 [8CLAY 8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 384375 [8S.BESS 8 500.00] TO BUS 385123 [8BILLNGSS 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 384512 [8SNOWDN8 500.00] TO BUS 384600 [8FARLEY 8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 384512 [8SNOWDN8 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 385123 [8BILLNGSS 500.00] TO BUS 385178 [8AUTAUSS8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 500200 [COLFAX 6 230.00] TO BUS 500770 [RODEMR 6 230.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 155MVA | BUS 506935 [FLINTCR7 345.00] TO BUS 547481 [MON383 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 154MVA | BUS 506945 [CHAMSPR7 345.00] TO BUS 506959 [TONTITN7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.6% | 157MVA | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 154MVA | BUS 508072 [NWTXARK7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.5% | 155MVA | BUS 508298 [LYDIA 7 345.00] TO BUS 508359 [WELSH 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.4% | 157MVA | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.5% | 157MVA | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 155MVA | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 510380 [DELWARE7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 155MVA | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.8% | 154MVA | BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 510907 [PITTSB-7 345.00] TO BUS 515136 [SUNNYSD7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 154MVA | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.1% | 153MVA | BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 2 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.3% | 157MVA | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 153MVA | BUS 334028 [7GRIMES 345.00] TO BUS 334029 [7FRONTR 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.4% | 153MVA | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 153MVA | BUS 337561 [8ELDEHV 500.00] TO BUS 337562 [7ELDEHV 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 337643 [8SHERID 500.00] TO BUS 337651 [8WH BLF 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 337808 [8MABEL 500.00] TO BUS 337860 [8KNWRIVL 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 337922 [8P HILL 500.00] TO BUS 337923 [5P HILL 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.2% | 154MVA | BUS 338010 [3PRICE 115.00] TO BUS 338045 [5PRICE 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 110.8% | 169MVA | BUS 338140 [8HOLBT 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.7% | 154MVA | BUS 338142 [5ISES 1 161.00] TO BUS 338151 [5NEWPO 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 112% | 170MVA | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 153MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 2 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 153MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338152 [5ISES 2 161.00] CKT 3 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 113.1% | 172MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.4% | 161MVA | BUS 338110 [5HILLTOP 161.00] TO BUS 505508 [DARDANE5 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 106.7% | 162MVA | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 105.8% | 161MVA | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 300038 [7ESSEX 345.00] TO BUS 300046 [7NEWMAD 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.6% | 156MVA | BUS 300040 [7FLETCH 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.6% | 155MVA | BUS 300041 [7FRANKS 345.00] TO BUS 300042 [7HUBEN 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 300041 [7FRANKS 345.00] TO BUS 344154 [7BLAND 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 300041 [7FRANKS 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 107.4% | 164MVA | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 108.6% | 165MVA | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 154MVA | BUS 344224 [7CALAWY 1 345.00] TO BUS 344327 [7LOOSECRK 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.9% | 154MVA | BUS 360015 [8MARSHALL KY500.00] TO BUS 360040 [8CUMBERLAND 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 155MVA | BUS 360017 [8WEAKLEY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360019 [8JACKSON TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 360025 [8CORDOVA TN 500.00] TO BUS 360542 [8HAYWOOD TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 155MVA | BUS 360037 [8JVILLE FP 500.00] TO BUS 360582 [8GLEASON CT 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.2% | 153MVA | BUS 360093 [8BULL RUN FP500.00] TO BUS 360097 [8VOLUNTEER 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.5% | 155MVA | BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.7% | 155MVA | BUS 506945 [CHAMSPR7 345.00] TO BUS 509745 [CLARKSV7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 102.2% | 156MVA | BUS 508298 [LYDIA 7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.1% | 154MVA | BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100% | 153MVA | BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 101.3% | 155MVA | BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 153MVA | BUS 337926 [5QUITMN 161.00] TO BUS 337940 [5HAMLET* 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.3% | 153MVA | BUS 337562 [7ELDEHV 345.00] TO BUS 337376 [7SAREPT 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 337940 [5HAMLET* 161.00] TO BUS 338015 [ 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.6% | 154MVA | BUS 338140 [8HOLBT 500.00] TO BUS 338015 [ 161.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 338131 5MELBRN 161.00 1 | 338130 5CALCR 161.00 - 338131 5MELBRN 161.00 1 | 100.5% | 153MVA | BUS 337376 [7SAREPT 345.00] TO BUS 508809 [LONGWD 7 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 102.2% | 155MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.79 | 101.86 | 9.1
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.8% | 155MVA | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.79 | 101.86 | 9.1
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.5% | 154MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.79 | 101.86 | 9.1
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.7% | 155MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.31 | 101.48 | 9.6
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.3% | 154MVA | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.31 | 101.48 | 9.6
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.1% | 154MVA | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 148 | 154.31 | 101.48 | 9.6
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 103.8% | 158MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.72 | 103.41 | 26.8
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 102.4% | 156MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.72 | 103.41 | 26.8
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 102.8% | 157MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.72 | 103.41 | 26.8
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 103.4% | 158MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 157.72 | 103.41 | 26.8
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 103.3% | 157MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 156.32 | 102.79 | 27.8
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.8% | 155MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 156.32 | 102.79 | 27.8
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 102.3% | 155MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 156.32 | 102.79 | 27.8
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 102.8% | 156MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 156.32 | 102.79 | 27.8
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101% | 154MVA | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 103.5% | 157MVA | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 109.1% | 166MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.8% | 155MVA | BUS 337957 [8KEO 50 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 108.6% | 165MVA | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 100.1% | 153MVA | BUS 338187 [8DELL 5 500.00] TO BUS 300035 [8NEWMAD 500.00] CKT 1 | Same | NA | NA | NA | NA
10W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 100.1% | 152MVA | BUS 338188 [8SANSOUCI 500.00] TO BUS 360021 [8SHELBY TN 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 103.9% | 158MVA | BUS 338140 [8HOLBT 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 105.1% | 160MVA | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 106.4% | 161MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 100.7% | 153MVA | BUS 300046 [7NEWMAD 345.00] TO BUS 300051 [7WILHLM 345.00] CKT 1 | Same | NA | NA | NA | NA
14W | 338130 5CALCR 161.00 | 505448 NORFORK5 161.00 1 | 338130 5CALCR 161.00 - 505448 NORFORK5 161.00 1 | 101.9% | 155MVA | BUS 300051 [7WILHLM 345.00] TO BUS 300054 [7GOBKNOB 345.00] CKT 1 | Same | NA | NA | NA | NA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338131 5MELBRN 161.00 - 338132 5SAGE * 161.00 1 | 101.3% | 157MVA | BUS 338145 [8ISES 5 500.00] TO BUS 338187 [8DELL 5 500.00] CKT 1 | Same | NA | NA | NA | NA
10S | 338131 5MELBRN 161.00 | 338132 5SAGE * 161.00 1 | 338131 5MELBRN 161.00 - 338132 5SAGE * 161.00 1 | 100.4% | 155MVA | BUS 337909 [8ANO 50 500.00] TO BUS 515305 [FTSMITH8 500.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338169 5TRUMAN 161.00 | 338707 5TRUM-W# 161.00 1 | 338169 5TRUMAN 161.00 - 338707 5TRUM-W# 161.00 1 | 114.6% | 163MVA | BUS 338151 [5NEWPO 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 155.51 | 108.47 | 35.1
18S | 338169 5TRUMAN 161.00 | 338707 5TRUM-W# 161.00 1 | 338169 5TRUMAN 161.00 - 338707 5TRUM-W# 161.00 1 | 108.2% | 155MVA | BUS 338170 [5JONES 161.00] TO BUS 338171 [5CASH 1 161.00] CKT 1 | Jonesboro - Newport | 148 | 155.51 | 108.47 | 35.1
18S | 338169 5TRUMAN 161.00 | 338707 5TRUM-W# 161.00 1 | 338169 5TRUMAN 161.00 - 338707 5TRUM-W# 161.00 1 | 110.4% | 158MVA | BUS 338171 [5CASH 1 161.00] TO BUS 338172 [5NEW-AB 161.00] CKT 1 | Jonesboro - Newport | 148 | 155.51 | 108.47 | 35.1
18S | 338169 5TRUMAN 161.00 | 338707 5TRUM-W# 161.00 1 | 338169 5TRUMAN 161.00 - 338707 5TRUM-W# 161.00 1 | 112.9% | 161MVA | BUS 338172 [5NEW-AB 161.00] TO BUS 338173 [5NEW-IN 161.00] CKT 1 | Jonesboro - Newport | 148 | 155.51 | 108.47 | 35.1
18S | 338169 5TRUMAN 161.00 | 338707 5TRUM-W# 161.00 1 | 338169 5TRUMAN 161.00 - 338707 5TRUM-W# 161.00 1 | 103.4% | 147MVA | BUS 338170 [5JONES 161.00] TO BUS 505420 [HERGETT5 161.00] CKT 1 | Same | NA | NA | NA | NA
18S | 338483 3NLR-DX 115.00 | 338487 3LAKEWD 115.00 1 | 338483 3NLR-DX 115.00 - 338487 3LAKEWD 115.00 1 | 106.3% | 166MVA | BUS 337930 [3MAYFL 115.00] TO BUS 337931 [3MORGAN 115.00] CKT 1 | Mayflower - N.L.R. Levy | CL Issue | CL Issue | CL Issue | 167
10S | 338682 5OSAGE # 161.00 | 506932 EUREKA 5 161.00 1 | 338682 5OSAGE # 161.00 - 506932 EUREKA 5 161.00 1 | 100.1% | 224MVA | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | CL Issue | CL Issue | CL Issue | 217.5
18S | 338813 5MIDWAY# 161.00 | 505460 BULL SH5 161.00 1 | 338813 5MIDWAY# 161.00 - 505460 BULL SH5 161.00 1 | 102.7% | 164MVA | BUS 338814 [5SOLAND# 161.00] TO BUS 505448 [NORFORK5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | CL Issue | CL Issue | CL Issue | 156.8
18S | 338814 5SOLAND# 161.00 | 505448 NORFORK5 161.00 1 | 338814 5SOLAND# 161.00 - 505448 NORFORK5 161.00 1 | 105.6% | 165MVA | BUS 338813 [5MIDWAY# 161.00] TO BUS 505460 [BULL SH5 161.00] CKT 1 | Bull Shoals SPA - Norfork SPA | CL Issue | CL Issue | CL Issue | 156.8
14W | 500510 MADISON6 230.00 | 500520 MANDEV 6 230.00 1 | 500510 MADISON6 230.00 - 500520 MANDEV 6 230.00 1 | 122.3% | 569MVA | BUS 303221 [6TALISK 230.00] TO BUS 335845 [6BOGCHTA 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 500510 MADISON6 230.00 | 500520 MANDEV 6 230.00 1 | 500510 MADISON6 230.00 - 500520 MANDEV 6 230.00 1 | 115.1% | 537MVA | BUS 303221 [6TALISK 230.00] TO BUS 500640 [NSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA
18S | 500510 MADISON6 230.00 | 500520 MANDEV 6 230.00 1 | 500510 MADISON6 230.00 - 500520 MANDEV 6 230.00 1 | 106.1% | 495MVA | BUS 303221 [6TALISK 230.00] TO BUS 335845 [6BOGCHTA 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 500510 MADISON6 230.00 | 500750 RAMSAY 6 230.00 1 | 500510 MADISON6 230.00 - 500750 RAMSAY 6 230.00 1 | 117.5% | 817MVA | BUS 303221 [6TALISK 230.00] TO BUS 335845 [6BOGCHTA 230.00] CKT 1 | Same | NA | NA | NA | NA
14W | 500510 MADISON6 230.00 | 500750 RAMSAY 6 230.00 1 | 500510 MADISON6 230.00 - 500750 RAMSAY 6 230.00 1 | 112.8% | 785MVA | BUS 303221 [6TALISK 230.00] TO BUS 500640 [NSLID 6 230.00] CKT 1 | Same | NA | NA | NA | NA

## Voltage Rev2
Contingency Scan - Voltages
Draft 2010-2012 Construction Plan Revision 2 Approved and Proposed Projects Included
Season | Problem Area | Voltage | Contingency | Breaker to Breaker | Cload | Voltage
2014S | 334000 2CALVERT 69.000 | 0.91667 | BUS 334002 [2HEARNE 69.000] TO BUS 334003 [2TXHEARN 69.000] CKT 1 | Bryan - Hearne (via APL Hearne) | 1.8 | 0.91689
2014S | 334000 2CALVERT 69.000 | 0.91157 | BUS 334003 [2TXHEARN 69.000] TO BUS 334004 [2APLHERN 69.000] CKT 1 | Bryan - Hearne (via APL Hearne) | 1.8 | 0.91689
2014S | 334000 2CALVERT 69.000 | 0.91525 | BUS 334004 [2APLHERN 69.000] TO BUS 334005 [2BRYAN A 69.000] CKT 1 | Bryan - Hearne (via APL Hearne) | 1.8 | 0.91689
2018S | 334000 2CALVERT 69.000 | 0.90854 | BUS 334002 [2HEARNE 69.000] TO BUS 334003 [2TXHEARN 69.000] CKT 1 | Bryan - Hearne (via APL Hearne) | 1.9 | 0.90882
2018S | 334000 2CALVERT 69.000 | 0.90281 | BUS 334003 [2TXHEARN 69.000] TO BUS 334004 [2APLHERN 69.000] CKT 1 | Bryan - Hearne (via APL Hearne) | 1.9 | 0.90882
2018S | 334000 2CALVERT 69.000 | 0.8978 |  | Bryan - Hearne (via APL Hearne) | 1.9 | 0.90882
2018S | 334000 2CALVERT 69.000 | 0.91544 | BUS 334002 [2HEARNE 69.000] TO BUS 334006 [2HUMBHRN 69.000] CKT 1 | Bryan - Hearne (via Tesco) | 2 | 0.91676
2018S | 334000 2CALVERT 69.000 | 0.90096 | BUS 334006 [2HUMBHRN 69.000] TO BUS 334007 [2TESCO 69.000] CKT 1 | Bryan - Hearne (via Tesco) | 2 | 0.91676
2018S | 334000 2CALVERT 69.000 | 0.90308 | BUS 334007 [2TESCO 69.000] TO BUS 334008 [2BRYAN B 69.000] CKT 1 | Bryan - Hearne (via Tesco) | 2 | 0.91676
2010W | 334020 4BRYAN 138.00 | 1.06 | BUS 334020 [4BRYAN 138.00] TO BUS 334021 [4COLSTTA 138.00] CKT 1 | Bryan - Grimes | 0 | 1.0599
2014S | 334020 4BRYAN 138.00 | 1.059 | BUS 334020 [4BRYAN 138.00] TO BUS 334021 [4COLSTTA 138.00] CKT 1 | Bryan - Grimes | 0 | 1.0578
2014S | 334020 4BRYAN 138.00 | 1.0524 | BUS 334021 [4COLSTTA 138.00] TO BUS 334022 [4SPEEDWY 138.00] CKT 1 | Bryan - Grimes | 0 | 1.0578
2014S | 334020 4BRYAN 138.00 | 1.0536 | BUS 334022 [4SPEEDWY 138.00] TO BUS 334023 [4NAVSOTA 138.00] CKT 1 | Bryan - Grimes | 0 | 1.0578
2018S | 334045 4FISHCRK 138.00 | 0.91333 | BUS 334045 [4FISHCRK 138.00] TO BUS 334075 [4LONGMIR 138.00] CKT 1 | Navasota - Longmire | 98.7 | CL Issue
2018S | 334084 4CLVELND 138.00 | 0.91967 | BUS 334084 [4CLVELND 138.00] TO BUS 334208 [4JACINTO 138.00] CKT 1 | Same | NA | NA
2014S | 334111 4NEWCANY 138.00 | 0.91055 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334111 4NEWCANY 138.00 | 0.85724 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2014S | 334112 4HICKORY 138.00 | 0.91956 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334112 4HICKORY 138.00 | 0.87311 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334113 4EASTGAT 138.00 | 0.88968 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334114 4HUFFMAN 138.00 | 0.88588 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334115 6L533TP8 138.00 | 0.91321 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334116 4KLMP-EX 138.00 | 0.91318 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334209 4ROLKERD 138.00 | 0.91633 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334210 4ADAYTON 138.00 | 0.91725 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334211 4BDAYTON 138.00 | 0.91729 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2018S | 334216 4GORDON 138.00 | 0.9161 | BUS 334100 [4PORTER 138.00] TO BUS 334111 [4NEWCANY 138.00] CKT 1 | Same | NA | NA
2014W | 334283 4MILLCR 138.00 | 0.90683 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2018S | 334283 4MILLCR 138.00 | 0.91734 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2014W | 334284 4PINELND 138.00 | 0.91001 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2014W | 334285 4BROADUS 138.00 | 0.91129 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2014W | 334286 4ETOIL 138.00 | 0.91171 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2014W | 334300 4PEACH 138.00 | 0.91532 | BUS 334282 [4RAYBURN 138.00] TO BUS 334283 [4MILLCR 138.00] CKT 1 | Same | NA | NA
2018S | 334437 6KOLBS 230.00 | 0.91862 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
2018S | 334438 6HANKS 230.00 | 0.9184 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
2018S | 334439 6VFWPK 230.00 | 0.91774 | BUS 334434 [6SABINE 230.00] TO BUS 334439 [6VFWPK 230.00] CKT 1 | Same | NA | NA
2010S | 335137 2PPC NO 69.000 | 0.89979 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
2010W | 335137 2PPC NO 69.000 | 0.87558 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
2014S | 335137 2PPC NO 69.000 | 0.8876 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
2014W | 335137 2PPC NO 69.000 | 0.87171 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
2018S | 335137 2PPC NO 69.000 | 0.89213 | BUS 335136 [6PPG 23 230.00] TO BUS 335137 [2PPC NO 69.000] CKT 1 | Same | NA | NA
2010S | 335379 4SCOTT1 138.00 | 0.91886 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
2010S | 335380 4MEAUX 138.00 | 0.89842 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.88484
2010S | 335380 4MEAUX 138.00 | 0.8793 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.88484
2010S | 335380 4MEAUX 138.00 | 0.91553 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010S | 335380 4MEAUX 138.00 | 0.91993 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
2010W | 335380 4MEAUX 138.00 | 0.89159 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.90167
2010W | 335380 4MEAUX 138.00 | 0.9014 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.90167
2010S | 335385 4LEROY 138.00 | 0.89038 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.87668
2010S | 335385 4LEROY 138.00 | 0.87109 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.87668
2010S | 335385 4LEROY 138.00 | 0.91542 | BUS 335379 [4SCOTT1 138.00] TO BUS 303132 [4JUDICE 138.00] CKT 1 | Same | NA | NA
2010S | 335385 4LEROY 138.00 | 0.90766 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010S | 335385 4LEROY 138.00 | 0.91209 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
2010W | 335385 4LEROY 138.00 | 0.88171 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.89193
2010W | 335385 4LEROY 138.00 | 0.89163 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.89193
2010S | 335386 4ABBVIL 138.00 | 0.88483 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.87067
2010S | 335386 4ABBVIL 138.00 | 0.86092 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 22.6 | 0.87067
2010S | 335386 4ABBVIL 138.00 | 0.90988 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010W | 335386 4ABBVIL 138.00 | 0.87644 | BUS 335387 [4DELCAMB 138.00] TO BUS 335388 [4MORIL 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.88857
2010W | 335386 4ABBVIL 138.00 | 0.88824 | BUS 335387 [4DELCAMB 138.00] TO BUS 303150 [4LEBLAN 138.00] CKT 1 | Moril - Leblanc | 9.4 | 0.88857
2010S | 335387 4DELCAMB 138.00 | 0.90216 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010S | 335388 4MORIL 138.00 | 0.91189 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010S | 335391 4CECELIA 138.00 | 0.91386 | BUS 335388 [4MORIL 138.00] TO BUS 500410 [HOPKINS4 138.00] CKT 1 | Same | NA | NA
2010S | 335391 4CECELIA 138.00 | 0.9137 | BUS 502403 [BONIN 6 230.00] TO BUS 502421 [LABBE 230.00] CKT 1 | Same | NA | NA
2010S | 335435 2CARNCRO 69.000 | 0.9161 | BUS 335346 [2SCOTT 69.000] TO BUS 335435 [2CARNCRO 69.000] CKT 1 | Same | NA | NA
2010S | 336085 3ALLIA 115.00 | 0.46607 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
2010W | 336085 3ALLIA 115.00 | 0.50149 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
2010S | 336092 3CARLSL 115.00 | 0.80455 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
2010S | 336092 3CARLSL 115.00 | 0.86495 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
2010W | 336092 3CARLSL 115.00 | 0.81563 | BUS 336084 [3BARATA 115.00] TO BUS 336085 [3ALLIA 115.00] CKT 1 | Same | NA | NA
2010W | 336092 3CARLSL 115.00 | 0.86587 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
2014S | 336092 3CARLSL 115.00 | 0.90477 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
2014W | 336092 3CARLSL 115.00 | 0.90047 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
2018S | 336092 3CARLSL 115.00 | 0.89998 | BUS 336092 [3CARLSL 115.00] TO BUS 336293 [3PTNICK 115.00] CKT 1 | Same | NA | NA
2018S | 336230 3CLAYTN 115.00 | 0.9119 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
2018S | 336231 3NORCO 115.00 | 0.91443 | BUS 336220 [3GYPSY 115.00] TO BUS 336230 [3CLAYTN 115.00] CKT 1 | Same | NA | NA
2010S | 336772 3HZLHST 115.00 | 0.91695 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.91707
2010S | 336772 3HZLHST 115.00 | 0.88958 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.91707
2010S | 336773 3COPHSW* 115.00 | 0.91514 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.91526
2010S | 336773 3COPHSW* 115.00 | 0.88725 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.91526
2010S | 336774 3GALLMAN 115.00 | 0.90807 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.9082
2010S | 336774 3GALLMAN 115.00 | 0.87755 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.9082
2010S | 336775 3CRYSPG 115.00 | 0.90169 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.90181
2010S | 336775 3CRYSPG 115.00 | 0.86799 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.90181
2010S | 336776 3TERRY 115.00 | 0.8853 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.88543
2010S | 336776 3TERRY 115.00 | 0.84568 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.88543
2010S | 336777 3BYRAM 115.00 | 0.88022 | BUS 336777 [3BYRAM 115.00] TO BUS 336778 [3ELTON 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.88035
2010S | 336777 3BYRAM 115.00 | 0.83768 | BUS 336778 [3ELTON 115.00] TO BUS 336870 [3JAX-SW 115.00] CKT 1 | Southwest Jackson - Byram | 8.8 | 0.88035
2018S | 336898 3MORTON 115.00 | 0.91909 | BUS 336897 [3PELAHE 115.00] TO BUS 336898 [3MORTON 115.00] CKT 1 | Same | NA | NA
2010S | 337010 8WOLFCRK 500.00 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
2010W | 337010 8WOLFCRK 500.00 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
2014S | 337010 8WOLFCRK 500.00 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
2014W | 337010 8WOLFCRK 500.00 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
2018S | 337010 8WOLFCRK 500.00 | 1.0504 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | NA | NA
2010S | 337084 DELTA U2 69.000 | 1.0521 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 28.2 | 1.0597
2010S | 337084 DELTA U2 69.000 | 1.0598 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 28.2 | 1.0597
2010S | 337084 DELTA U2 69.000 | 1.0581 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 28.2 | 1.0597
2010S | 337084 DELTA U2 69.000 | 1.0522 | BUS 337081 [3WCLEVLD 115.00] TO BUS 337085 [3DELTA-MS 115.00] CKT 1 | Delta SES - Greenwood | 28.2 | 1.0597
2010S | 337084 DELTA U2 69.000 | 1.0537 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Delta SES - Batesville | 30.4 | 1.0539
2010S | 337084 DELTA U2 69.000 | 1.0501 | BUS 337113 [3DREWMS 115.00] TO BUS 337115 [3WEBB 1 115.00] CKT 1 | Delta SES - Batesville | 30.4 | 1.0539
2010S | 337084 DELTA U2 69.000 | 1.0504 | BUS 337032 [3ATTALA 115.00] TO BUS 337033 [3KSCUKO 115.00] CKT 1 | Attala - Winona | 32.5 | 1.0522
2014S | 337084 DELTA U2 69.000 | 1.0504 | BUS 337121 [6OAKLAND 230.00] TO BUS 337122 [6ENID 2 230.00] CKT 1 | Tillatoba - Batesville | 15.1 | 1.0509
2014S | 337084 DELTA U2 69.000 | 1.0505 | BUS 337122 [6ENID 2 230.00] TO BUS 337123 [6BATESV 230.00] CKT 1 | Tillatoba - Batesville | 15.1 | 1.0509
2014S | 337084 DELTA U2 69.000 | 1.0509 | BUS 337120 [6TILTOB 230.00] TO BUS 337121 [6OAKLAND 230.00] CKT 1 | Tillatoba - Batesville | 15.1 | 1.0509
2014S | 337084 DELTA U2 69.000 | 1.0529 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337095 [3SHLBY* 115.00] CKT 1 | Delta SES - Clarksdale | 16.8 | 1.0529
2014S | 337084 DELTA U2 69.000 | 1.0515 | BUS 337095 [3SHLBY* 115.00] TO BUS 337097 [3SHELBY-MS 115.00] CKT 1 | Delta SES - Clarksdale | 16.8 | 1.0529
2014S | 337084 DELTA U2 69.000 | 1.0565 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 29.9 | 1.064
2014S | 337084 DELTA U2 69.000 | 1.057 | BUS 337081 [3WCLEVLD 115.00] TO BUS 337085 [3DELTA-MS 115.00] CKT 1 | Delta SES - Greenwood | 29.9 | 1.064
2014S | 337084 DELTA U2 69.000 | 1.064 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 29.9 | 1.064
2014S | 337084 DELTA U2 69.000 | 1.0624 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 29.9 | 1.064
2014S | 337084 DELTA U2 69.000 | 1.0513 | BUS 337115 [3WEBB 1 115.00] TO BUS 337116 [3MARKS 115.00] CKT 1 | Delta SES - Batesville | 31.2 | 1.0576
2014S | 337084 DELTA U2 69.000 | 1.0517 | BUS 337116 [3MARKS 115.00] TO BUS 337126 [3BATESV 115.00] CKT 1 | Delta SES - Batesville | 31.2 | 1.0576
2014S | 337084 DELTA U2 69.000 | 1.0574 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Delta SES - Batesville | 31.2 | 1.0576
2014S | 337084 DELTA U2 69.000 | 1.0539 | BUS 337113 [3DREWMS 115.00] TO BUS 337115 [3WEBB 1 115.00] CKT 1 | Delta SES - Batesville | 31.2 | 1.0576
2014S | 337084 DELTA U2 69.000 | 1.0508 | BUS 336993 [3BLZONI 115.00] TO BUS 336994 [3ISOLA* 115.00] CKT 1 | Indianola - Yazoo | 34.2 | 1.0511
2014S | 337084 DELTA U2 69.000 | 1.0509 | BUS 336995 [3INVER* 115.00] TO BUS 337051 [3INDIAN 115.00] CKT 1 | Indianola - Yazoo | 34.2 | 1.0511
2014S | 337084 DELTA U2 69.000 | 1.0507 | BUS 336994 [3ISOLA* 115.00] TO BUS 336995 [3INVER* 115.00] CKT 1 | Indianola - Yazoo | 34.2 | 1.0511
2014S | 337084 DELTA U2 69.000 | 1.0527 | BUS 337080 [3PACE 1 115.00] TO BUS 337081 [3WCLEVLD 115.00] CKT 1 | Delta SES - N Greenville | 35.3 | 1.0574
2014S | 337084 DELTA U2 69.000 | 1.0503 | BUS 337079 [3ROSEDL 115.00] TO BUS 337080 [3PACE 1 115.00] CKT 1 | Delta SES - N Greenville | 35.3 | 1.0574
2014S | 337084 DELTA U2 69.000 | 1.0512 | BUS 337052 [3MORHED 115.00] TO BUS 337053 [3I.BENA 115.00] CKT 1 | Indianola - Greenwood | 39.5 | 1.0553
2014S | 337084 DELTA U2 69.000 | 1.0527 | BUS 337053 [3I.BENA 115.00] TO BUS 337054 [3GRNWOD 115.00] CKT 1 | Indianola - Greenwood | 39.5 | 1.0553
2014S | 337084 DELTA U2 69.000 | 1.0509 | BUS 337005 [8ATTALA 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | Same | NA | NA
2014S | 337084 DELTA U2 69.000 | 1.051 | BUS 337056 [3CRLTN* 115.00] TO BUS 337057 [3CARLTN 115.00] CKT 1 | Same | NA | NA
2014S | 337084 DELTA U2 69.000 | 1.0541 | BUS 337086 [3CLEVND 115.00] TO BUS 337087 [3S CLEV 115.00] CKT 1 | Same | NA | NA
2014S | 337084 DELTA U2 69.000 | 1.0505 | BUS 337088 [3SHAW* 115.00] TO BUS 337089 [3EPA-SHA 115.00] CKT 1 | Same | NA | NA
2014S | 337084 DELTA U2 69.000 | 1.0504 | BUS 337123 [6BATESV 230.00] TO BUS 338405 [6LSPWR 230.00] CKT 1 | Same | NA | NA
2018S | 337084 DELTA U2 69.000 | 1.0524 | BUS 337054 [3GRNWOD 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 31 | 1.0604
2018S | 337084 DELTA U2 69.000 | 1.0526 | BUS 337081 [3WCLEVLD 115.00] TO BUS 337085 [3DELTA-MS 115.00] CKT 1 | Delta SES - Greenwood | 31 | 1.0604
2018S | 337084 DELTA U2 69.000 | 1.0613 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337090 [3RULEVL 115.00] CKT 1 | Delta SES - Greenwood | 31 | 1.0604
2018S | 337084 DELTA U2 69.000 | 1.0586 | BUS 337090 [3RULEVL 115.00] TO BUS 337091 [3SHLATR 115.00] CKT 1 | Delta SES - Greenwood | 31 | 1.0604
2018S | 337084 DELTA U2 69.000 | 1.051 | BUS 337033 [3KSCUKO 115.00] TO BUS 337060 [3WINONA 115.00] CKT 1 | Attala - Winona | 31.4 | 1.0508
2018S | 337084 DELTA U2 69.000 | 1.0521 | BUS 337085 [3DELTA-MS 115.00] TO BUS 337113 [3DREWMS 115.00] CKT 1 | Delta SES - Batesville | 32 | 1.0524
2018S | 337084 DELTA U2 69.000 | 1.0504 | BUS 337023 [3GRNWD* 115.00] TO BUS 337054 [3GRNWOD 115.00] CKT 1 | Pickens - Greenwood | 43.1 | 1.0503
2018S | 337084 DELTA U2 69.000 | 1.05 | BUS 337000 [6MCADAM 230.00] TO BUS 337011 [6ATTALA 230.00] CKT 1 | Same | NA | NA
2018S | 337084 DELTA U2 69.000 | 1.05 | BUS 337011 [6ATTALA 230.00] TO BUS 337032 [3ATTALA 115.00] CKT 1 | Same | NA | NA
2018S | 337136 3SNTOBI 115.00 | 0.90116 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337137 3CLDWTR 115.00 | 0.88404 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337138 3HRNADO 115.00 | 0.91678 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337138 3HRNADO 115.00 | 0.91556 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337138 3HRNADO 115.00 | 0.86693 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337139 3GETWEL 115.00 | 0.91397 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337139 3GETWEL 115.00 | 0.91553 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337139 3GETWEL 115.00 | 0.86789 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337140 6GETWELL 230.00 | 0.91142 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337140 6GETWELL 230.00 | 0.91664 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337140 6GETWELL 230.00 | 0.87105 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337141 3NESBT* 115.00 | 0.91312 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337141 3NESBT* 115.00 | 0.91297 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337141 3NESBT* 115.00 | 0.86389 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337142 3NESBIT 115.00 | 0.91118 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337142 3NESBIT 115.00 | 0.91053 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337142 3NESBIT 115.00 | 0.86068 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337143 3PLUM PT 115.00 | 0.91357 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337143 3PLUM PT 115.00 | 0.91207 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337143 3PLUM PT 115.00 | 0.86214 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337144 3GRNBRK 115.00 | 0.91778 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2014S | 337144 3GRNBRK 115.00 | 0.91663 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337144 3GRNBRK 115.00 | 0.86854 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337150 3HN LAK 115.00 | 0.88425 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337151 3DESOTO-MS 115.00 | 0.88786 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337152 3WALLS 115.00 | 0.9039 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2010S | 337180 6HN LAK 230.00 | 0.91212 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337180 6HN LAK 230.00 | 0.87913 | BUS 337162 [6FRPORT 230.00] TO BUS 337180 [6HN LAK 230.00] CKT 1 | Same | NA | NA
2018S | 337367 3ARCADIA 115.00 | 0.89968 | BUS 337371 [3VIENNA-LA 115.00] TO BUS 303310 [3TRUS 115.00] CKT 1 | Vienna - Minden | 101.6 | CL Issue
2010S | 337368 8MTOLIV 500.00 | 1.0686 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2010W | 337368 8MTOLIV 500.00 | 1.0668 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2014S | 337368 8MTOLIV 500.00 | 1.0697 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2014W | 337368 8MTOLIV 500.00 | 1.0725 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2018S | 337368 8MTOLIV 500.00 | 1.0722 | BUS 337368 [8MTOLIV 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2018S | 337555 3T.E. F 115.00 | 0.91794 | BUS 337539 [3ELDEHV 115.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | Same | NA | NA
2010S | 337802 3BAUXIT 115.00 | 0.91008 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 135 | CL Issue
2010S | 337803 3BRYANT 115.00 | 0.90717 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 135 | CL Issue
2010S | 337967 3RICUS 115.00 | 1.0507 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 31.1 | 1.0569
2010S | 337967 3RICUS 115.00 | 1.051 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 31.1 | 1.0569
2010S | 337967 3RICUS 115.00 | 1.0522 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 31.1 | 1.0569
2010S | 337967 3RICUS 115.00 | 1.0555 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 31.1 | 1.0569
2010S | 337967 3RICUS 115.00 | 1.0524 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 31.1 | 1.0569
2010W | 337967 3RICUS 115.00 | 1.0572 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.0573 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.058 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.0508 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.0603 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.0581 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0614
2010W | 337967 3RICUS 115.00 | 1.053 | BUS 337967 [3RICUS 115.00] TO BUS 337972 [3ALMYRA 115.00] CKT 1 | Stuttgart Ricuskey - Gillett | 29.5 | 1.0532
2010W | 337967 3RICUS 115.00 | 1.0516 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | NA | NA
2010W | 337967 3RICUS 115.00 | 1.0511 | BUS 337627 [3PB-IP* 115.00] TO BUS 337628 [3PB-IP 115.00] CKT 1 | Same | NA | NA
2014S | 337967 3RICUS 115.00 | 1.0531 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0547
2014W | 337967 3RICUS 115.00 | 1.0528 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0576
2014W | 337967 3RICUS 115.00 | 1.053 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0576
2014W | 337967 3RICUS 115.00 | 1.0538 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0576
2014W | 337967 3RICUS 115.00 | 1.0566 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0576
2014W | 337967 3RICUS 115.00 | 1.054 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0576
2018S | 337967 3RICUS 115.00 | 1.0502 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 38.9 | 1.052
2010W | 337969 3STUTT-I 115.00 | 1.0516 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0555
2010W | 337969 3STUTT-I 115.00 | 1.0517 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0555
2010W | 337969 3STUTT-I 115.00 | 1.0523 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0555
2010W | 337969 3STUTT-I 115.00 | 1.0545 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0555
2010W | 337969 3STUTT-I 115.00 | 1.0525 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0555
2014W | 337969 3STUTT-I 115.00 | 1.0504 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 25.8 | 1.0514
2010W | 337970 3ULM 11 115.00 | 1.051 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0519
2010W | 337972 3ALMYRA 115.00 | 1.0501 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 22.8 | 1.0511
2018S | 337981 3MARVEL 115.00 | 0.91616 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
2018S | 337982 3BARTON 115.00 | 0.91266 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
2018S | 337983 3HELN-W* 115.00 | 0.90962 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
2018S | 337984 3HELN-C 115.00 | 0.90798 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | NA | NA
2018S | 338006 3CABOT 115.00 | 0.91764 | BUS 338006 [3CABOT 115.00] TO BUS 338016 [3HOLBT 115.00] CKT 1 | Same | NA | NA
2018S | 338007 3BEEBE 115.00 | 0.91847 | BUS 338006 [3CABOT 115.00] TO BUS 338016 [3HOLBT 115.00] CKT 1 | Same | NA | NA
2010S | 338205 3PARAG 115.00 | 1.0588 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 15.7 | 1.0589
2010S | 338205 3PARAG 115.00 | 1.0581 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 15.7 | 1.0589
2010S | 338205 3PARAG 115.00 | 1.0578 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 15.7 | 1.0589
2010S | 338205 3PARAG 115.00 | 1.0584 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 15.7 | 1.0589
2010S | 338205 3PARAG 115.00 | 1.0534 | BUS 338170 [5JONES 161.00] TO BUS 338703 [5JONE-N# 161.00] CKT 1 | Jonesboro - Paragould | 17.5 | 1.0547
2010S | 338205 3PARAG 115.00 | 1.0547 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 17.5 | 1.0547
2010S | 338205 3PARAG 115.00 | 1.0535 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 17.5 | 1.0547
2010S | 338205 3PARAG 115.00 | 1.059 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014S | 338205 3PARAG 115.00 | 1.0603 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 17.1 | 1.0603
2014S | 338205 3PARAG 115.00 | 1.0595 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 17.1 | 1.0603
2014S | 338205 3PARAG 115.00 | 1.0591 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 17.1 | 1.0603
2014S | 338205 3PARAG 115.00 | 1.0598 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 17.1 | 1.0603
2014S | 338205 3PARAG 115.00 | 1.052 | BUS 338170 [5JONES 161.00] TO BUS 338703 [5JONE-N# 161.00] CKT 1 | Jonesboro - Paragould | 19.6 | 1.0538
2014S | 338205 3PARAG 115.00 | 1.0537 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 19.6 | 1.0538
2014S | 338205 3PARAG 115.00 | 1.0525 | BUS 338703 [5JONE-N# 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 19.6 | 1.0538
2014S | 338205 3PARAG 115.00 | 1.0603 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2018S | 338205 3PARAG 115.00 | 1.0522 | BUS 338205 [3PARAG 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 18.6 | 1.0523
2018S | 338205 3PARAG 115.00 | 1.0511 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338208 [3WALNUT 115.00] CKT 1 | Walnut Ridge - Paragould | 18.6 | 1.0523
2018S | 338205 3PARAG 115.00 | 1.0507 | BUS 338206 [3SEDGWK* 115.00] TO BUS 338704 [3LIGHT # 115.00] CKT 1 | Walnut Ridge - Paragould | 18.6 | 1.0523
2018S | 338205 3PARAG 115.00 | 1.0516 | BUS 338704 [3LIGHT # 115.00] TO BUS 338710 [3CRO-RG# 115.00] CKT 1 | Walnut Ridge - Paragould | 18.6 | 1.0523
2018S | 338205 3PARAG 115.00 | 1.0503 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 21.8 | 1.0505
2018S | 338205 3PARAG 115.00 | 1.0519 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010S | 338206 3SEDGWK* 115.00 | 1.0587 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010W | 338206 3SEDGWK* 115.00 | 1.065 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014S | 338206 3SEDGWK* 115.00 | 1.0598 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014W | 338206 3SEDGWK* 115.00 | 1.0683 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2018S | 338206 3SEDGWK* 115.00 | 1.051 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010S | 338207 3T.E.#7 115.00 | 1.0571 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010W | 338207 3T.E.#7 115.00 | 1.0634 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014S | 338207 3T.E.#7 115.00 | 1.0582 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014W | 338207 3T.E.#7 115.00 | 1.0668 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010S | 338208 3WALNUT 115.00 | 1.0589 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010W | 338208 3WALNUT 115.00 | 1.0652 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014S | 338208 3WALNUT 115.00 | 1.06 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2014W | 338208 3WALNUT 115.00 | 1.0686 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2018S | 338208 3WALNUT 115.00 | 1.0513 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | NA | NA
2010S | 338552 HARRISON-S1 69.000 | 1.0521 | BUS 338104 [5HARR-E 161.00] TO BUS 338105 [5OMAHA * 161.00] CKT 1 | Ozark Beach - Harrison East | 9.4 | 1.0523
2010S | 338552 HARRISON-S1 69.000 | 1.0505 | BUS 338105 [5OMAHA * 161.00] TO BUS 547474 [OZD312 5 161.00] CKT 1 | Ozark Beach - Harrison East | 9.4 | 1.0523
2010S | 338552 HARRISON-S1 69.000 | 1.0521 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 217.5 | CL Issue
2014W | 338552 HARRISON-S1 69.000 | 1.0535 | BUS 338101 [5GR FOR 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0523
2014W | 338552 HARRISON-S1 69.000 | 1.0553 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0523
2014W | 338552 HARRISON-S1 69.000 | 1.0519 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0523
2014W | 338552 HARRISON-S1 69.000 | 1.053 | BUS 338104 [5HARR-E 161.00] TO BUS 338105 [5OMAHA * 161.00] CKT 1 | Ozark Beach - Harrison East | 7.6 | 1.0533
2014W | 338552 HARRISON-S1 69.000 | 1.0521 | BUS 338105 [5OMAHA * 161.00] TO BUS 547474 [OZD312 5 161.00] CKT 1 | Ozark Beach - Harrison East | 7.6 | 1.0533
2014W | 338552 HARRISON-S1 69.000 | 1.0501 | BUS 338109 [5MARSHL 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0501
2010W | 338570 BLACKROCK1 69.000 | 1.0523 | BUS 338144 [8ISXF 5 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | NA | NA
2014W | 338570 BLACKROCK1 69.000 | 1.0529 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 9.6 | 1.0524
2014W | 338570 BLACKROCK1 69.000 | 1.0522 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 9.6 | 1.0524
2014W | 338570 BLACKROCK1 69.000 | 1.0525 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 9.6 | 1.0524
2018S | 338570 BLACKROCK1 69.000 | 1.0675 | BUS 338151 [5NEWPO 161.00] TO BUS 338153 [5SWIFTN 161.00] CKT 1 | Walnut Ridge - Newport | 14 | 1.0693
2018S | 338570 BLACKROCK1 69.000 | 1.068 | BUS 338153 [5SWIFTN 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 | 1.0693
2018S | 338570 BLACKROCK1 69.000 | 1.0694 | BUS 338213 [5WALNUT 161.00] TO BUS 338705 [5HOXIES# 161.00] CKT 1 | Walnut Ridge - Newport | 14 | 1.0693
2010W | 338578 OPPELO 69.000 | 1.0501 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 5.8 | 1.0502
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 5.8 | 1.0502
2010W | 338578 OPPELO 69.000 | 1.0507 | BUS 337923 [5P HILL 161.00] TO BUS 337924 [5ST VIN 161.00] CKT 1 | Arkansas Nuclear One - Pleasant Hill | 15.5 | 1.0501
2010W | 338578 OPPELO 69.000 | 1.0511 | BUS 337921 [5MOR-E 161.00] TO BUS 337927 [5GLEASN 161.00] CKT 1 | Conway West - Morrilton East | 21.4 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0511 | BUS 337927 [5GLEASN 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 21.4 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0505 | BUS 338422 [5CONW-W 161.00] TO BUS 338424 [5TYLER 161.00] CKT 1 | Conway West - Morrilton East | 21.4 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 337826 [3LR-PIN 115.00] TO BUS 337840 [3LR-WAL 115.00] CKT 1 | L. R. Gaines - Pinnacle | 49.1 | 1.0514
2010W | 338578 OPPELO 69.000 | 1.0503 | BUS 337932 [3MAUMEL* 115.00] TO BUS 337933 [3MAUMEL 115.00] CKT 1 | Mayflower - N.L.R. Levy | 68.8 | 1.0501
2010W | 338578 OPPELO 69.000 | 1.0514 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0501 | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0513 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0511 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 72.8 | 1.0515
2010W | 338578 OPPELO 69.000 | 1.0506 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 101 | 1.0506
2010W | 338578 OPPELO 69.000 | 1.0503 | BUS 337803 [3BRYANT 115.00] TO BUS 338757 [3BRYNTS# 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 101 | 1.0506
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 337802 [3BAUXIT 115.00] TO BUS 338757 [3BRYNTS# 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 101 | 1.0506
2010W | 338578 OPPELO 69.000 | 1.0501 | BUS 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0501 | BUS 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0501 | BUS 337939 [5GOLDCR* 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0507 | BUS 337940 [5HAMLET* 161.00] TO BUS 337941 [5HAMLT 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0507 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0507 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0503 | BUS 338421 [5CONW-S 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 140.8 | 1.054
2010W | 338578 OPPELO 69.000 | 1.0515 | BUS 337826 [3LR-PIN 115.00] TO BUS 337829 [5LR-PIN 161.00] CKT 1 | Same | NA | NA
2010W | 338578 OPPELO 69.000 | 1.0505 | BUS 337908 [5MORLND 161.00] TO BUS 337924 [5ST VIN 161.00] CKT 1 | Arkansas Nuclear One - Pleasant Hill | 15.5 | 1.5015
2010W | 338578 OPPELO 69.000 | 1.0502 | BUS 337907 [5ATKINS 161.00] TO BUS 337921 [5MOR-E 161.00] CKT 1 | Morrilton East - Russellville East | 13.7 | 1.5016
2010W | 338578 OPPELO 69.000 | 1.0503 | BUS 338006 [3CABOT 115.00] TO BUS 338756 [3WARD # 115.00] CKT 1 | Searcy Price - Jacksonville North | 111.9 | CL Issue
2014W | 338578 OPPELO 69.000 | 1.05 | BUS 337826 [3LR-PIN 115.00] TO BUS 337829 [5LR-PIN 161.00] CKT 1 | Same | #N/A | NA
2014W | 338578 OPPELO 69.000 | 1.0502 | BUS 338420 [5DONAGHE 161.00] TO BUS 338421 [5CONW-S 161.00] CKT 1 | Conway West - Hamlet | 117 | CL Issue
2014W | 338578 OPPELO 69.000 | 1.0506 | BUS 338420 [5DONAGHE 161.00] TO BUS 338422 [5CONW-W 161.00] CKT 1 | Conway West - Hamlet | 117 | CL Issue
2014S | 338581 DELUCE1 69.000 | 1.0552 | BUS 337620 [3WOODW 115.00] TO BUS 337962 [3ALTHEI* 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0554 | BUS 337962 [3ALTHEI* 115.00] TO BUS 337964 [3WABSKA 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0564 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0508 | BUS 337965 [3STUT N* 115.00] TO BUS 337966 [3STUT-N 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0594 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0566 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 34.7 | 1.0607
2014S | 338581 DELUCE1 69.000 | 1.0511 | BUS 337620 [3WOODW 115.00] TO BUS 337633 [6WOODW 230.00] CKT 1 | Same | #N/A | NA
2018S | 338581 DELUCE1 69.000 | 1.0504 | BUS 337964 [3WABSKA 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 38.9 | 1.0554
2018S | 338581 DELUCE1 69.000 | 1.054 | BUS 337965 [3STUT N* 115.00] TO BUS 337967 [3RICUS 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 38.9 | 1.0554
2018S | 338581 DELUCE1 69.000 | 1.0506 | BUS 337965 [3STUT N* 115.00] TO BUS 338741 [3HUMPHRY 115.00] CKT 1 | Stuttgart Ricuskey - Woodward | 38.9 | 1.0554
2014S | 338583 WARD1 69.000 | 1.0502 | BUS 337950 [3JXNVL-N 115.00] TO BUS 338016 [3HOLBT 115.00] CKT 1 | Searcy Price - Holland Bottoms | 137.4 | CL Issue
2010S | 338585 HEBERSP1 69.000 | 1.0546 | BUS 337926 [5QUITMN 161.00] TO BUS 337939 [5GOLDCR* 161.00] CKT 1 | Conway West & Quitman - Sylvan Hills | 188.3 | 1.0547
2014S | 338585 HEBERSP1 69.000 | 1.0546 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 110.2 | CL Issue
2014W | 338585 HEBERSP1 69.000 | 1.0506 | BUS 338101 [5GR FOR 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0509
2014W | 338585 HEBERSP1 69.000 | 1.0507 | BUS 338102 [5HARR-W 161.00] TO BUS 338103 [5GRFORS 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0509
2014W | 338585 HEBERSP1 69.000 | 1.0507 | BUS 338102 [5HARR-W 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0509
2014W | 338585 HEBERSP1 69.000 | 1.051 | BUS 338104 [5HARR-E 161.00] TO BUS 338681 [5HARR-S 161.00] CKT 1 | Eureka Springs - Harrison East | 0 | 1.0509
2014W | 338585 HEBERSP1 69.000 | 1.0514 | BUS 338104 [5HARR-E 161.00] TO BUS 338107 [5EVRTON 161.00] CKT 1 | Harrison East - Hilltop | 6.3 | 1.0516
2014W | 338585 HEBERSP1 69.000 | 1.0515 | BUS 338108 [5ST_JOE 161.00] TO BUS 338110 [5HILLTOP 161.00] CKT 1 | Harrison East - Hilltop | 6.3 | 1.0516
2014W | 338585 HEBERSP1 69.000 | 1.0507 | BUS 338104 [5HARR-E 161.00] TO BUS 338105 [5OMAHA * 161.00] CKT 1 | Ozark Beach - Harrison East | 7.6 | 1.0508
2014W | 338585 HEBERSP1 69.000 | 1.0506 | BUS 338105 [5OMAHA * 161.00] TO BUS 547474 [OZD312 5 161.00] CKT 1 | Ozark Beach - Harrison East | 7.6 | 1.0508
2014W | 338585 HEBERSP1 69.000 | 1.051 | BUS 337919 [L&D #91 161.00] TO BUS 337920 [5MOR-W 161.00] CKT 1 | Morrilton East - AECC Hydro STA No. 9 | 12 | 1.0511
2014W | 338585 HEBERSP1 69.000 | 1.051 | BUS 337920 [5MOR-W 161.00] TO BUS 337921 [5MOR-E 161.00] CKT 1 | Morrilton East - AECC Hydro STA No. 9 | 12 | 1.0511
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 337908 [5MORLND 161.00] TO BUS 337912 [5ANO 16 161.00] CKT 1 | Arkansas Nuclear One - Pleasant Hill | 17.2 | 1.0501
2014W | 338585 HEBERSP1 69.000 | 1.0503 | BUS 337908 [5MORLND 161.00] TO BUS 337924 [5ST VIN 161.00] CKT 1 | Arkansas Nuclear One - Pleasant Hill | 17.2 | 1.0501
2014W | 338585 HEBERSP1 69.000 | 1.0503 | BUS 337923 [5P HILL 161.00] TO BUS 337924 [5ST VIN 161.00] CKT 1 | Arkansas Nuclear One - Pleasant Hill | 17.2 | 1.0501
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 337934 [3MURTAP* 115.00] TO BUS 337935 [3MURHYD 115.00] CKT 1 | Sylvan Hills - N.L.R. Levy | 40.3 | 1.0502
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 337935 [3MURHYD 115.00] TO BUS 338482 [MURY U1 6.9000] CKT 1 | Sylvan Hills - N.L.R. Levy | 40.3 | 1.0502
2014W | 338585 HEBERSP1 69.000 | 1.0502 | BUS 338225 [5POCAHA 161.00] TO BUS 338688 [5POCAHA# 161.00] CKT 1 | Water Valley SPA - Jim Hill | 54.8 | 1.0501
2014W | 338585 HEBERSP1 69.000 | 1.0503 | BUS 337919 [L&D #91 161.00] TO BUS 338744 [5OPPELO# 161.00] CKT 1 | AECC Hydro STA No. 9 - Pinnacle | 64.5 | 1.051
2014W | 338585 HEBERSP1 69.000 | 1.05 | BUS 338031 [5WYN-S 161.00] TO BUS 338883 [5WYNN-E# 161.00] CKT 1 | Parkin - Moses SES | 66.4 | 1.0505
2014W | 338585 HEBERSP1 69.000 | 1.0502 | BUS 338033 [5PARKIN 161.00] TO BUS 338883 [5WYNN-E# 161.00] CKT 1 | Parkin - Moses SES | 66.4 | 1.0505
2014W | 338585 HEBERSP1 69.000 | 1.0546 | BUS 337926 [5QUITMN 161.00] TO BUS 338831 [5BEE BR 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0515 | BUS 338107 [5EVRTON 161.00] TO BUS 338108 [5ST_JOE 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0507 | BUS 338109 [5MARSHL 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0545 | BUS 338831 [5BEE BR 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0545 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338833 [5CLINTON 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0509 | BUS 338832 [5CLIN-W# 161.00] TO BUS 338834 [5BOTKIN# 161.00] CKT 1 | Hilltop - Quitman | 78.7 | 1.0546
2014W | 338585 HEBERSP1 69.000 | 1.0502 | BUS 336945 [8LAKEOV 500.00] TO BUS 337009 [8MCADAM 500.00] CKT 1 | #N/A | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0505 | BUS 337420 [8STERL 500.00] TO BUS 337561 [8ELDEHV 500.00] CKT 1 | #N/A | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 337009 [8MCADAM 500.00] TO BUS 337010 [8WOLFCRK 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0503 | BUS 337860 [8KNWRIVL 500.00] TO BUS 337957 [8KEO 50 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 337940 [5HAMLET* 161.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0517 | BUS 337936 [3SYLVN 115.00] TO BUS 337938 [5SYLVN 161.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 337936 [3SYLVN 115.00] TO BUS 337950 [3JXNVL-N 115.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0515 | BUS 337940 [5HAMLET* 161.00] TO BUS 337941 [5HAMLT 161.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0514 | BUS 337940 [5HAMLET* 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.052 | BUS 337957 [8KEO 50 500.00] TO BUS 338140 [8HOLBT 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0512 | BUS 338140 [8HOLBT 500.00] TO BUS 338145 [8ISES 5 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0509 | BUS 338170 [5JONES 161.00] TO BUS 338702 [5JONE-W# 161.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0507 | BUS 335844 [8BOGCHTA 500.00] TO BUS 388700 [8DANIEL 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 360021 [8SHELBY TN 500.00] TO BUS 360025 [8CORDOVA TN 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0502 | BUS 360021 [8SHELBY TN 500.00] TO BUS 360568 [8LAG CRK CT 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 360627 [8CHOCTAW CC 500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0501 | BUS 360631 [8FRENCH CAMP500.00] TO BUS 360654 [8CHOCTAW MS 500.00] CKT 1 | Same | #N/A | NA
2014W | 338585 HEBERSP1 69.000 | 1.0516 | BUS 337938 [5SYLVN 161.00] TO BUS 338748 [5GRAVEL# 161.00] CKT 1 | Sylvan Hills - Hamlet | 9.6 | 1.0514
2014W | 338585 HEBERSP1 69.000 | 1.0504 | BUS 337940 [5HAMLET* 161.00] TO BUS 338423 [5CONIND 161.00] CKT 1 | Sylvan Hills - Hamlet | 9.6 | 1.0514
2014W | 338585 HEBERSP1 69.000 | 1.0544 | BUS 337926 [5QUITMN 161.00] TO BUS 338112 [5HEBR-S 161.00] CKT 1 | Quitman - Greers Ferry SPA | 102.2 | CL Issue
2014W | 338585 HEBERSP1 69.000 | 1.0545 | BUS 338112 [5HEBR-S 161.00] TO BUS 338113 [5HEBR-I 161.00] CKT 1 | Quitman - Greers Ferry SPA | 102.2 | CL Issue
2014W | 338585 HEBERSP1 69.000 | 1.0547 | BUS 338113 [5HEBR-I 161.00] TO BUS 338758 [5HEBR-N# 161.00] CKT 1 | Quitman - Greers Ferry SPA | 102.2 | CL Issue
2010S | 338704 3LIGHT # 115.00 | 1.0583 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2010W | 338704 3LIGHT # 115.00 | 1.0646 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2014S | 338704 3LIGHT # 115.00 | 1.0594 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2014W | 338704 3LIGHT # 115.00 | 1.0679 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2018S | 338704 3LIGHT # 115.00 | 1.0507 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2010S | 338710 3CRO-RG# 115.00 | 1.0584 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2010W | 338710 3CRO-RG# 115.00 | 1.0503 | BUS 338204 [5PARAG 161.00] TO BUS 338706 [5PARA-S# 161.00] CKT 1 | Jonesboro - Paragould | 19.2 | 1.0505
2010W | 338710 3CRO-RG# 115.00 | 1.0646 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2014S | 338710 3CRO-RG# 115.00 | 1.0595 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2014W | 338710 3CRO-RG# 115.00 | 1.068 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2018S | 338710 3CRO-RG# 115.00 | 1.0509 | BUS 338208 [3WALNUT 115.00] TO BUS 338213 [5WALNUT 161.00] CKT 1 | Same | #N/A | NA
2018S | 338756 3WARD # 115.00 | 0.91513 | BUS 338006 [3CABOT 115.00] TO BUS 338016 [3HOLBT 115.00] CKT 1 | Same | #N/A | NA
2010S | 338757 3BRYNTS# 115.00 | 0.90792 | BUS 337803 [3BRYANT 115.00] TO BUS 337804 [3MABEL 115.00] CKT 1 | Mabelvale - Hot Springs EHV | 135 | CL Issue
2018S | 338880 3HELN-I 115.00 | 0.90766 | BUS 337986 [3RITCH 115.00] TO BUS 338880 [3HELN-I 115.00] CKT 1 | Same | #N/A | NA