211022 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0519 | 1.041 | 0.92 | 1.05 | 263 | G_1WAT U3! ID 1+P1_2-1640_CLARN 4!,NATCH 4! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_1WAT U3! ID 1 |  | VH
211023 | 18W | Proposed | P3 | 41 | MANDEV 6 | VL |  |  |  |  | 0.917 | 0.9621 | 0.92 | 1.05 | 266 | G_1MICH U3! ID 1+P1_2-1686_MADISON6!,MANDEV 6! | 500520 |  |  |  | 230 | 230 | 502 | CLEC |  |  | P1_2-1686_MADISON6!,MANDEV 6! | G_1MICH U3! ID 1 | None
211024 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0508 | 1.0401 | 0.92 | 1.05 | 270 | G_1WHT BLUF U1 ID 1+1796 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U1 ID 1 |  | VH
211025 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0508 | 1.0401 | 0.92 | 1.05 | 272 | G_1WHT BLUF U2 ID 1+1796 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U2 ID 1 |  | VH
211026 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0509 | 1.0401 | 0.92 | 1.05 | 274 | G_1ANO U1 ID 1+P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U1 ID 1 |  | VH
211027 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 276 | G_1ANO U2 ID 1+P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U2 ID 1 |  | VH
211028 | 18W | Proposed | P3 | 41 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0298 | 0.92 | 1.05 | 279 | G_1ISES U1 ID 1+P1_2-38_5WPLAIN!,5KOSH! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ISES U1 ID 1 |  | VH
211029 | 18W | Proposed | P3 | 41 | 2BLACK ROCK | VH |  |  |  |  | 1.059 | 1.0298 | 0.92 | 1.05 | 280 | G_1ISES U1 ID 1+P1_2-59_5KOSH!,5COXCRK% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ISES U1 ID 1 |  | VH
211030 | 18W | Proposed | P3 | 41 | 2WARD | VH |  |  |  |  | 1.0522 | 1.0403 | 0.92 | 1.05 | 281 | G_1ISES U1 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
211031 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0517 | 1.0401 | 0.92 | 1.05 | 283 | G_1ISES U1 ID 1+1796 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ISES U1 ID 1 |  | VH
211032 | 18W | Proposed | P3 | 41 | 2BLACK ROCK | VH |  |  |  |  | 1.0543 | 1.0298 | 0.92 | 1.05 | 287 | G_1ISES U2 ID 1+P1_2-38_5WPLAIN!,5KOSH! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ISES U2 ID 1 |  | VH
211033 | 18W | Proposed | P3 | 41 | 2BLACK ROCK | VH |  |  |  |  | 1.0545 | 1.0298 | 0.92 | 1.05 | 288 | G_1ISES U2 ID 1+P1_2-59_5KOSH!,5COXCRK% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ISES U2 ID 1 |  | VH
211034 | 18W | Proposed | P3 | 41 | 8HOLND BTM% | VH |  |  |  |  | 1.0511 | 1.0256 | 0.92 | 1.05 | 295 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
211035 | 18W | Proposed | P3 | 41 | 8ISES-XF | VH |  |  |  |  | 1.0554 | 1.0293 | 0.92 | 1.05 | 295 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
211036 | 18W | Proposed | P3 | 41 | 8ISES% | VH |  |  |  |  | 1.0555 | 1.0293 | 0.92 | 1.05 | 295 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
211037 | 18W | Proposed | P3 | 41 | 2WARD | VH |  |  |  |  | 1.0587 | 1.0403 | 0.92 | 1.05 | 295 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
211038 | 18W | Proposed | P3 | 41 | 8ISES% | VH |  |  |  |  | 1.0504 | 1.0293 | 0.92 | 1.05 | 297 | G_1ISES U2 ID 1+P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U2 ID 1 |  | VH
211039 | 18W | Proposed | P3 | 41 | 8LAG CRK CT | VH |  |  |  |  | 1.0525 | 1.0401 | 0.92 | 1.05 | 303 | G_1ISES U2 ID 1+1796 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ISES U2 ID 1 |  | VH
211040 | 18W | Proposed | P3 | 41 | 2MCCLELLAN | VH |  |  |  |  | 1.0558 | 1.0256 | 0.92 | 1.05 | 307 | G_1MCCLELAN U1 ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1208_7SAREPTA%,LONGWD 7 | G_1MCCLELAN U1 ID 1 |  | VH
211041 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.92 | 0.9347 | 0.92 | 1.05 | 309 | G_G1DOLHIL! ID 1+P1_2-268_4NEWTONB!,4TOLEDO% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-268_4NEWTONB!,4TOLEDO% | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211042 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9197 | 0.9347 | 0.92 | 1.05 | 311 | G_G1DOLHIL! ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211043 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9189 | 0.9347 | 0.92 | 1.05 | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211044 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9177 | 0.9347 | 0.92 | 1.05 | 313 | G_G1DOLHIL! ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1208_7SAREPTA%,LONGWD 7 | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211045 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9195 | 0.9347 | 0.92 | 1.05 | 316 | G_G1DOLHIL! ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1649_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211046 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9188 | 0.9347 | 0.92 | 1.05 | 318 | G_G1DOLHIL! ID 1+P1_2-1861_PIRKEY 4! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1861_PIRKEY 4! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211047 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9194 | 0.9347 | 0.92 | 1.05 | 319 | G_G1DOLHIL! ID 1+P1_2-1863_PIRKEY 4!,LEBROCK7! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1863_PIRKEY 4!,LEBROCK7! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211048 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.052 | 1.041 | 0.92 | 1.05 | 320 | G_G1NESBIT! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1639_CLARN 6!,MESSICK6! | G_G1NESBIT! ID 1 |  | VH
211049 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0535 | 1.041 | 0.92 | 1.05 | 321 | G_G1NESBIT! ID 1+P1_2-1640_CLARN 4!,NATCH 4! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_G1NESBIT! ID 1 |  | VH
211050 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0524 | 1.041 | 0.92 | 1.05 | 322 | G_G2RODEMR! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1639_CLARN 6!,MESSICK6! | G_G2RODEMR! ID 1 |  | VH
211051 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0541 | 1.041 | 0.92 | 1.05 | 323 | G_G2RODEMR! ID 1+P1_2-1640_CLARN 4!,NATCH 4! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_G2RODEMR! ID 1 |  | VH
211052 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0527 | 1.041 | 0.92 | 1.05 | 324 | G_G3MADISN! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1639_CLARN 6!,MESSICK6! | G_G3MADISN! ID 1 |  | VH
211053 | 18W | Proposed | P3 | 41 | PRICE 4 | VH |  |  |  |  | 1.0502 | 1.0385 | 0.92 | 1.05 | 324 | G_G3MADISN! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 500730 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1639_CLARN 6!,MESSICK6! | G_G3MADISN! ID 1 |  | VH
211054 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0546 | 1.041 | 0.92 | 1.05 | 325 | G_G3MADISN! ID 1+P1_2-1640_CLARN 4!,NATCH 4! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_G3MADISN! ID 1 |  | VH
211055 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9199 | 0.9347 | 0.92 | 1.05 | 327 | G_PIRKEY 1 ID 1+P1_2-268_4NEWTONB!,4TOLEDO% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-268_4NEWTONB!,4TOLEDO% | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211056 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9195 | 0.9347 | 0.92 | 1.05 | 329 | G_PIRKEY 1 ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211057 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9175 | 0.9347 | 0.92 | 1.05 | 330 | G_PIRKEY 1 ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1208_7SAREPTA%,LONGWD 7 | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211058 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9192 | 0.9347 | 0.92 | 1.05 | 331 | G_PIRKEY 1 ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1649_COLFAX 6!,RODEMR 6% | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211059 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9188 | 0.9347 | 0.92 | 1.05 | 332 | G_PIRKEY 1 ID 1+P1_2-1663_DOLHILL7%,G1DOLHIL! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1663_DOLHILL7%,G1DOLHIL! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211060 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9161 | 0.9347 | 0.92 | 1.05 | 333 | G_PIRKEY 1 ID 1+P1_2-1863_PIRKEY 4!,LEBROCK7! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1863_PIRKEY 4!,LEBROCK7! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211061 | 23S | Proposed | P0 | 42 | 5HORN LAKE% | VH |  |  |  |  | 1.0567 | 1.0567 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
211062 | 23S | Proposed | P3 | 42 | 4NEW_IBERIA! | VL |  |  |  |  | 0.8985 | 0.9929 | 0.92 | 1.05 | 1 | P1_2-568_4MORIL!,4CECELIA!+G_G3TECHE! ID 1 | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-568_4MORIL!,4CECELIA! | G_G3TECHE! ID 1 |  | Contingency: Trip bus as result of con
211063 | 23S | Proposed | P3 | 42 | 3ASHLAND | VL |  |  |  |  | 0.8949 | 1.0148 | 0.92 | 1.05 | 2 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1
211064 | 23S | Proposed | P3 | 42 | 3HOUMA! | VL |  |  |  |  | 0.8969 | 1.0147 | 0.92 | 1.05 | 2 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
211065 | 23S | Proposed | P3 | 42 | 3CHAVIN! | VL |  |  |  |  | 0.9192 | 1.0257 | 0.92 | 1.05 | 2 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
211066 | 23S | Proposed | P3 | 42 | HOUMA 3 | VL |  |  |  |  | 0.8969 | 1.0147 | 0.92 | 1.05 | 2 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
211067 | 23S | Proposed | P3 | 42 | 3MT PINE.S% | VL |  |  |  |  | 0.8284 | 0.9921 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211068 | 23S | Proposed | P3 | 42 | 3ROYAL | VL |  |  |  |  | 0.8395 | 0.989 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211069 | 23S | Proposed | P3 | 42 | 3MILTON | VL |  |  |  |  | 0.8662 | 0.9852 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211070 | 23S | Proposed | P3 | 42 | 3HS.W | VL |  |  |  |  | 0.8152 | 0.9872 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211071 | 23S | Proposed | P3 | 42 | 3HS.S | VL |  |  |  |  | 0.8074 | 0.9854 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211072 | 23S | Proposed | P3 | 42 | 3ALBRIGHT | VL |  |  |  |  | 0.901 | 0.9853 | 0.92 | 1.05 | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211073 | 23S | Proposed | P3 | 42 | 3MT PINE.S% | VL |  |  |  |  | 0.8282 | 0.9921 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211074 | 23S | Proposed | P3 | 42 | 3ROYAL | VL |  |  |  |  | 0.8393 | 0.989 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211075 | 23S | Proposed | P3 | 42 | 3MILTON | VL |  |  |  |  | 0.8661 | 0.9852 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211076 | 23S | Proposed | P3 | 42 | 3HS.W | VL |  |  |  |  | 0.815 | 0.9872 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211077 | 23S | Proposed | P3 | 42 | 3HS.S | VL |  |  |  |  | 0.8072 | 0.9854 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211078 | 23S | Proposed | P3 | 42 | 3ALBRIGHT | VL |  |  |  |  | 0.9009 | 0.9853 | 0.92 | 1.05 | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211118 | 23S | Proposed | P3 | 42 | 4CANEY | VL |  |  |  |  | 0.8593 | 0.991 | 0.92 | 1.05 | 202 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
211119 | 23S | Proposed | P3 | 42 | CENTNL 4 | VL |  |  |  |  | 0.9082 | 0.9878 | 0.92 | 1.05 | 202 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
211120 | 23S | Proposed | P3 | 42 | OAKDALE4 | VL |  |  |  |  | 0.8613 | 0.989 | 0.92 | 1.05 | 202 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
211121 | 23S | Proposed | P3 | 42 | PNPRARIE 4 | VL |  |  |  |  | 0.852 | 1.0043 | 0.92 | 1.05 | 202 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
211122 | 23S | Proposed | P3 | 42 | WSTBAY 4 | VL |  |  |  |  | 0.8733 | 0.9873 | 0.92 | 1.05 | 202 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
211138 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8943 | 0.979 | 0.92 | 1.05 | 206 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211139 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.893 | 0.9778 | 0.92 | 1.05 | 206 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211140 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9087 | 0.992 | 0.92 | 1.05 | 206 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211141 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8971 | 0.979 | 0.92 | 1.05 | 207 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211142 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8958 | 0.9778 | 0.92 | 1.05 | 207 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211143 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9114 | 0.992 | 0.92 | 1.05 | 207 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211144 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.897 | 0.979 | 0.92 | 1.05 | 208 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211145 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8957 | 0.9778 | 0.92 | 1.05 | 208 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211146 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9113 | 0.992 | 0.92 | 1.05 | 208 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211147 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8959 | 0.979 | 0.92 | 1.05 | 209 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211148 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8946 | 0.9778 | 0.92 | 1.05 | 209 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211149 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9102 | 0.992 | 0.92 | 1.05 | 209 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211150 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8971 | 0.979 | 0.92 | 1.05 | 210 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211151 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8958 | 0.9778 | 0.92 | 1.05 | 210 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211152 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9114 | 0.992 | 0.92 | 1.05 | 210 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211153 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.897 | 0.979 | 0.92 | 1.05 | 211 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211154 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8957 | 0.9778 | 0.92 | 1.05 | 211 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211155 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9114 | 0.992 | 0.92 | 1.05 | 211 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211156 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8931 | 0.979 | 0.92 | 1.05 | 212 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211157 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8918 | 0.9778 | 0.92 | 1.05 | 212 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211158 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9075 | 0.992 | 0.92 | 1.05 | 212 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211159 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.897 | 0.979 | 0.92 | 1.05 | 213 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211160 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8956 | 0.9778 | 0.92 | 1.05 | 213 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211161 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9113 | 0.992 | 0.92 | 1.05 | 213 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211162 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8966 | 0.979 | 0.92 | 1.05 | 214 | P1_2-1654_COUGH 4!,PLAISAN4!+G_BONIN2 ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_BONIN2 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211163 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8952 | 0.9778 | 0.92 | 1.05 | 214 | P1_2-1654_COUGH 4!,PLAISAN4!+G_BONIN2 ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_BONIN2 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211164 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9109 | 0.992 | 0.92 | 1.05 | 214 | P1_2-1654_COUGH 4!,PLAISAN4!+G_BONIN2 ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_BONIN2 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211165 | 23S | Proposed | P3 | 42 | 4VEAZIE | VL |  |  |  |  | 0.8966 | 0.979 | 0.92 | 1.05 | 215 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211166 | 23S | Proposed | P3 | 42 | GUIDRY 4 | VL |  |  |  |  | 0.8952 | 0.9778 | 0.92 | 1.05 | 215 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211167 | 23S | Proposed | P3 | 42 | PLAISAN4 | VL |  |  |  |  | 0.9109 | 0.992 | 0.92 | 1.05 | 215 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211168 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9159 | 0.984 | 0.92 | 1.05 | 281 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+74 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 | turn on switch shunt at BEADLE 230kV sub
211169 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9164 | 0.9857 | 0.92 | 1.05 | 281 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+74 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 | turn on switch shunt at BEADLE 230kV sub
211170 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.916 | 0.984 | 0.92 | 1.05 | 282 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+190 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 | turn on switch shunt at BEADLE 230kV sub
211171 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9165 | 0.9857 | 0.92 | 1.05 | 282 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+190 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 | turn on switch shunt at BEADLE 230kV sub
211172 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9161 | 0.984 | 0.92 | 1.05 | 283 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+196 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211173 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9166 | 0.9857 | 0.92 | 1.05 | 283 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+196 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211174 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.916 | 0.984 | 0.92 | 1.05 | 284 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+197 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211175 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9166 | 0.9857 | 0.92 | 1.05 | 284 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+197 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211176 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.915 | 0.984 | 0.92 | 1.05 | 285 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+198 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211177 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9155 | 0.9857 | 0.92 | 1.05 | 285 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+198 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211178 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.915 | 0.984 | 0.92 | 1.05 | 286 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+199 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211179 | 23S | Proposed | P3 | 42 | BEADLE 6 | VL |  |  |  |  | 0.9155 | 0.9857 | 0.92 | 1.05 | 286 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+199 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211180 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9013 | 0.984 | 0.92 | 1.05 | 287 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+74 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
211181 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.8997 | 0.984 | 0.92 | 1.05 | 288 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+188 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | Facility: Radial
211182 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9014 | 0.984 | 0.92 | 1.05 | 289 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+190 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | Facility: Radial
211183 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9014 | 0.984 | 0.92 | 1.05 | 290 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+196 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | Facility: Radial
211184 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9014 | 0.984 | 0.92 | 1.05 | 291 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+197 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 |  | Facility: Radial
211185 | 23S | Proposed | P3 | 42 | B.BRID 2 | VL |  |  |  |  | 0.9189 | 0.9527 | 0.92 | 1.05 | 292 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+198 | 500120 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211186 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.8901 | 0.984 | 0.92 | 1.05 | 292 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+198 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
211187 | 23S | Proposed | P3 | 42 | B.BRID 2 | VL |  |  |  |  | 0.9189 | 0.9527 | 0.92 | 1.05 | 293 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+199 | 500120 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211188 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.8901 | 0.984 | 0.92 | 1.05 | 293 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+199 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
211189 | 23S | Proposed | P3 | 42 | ELKS 6 | VL |  |  |  |  | 0.9011 | 0.984 | 0.92 | 1.05 | 294 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+200 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
211190 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9161 | 1.0157 | 0.92 | 1.05 | 297 | G_1STFRG1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1STFRG1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211191 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9176 | 1.0158 | 0.92 | 1.05 | 297 | G_1STFRG1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1STFRG1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211192 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9192 | 1.0157 | 0.92 | 1.05 | 298 | G_1FRNTR 1! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1FRNTR 1! ID 1 | Turn on switch shunt at Couch 69 kV sub
211193 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9192 | 1.0157 | 0.92 | 1.05 | 299 | G_1FRNTR 2! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1FRNTR 2! ID 1 | Turn on switch shunt at Couch 69 kV sub
211194 | 23S | Proposed | P3 | 42 | 4KIRBY | VL |  |  |  |  | 0.9187 | 0.9933 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211195 | 23S | Proposed | P3 | 42 | 4CALL! | VL |  |  |  |  | 0.9145 | 0.994 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211196 | 23S | Proposed | P3 | 42 | 4NBUNA | VL |  |  |  |  | 0.9083 | 0.9974 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334304 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211197 | 23S | Proposed | P3 | 42 | 4BUNASW | VL |  |  |  |  | 0.9083 | 0.9974 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334305 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211198 | 23S | Proposed | P3 | 42 | 4TEMPLE | VL |  |  |  |  | 0.9083 | 0.9974 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334306 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211199 | 23S | Proposed | P3 | 42 | 4BUNA! | VL |  |  |  |  | 0.9076 | 0.9992 | 0.92 | 1.05 | 302 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334307 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211200 | 23S | Proposed | P3 | 42 | 2NECHESO | VL |  |  |  |  | 0.9101 | 0.9406 | 0.92 | 1.05 | 303 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211201 | 23S | Proposed | P3 | 42 | 2NECHESO | VL |  |  |  |  | 0.9098 | 0.9406 | 0.92 | 1.05 | 304 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211202 | 23S | Proposed | P3 | 42 | 2NECHESO | VL |  |  |  |  | 0.9133 | 0.9406 | 0.92 | 1.05 | 305 | G_1EXXONGT1! ID 1+P1_2-298_4CENTRAL-TX!,4UNION! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-298_4CENTRAL-TX!,4UNION! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211203 | 23S | Proposed | P3 | 42 | 2NECHESO | VL |  |  |  |  | 0.9107 | 0.9406 | 0.92 | 1.05 | 306 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211204 | 23S | Proposed | P3 | 42 | 2NECHESO | VL |  |  |  |  | 0.9083 | 0.9406 | 0.92 | 1.05 | 307 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
211205 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9179 | 1.0157 | 0.92 | 1.05 | 314 | G_1RVR_BND_G1! ID 1+1768 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1RVR_BND_G1! ID 1 | Turn on switch shunt at Couch 69 kV sub
211206 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9194 | 1.0158 | 0.92 | 1.05 | 314 | G_1RVR_BND_G1! ID 1+1768 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1RVR_BND_G1! ID 1 | Turn on switch shunt at Couch 69 kV sub
211207 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9177 | 1.0157 | 0.92 | 1.05 | 315 | G_1WAT U3! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WAT U3! ID 1 | Turn on switch shunt at Couch 69 kV sub
211208 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9191 | 1.0158 | 0.92 | 1.05 | 315 | G_1WAT U3! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WAT U3! ID 1 | Turn on switch shunt at Couch 69 kV sub
211209 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9171 | 1.0157 | 0.92 | 1.05 | 321 | G_1GGNS U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1GGNS U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211210 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9185 | 1.0158 | 0.92 | 1.05 | 321 | G_1GGNS U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1GGNS U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211211 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9179 | 1.0157 | 0.92 | 1.05 | 331 | G_1WHT BLUF U1 ID 1+1768 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WHT BLUF U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211212 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9194 | 1.0158 | 0.92 | 1.05 | 331 | G_1WHT BLUF U1 ID 1+1768 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WHT BLUF U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211213 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9179 | 1.0157 | 0.92 | 1.05 | 335 | G_1WHT BLUF U2 ID 1+1768 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WHT BLUF U2 ID 1 | Turn on switch shunt at Couch 69 kV sub
211214 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9193 | 1.0158 | 0.92 | 1.05 | 335 | G_1WHT BLUF U2 ID 1+1768 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1WHT BLUF U2 ID 1 | Turn on switch shunt at Couch 69 kV sub
211215 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9171 | 1.0157 | 0.92 | 1.05 | 341 | G_1ANO U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211216 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9186 | 1.0158 | 0.92 | 1.05 | 341 | G_1ANO U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211217 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9187 | 1.0157 | 0.92 | 1.05 | 345 | G_1ANO U2 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U2 ID 1 | Turn on switch shunt at Couch 69 kV sub
211218 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9167 | 1.0157 | 0.92 | 1.05 | 348 | G_1ISES U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ISES U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211219 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9181 | 1.0158 | 0.92 | 1.05 | 348 | G_1ISES U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ISES U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211220 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9189 | 1.0157 | 0.92 | 1.05 | 353 | G_1PLUM PT U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1PLUM PT U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211221 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9157 | 1.0157 | 0.92 | 1.05 | 355 | G_1CAL G1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1CAL G1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211222 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9171 | 1.0158 | 0.92 | 1.05 | 355 | G_1CAL G1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1CAL G1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211223 | 23S | Proposed | P3 | 42 | 2WEIRGAT | VL |  |  |  |  | 0.9176 | 0.982 | 0.92 | 1.05 | 365 | G_G1DOLHIL! ID 1+P1_2-239_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211224 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9195 | 1.0157 | 0.92 | 1.05 | 369 | G_G1DOLHIL! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_G1DOLHIL! ID 1 | Turn on switch shunt at Couch 69 kV sub
211225 | 23S | Proposed | P3 | 42 | TENRUSK7 | VH |  |  |  |  | 1.051 | 1.0146 | 0.92 | 1.05 | 371 | G_G1DOLHIL! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_G1DOLHIL! ID 1 |  | VH
211226 | 23S | Proposed | P3 | 42 | TENGEN 7 | VH |  |  |  |  | 1.051 | 1.0146 | 0.92 | 1.05 | 371 | G_G1DOLHIL! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_G1DOLHIL! ID 1 |  | VH
211227 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9188 | 1.0157 | 0.92 | 1.05 | 375 | G_G3TECHE! ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_G3TECHE! ID 1 | Turn on switch shunt at Couch 69 kV sub
211228 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9165 | 1.0157 | 0.92 | 1.05 | 378 | G_JBOGENE1 ID E+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JBOGENE1 ID E | Turn on switch shunt at Couch 69 kV sub
211229 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9179 | 1.0158 | 0.92 | 1.05 | 378 | G_JBOGENE1 ID E+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JBOGENE1 ID E | Turn on switch shunt at Couch 69 kV sub
211230 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9194 | 1.0157 | 0.92 | 1.05 | 383 | G_BVR #1 1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_BVR #1 1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211231 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9185 | 1.0157 | 0.92 | 1.05 | 385 | G_FLINTCR1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_FLINTCR1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211232 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9199 | 1.0158 | 0.92 | 1.05 | 385 | G_FLINTCR1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_FLINTCR1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211233 | 23S | Proposed | P3 | 42 | 2WEIRGAT | VL |  |  |  |  | 0.9134 | 0.982 | 0.92 | 1.05 | 386 | G_PIRKEY 1 ID 1+P1_2-239_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211234 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9182 | 1.0157 | 0.92 | 1.05 | 388 | G_PIRKEY 1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_PIRKEY 1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211235 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9196 | 1.0158 | 0.92 | 1.05 | 388 | G_PIRKEY 1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_PIRKEY 1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211236 | 23S | Proposed | P3 | 42 | TENRUSK7 | VH |  |  |  |  | 1.0518 | 1.0146 | 0.92 | 1.05 | 390 | G_PIRKEY 1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_PIRKEY 1 ID 1 |  | VH
211237 | 23S | Proposed | P3 | 42 | TENGEN 7 | VH |  |  |  |  | 1.0518 | 1.0146 | 0.92 | 1.05 | 390 | G_PIRKEY 1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_PIRKEY 1 ID 1 |  | VH
211238 | 23S | Proposed | P3 | 42 | 2WEIRGAT | VL |  |  |  |  | 0.9171 | 0.982 | 0.92 | 1.05 | 391 | G_WELSH2-1 ID 1+P1_2-239_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211239 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9195 | 1.0157 | 0.92 | 1.05 | 393 | G_WELSH2-1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_WELSH2-1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211240 | 23S | Proposed | P3 | 42 | TENRUSK7 | VH |  |  |  |  | 1.0511 | 1.0146 | 0.92 | 1.05 | 394 | G_WELSH2-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH2-1 ID 1 |  | VH
211241 | 23S | Proposed | P3 | 42 | TENGEN 7 | VH |  |  |  |  | 1.0511 | 1.0146 | 0.92 | 1.05 | 394 | G_WELSH2-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH2-1 ID 1 |  | VH
211242 | 23S | Proposed | P3 | 42 | 2WEIRGAT | VL |  |  |  |  | 0.9171 | 0.982 | 0.92 | 1.05 | 395 | G_WELSH3-1 ID 1+P1_2-239_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211243 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9195 | 1.0157 | 0.92 | 1.05 | 397 | G_WELSH3-1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_WELSH3-1 ID 1 | Turn on switch shunt at Couch 69 kV sub
211244 | 23S | Proposed | P3 | 42 | TENRUSK7 | VH |  |  |  |  | 1.0511 | 1.0146 | 0.92 | 1.05 | 398 | G_WELSH3-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH3-1 ID 1 |  | VH
211245 | 23S | Proposed | P3 | 42 | TENGEN 7 | VH |  |  |  |  | 1.0511 | 1.0146 | 0.92 | 1.05 | 398 | G_WELSH3-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH3-1 ID 1 |  | VH
211246 | 23S | Proposed | P3 | 42 | 2WEIRGAT | VL |  |  |  |  | 0.9175 | 0.982 | 0.92 | 1.05 | 399 | G_TURKCOAL ID 1+P1_2-239_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211247 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9181 | 1.0157 | 0.92 | 1.05 | 401 | G_TURKCOAL ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_TURKCOAL ID 1 | Turn on switch shunt at Couch 69 kV sub
211248 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9195 | 1.0158 | 0.92 | 1.05 | 401 | G_TURKCOAL ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_TURKCOAL ID 1 | Turn on switch shunt at Couch 69 kV sub
211249 | 23S | Proposed | P3 | 42 | TENRUSK7 | VH |  |  |  |  | 1.051 | 1.0146 | 0.92 | 1.05 | 402 | G_TURKCOAL ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_TURKCOAL ID 1 |  | VH
211250 | 23S | Proposed | P3 | 42 | TENGEN 7 | VH |  |  |  |  | 1.051 | 1.0146 | 0.92 | 1.05 | 402 | G_TURKCOAL ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_TURKCOAL ID 1 |  | VH
211251 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9187 | 1.0157 | 0.92 | 1.05 | 404 | G_MUSKOG4G ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_MUSKOG4G ID 1 | Turn on switch shunt at Couch 69 kV sub
211252 | 23S | Proposed | P3 | 42 | 2THAYER.S! | VL |  |  |  |  | 0.9147 | 1.0157 | 0.92 | 1.05 | 405 | G_JTEC GEN#2 1 ID 2+1768 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JTEC GEN#2 1 ID 2 | Turn on switch shunt at Couch 69 kV sub
211253 | 23S | Proposed | P3 | 42 | 2THAYER.N | VL |  |  |  |  | 0.9162 | 1.0158 | 0.92 | 1.05 | 405 | G_JTEC GEN#2 1 ID 2+1768 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JTEC GEN#2 1 ID 2 | Turn on switch shunt at Couch 69 kV sub
211254 | 18S | Proposed | P0 | 43 | 5HORN LAKE% | VH |  |  |  |  | 1.0573 | 1.0573 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
211255 | 18S | Proposed | P0 | 43 | 8E POINT AL | VH |  |  |  |  | 1.0537 | 1.0537 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
211256 | 18S | Proposed | P0 | 43 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
211257 | 18S | Proposed | P3 | 43 | 3MT PINE.S% | VL |  |  |  |  | 0.8429 | 0.993 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211258 | 18S | Proposed | P3 | 43 | 3ROYAL | VL |  |  |  |  | 0.8532 | 0.9902 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211259 | 18S | Proposed | P3 | 43 | 3MILTON | VL |  |  |  |  | 0.8781 | 0.987 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211260 | 18S | Proposed | P3 | 43 | 3HS.W | VL |  |  |  |  | 0.8306 | 0.9888 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211261 | 18S | Proposed | P3 | 43 | 3HS.S | VL |  |  |  |  | 0.8233 | 0.9875 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211262 | 18S | Proposed | P3 | 43 | 3ALBRIGHT | VL |  |  |  |  | 0.9102 | 0.9873 | 0.92 | 1.05 | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
211263 | 18S | Proposed | P3 | 43 | 3MT PINE.S% | VL |  |  |  |  | 0.8427 | 0.993 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211264 | 18S | Proposed | P3 | 43 | 3ROYAL | VL |  |  |  |  | 0.8531 | 0.9902 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211265 | 18S | Proposed | P3 | 43 | 3MILTON | VL |  |  |  |  | 0.8779 | 0.987 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211266 | 18S | Proposed | P3 | 43 | 3HS.W | VL |  |  |  |  | 0.8304 | 0.9888 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211267 | 18S | Proposed | P3 | 43 | 3HS.S | VL |  |  |  |  | 0.8232 | 0.9875 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211268 | 18S | Proposed | P3 | 43 | 3ALBRIGHT | VL |  |  |  |  | 0.91 | 0.9873 | 0.92 | 1.05 | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
211269 | 18S | Proposed | P3 | 43 | 8DANIEL | VH |  |  |  |  | 1.0779 | 1.0433 | 0.92 | 1.05 | 54 | P1_2-1604_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
211300 | 18S | Proposed | P3 | 43 | 4VEAZIE | VL |  |  |  |  | 0.891 | 0.9782 | 0.92 | 1.05 | 139 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211301 | 18S | Proposed | P3 | 43 | GUIDRY 4 | VL |  |  |  |  | 0.8897 | 0.9769 | 0.92 | 1.05 | 139 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211302 | 18S | Proposed | P3 | 43 | PLAISAN4 | VL |  |  |  |  | 0.9051 | 0.9909 | 0.92 | 1.05 | 139 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211306 | 18S | Proposed | P3 | 43 | 4VEAZIE | VL |  |  |  |  | 0.8916 | 0.9782 | 0.92 | 1.05 | 141 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211307 | 18S | Proposed | P3 | 43 | GUIDRY 4 | VL |  |  |  |  | 0.8903 | 0.9769 | 0.92 | 1.05 | 141 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211308 | 18S | Proposed | P3 | 43 | PLAISAN4 | VL |  |  |  |  | 0.9057 | 0.9909 | 0.92 | 1.05 | 141 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211321 | 18S | Proposed | P3 | 43 | 4VEAZIE | VL |  |  |  |  | 0.8899 | 0.9782 | 0.92 | 1.05 | 146 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211322 | 18S | Proposed | P3 | 43 | GUIDRY 4 | VL |  |  |  |  | 0.8885 | 0.9769 | 0.92 | 1.05 | 146 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211323 | 18S | Proposed | P3 | 43 | PLAISAN4 | VL |  |  |  |  | 0.9039 | 0.9909 | 0.92 | 1.05 | 146 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
211327 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 162 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+12 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G3INTHB ID 1 | turn on switch shunt at BEADLE 230kV sub
211329 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 163 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+14 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G4INTHB ID 1 | turn on switch shunt at BEADLE 230kV sub
211331 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 164 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+16 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G1INTHB ID 1 | turn on switch shunt at BEADLE 230kV sub
211333 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 165 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+17 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1FRNTR 1! ID 1 | turn on switch shunt at BEADLE 230kV sub
211335 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 166 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+18 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1FRNTR 2! ID 1 | turn on switch shunt at BEADLE 230kV sub
211337 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 167 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+27 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_4TOLEDO% ID 1 | turn on switch shunt at BEADLE 230kV sub
211339 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 168 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+28 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1EXXONGT1! ID 1 | turn on switch shunt at BEADLE 230kV sub
211341 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 169 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+37 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DYNEGY_U1! ID 1 | turn on switch shunt at BEADLE 230kV sub
211343 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 170 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+38 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DYNEGY_U2! ID 1 | turn on switch shunt at BEADLE 230kV sub
211345 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 171 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+42 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_2PPG_GEN ID C4 | turn on switch shunt at BEADLE 230kV sub
211347 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 172 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+43 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_2PPG_GEN ID C5 | turn on switch shunt at BEADLE 230kV sub
211349 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 173 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+46 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1NELSON_G1! ID 1 | turn on switch shunt at BEADLE 230kV sub
211351 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 174 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+47 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1NELSON_G2! ID 1 | turn on switch shunt at BEADLE 230kV sub
211353 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9164 | 0.9848 | 0.92 | 1.05 | 175 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+75 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 | turn on switch shunt at BEADLE 230kV sub
211355 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 176 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+133 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WHT BLUF U1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211357 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 177 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+134 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WHT BLUF U2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211359 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 178 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+137 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1CATHRINE U4 ID 1 | turn on switch shunt at BEADLE 230kV sub
211361 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 179 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+143 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DUKE HS S1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211363 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 180 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+146 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ANO U1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211365 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 181 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+148 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211367 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 182 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+149 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211369 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 183 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+170 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1CAL G1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211371 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 184 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+178 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1WKRAFT! ID 3 | turn on switch shunt at BEADLE 230kV sub
211373 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9167 | 0.9848 | 0.92 | 1.05 | 185 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 | turn on switch shunt at BEADLE 230kV sub
211375 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9165 | 0.9848 | 0.92 | 1.05 | 186 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+185 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 | turn on switch shunt at BEADLE 230kV sub
211377 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9167 | 0.9848 | 0.92 | 1.05 | 187 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+188 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G7COUGH! ID 1 | turn on switch shunt at BEADLE 230kV sub
211379 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9167 | 0.9848 | 0.92 | 1.05 | 188 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+191 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211381 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.916 | 0.9848 | 0.92 | 1.05 | 189 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+192 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211383 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.916 | 0.9848 | 0.92 | 1.05 | 190 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+193 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211385 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9177 | 0.9848 | 0.92 | 1.05 | 191 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+194 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 | turn on switch shunt at BEADLE 230kV sub
211387 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 192 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+230 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_FLINTCR1 ID 1 | turn on switch shunt at BEADLE 230kV sub
211389 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.9168 | 0.9848 | 0.92 | 1.05 | 193 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+235 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_MUSKOG4G ID 1 | turn on switch shunt at BEADLE 230kV sub
211391 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.8948 | 0.9848 | 0.92 | 1.05 | 194 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+192 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
211392 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.8948 | 0.9848 | 0.92 | 1.05 | 195 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+193 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
211393 | 18S | Proposed | P3 | 43 | ELKS 6 | VL |  |  |  |  | 0.901 | 0.9848 | 0.92 | 1.05 | 196 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+194 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
211394 | 18S | Proposed | P3 | 43 | 4NBUNA | VL |  |  |  |  | 0.9183 | 0.9994 | 0.92 | 1.05 | 204 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334304 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211395 | 18S | Proposed | P3 | 43 | 4BUNASW | VL |  |  |  |  | 0.9183 | 0.9995 | 0.92 | 1.05 | 204 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334305 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211396 | 18S | Proposed | P3 | 43 | 4TEMPLE | VL |  |  |  |  | 0.9183 | 0.9995 | 0.92 | 1.05 | 204 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334306 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211397 | 18S | Proposed | P3 | 43 | 4BUNA! | VL |  |  |  |  | 0.9176 | 1.0012 | 0.92 | 1.05 | 204 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334307 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211398 | 18S | Proposed | P3 | 43 | 2NECHESO | VL |  |  |  |  | 0.9138 | 0.9428 | 0.92 | 1.05 | 207 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211399 | 18S | Proposed | P3 | 43 | 2NECHESO | VL |  |  |  |  | 0.9134 | 0.9428 | 0.92 | 1.05 | 208 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211400 | 18S | Proposed | P3 | 43 | 2NECHESO | VL |  |  |  |  | 0.9142 | 0.9428 | 0.92 | 1.05 | 209 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 |  | Facility: Radial
211401 | 18S | Proposed | P3 | 43 | 2NECHESO | VL |  |  |  |  | 0.9119 | 0.9428 | 0.92 | 1.05 | 210 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
211402 | 18S | Proposed | P3 | 43 | 4NEW_IBERIA! | VL |  |  |  |  | 0.8986 | 0.9953 | 0.92 | 1.05 | 269 | G_G3TECHE! ID 1+P1_2-568_4MORIL!,4CECELIA! | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-568_4MORIL!,4CECELIA! | G_G3TECHE! ID 1 |  | Contingency: Trip bus as result of con
211409 | 15S | Approved | P2 | 44 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 420.4 | 295.5 | 448 | 93.8 |  |  |  |  | 4 | 8MABELVALE% - 8WRIGHTSVLE% 500 1+ 8MABELVALE% 500/ | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8WRIGHTSVLE% 500 1 | 8MABELVALE% 500/ | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211410 | 15S | Approved | P2 | 44 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 409.2 | 295.5 | 448 | 91.3 |  |  |  |  | 5 | 8MABELVALE% - 8ANO% 500 1+ 8MABELVALE% 500/115 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8ANO% 500 1 | 8MABELVALE% 500/115 | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211411 | 15S | Approved | P2 | 44 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 447.8 | 295.5 | 448 | 99.9 |  |  |  |  | 6 | 8MABELVALE% - 8MAYFLOWER% 500 1 + 8MABELVALE% 500 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8MAYFLOWER% 500 1 | 8MABELVALE% 500 | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211412 | 15S | Approved | P2 | 44 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 482.7 | 229.3 | 420 | 114.9 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MAYFLOWER% 500/115 1 | 8MAYFLOWER% 500/115 2 | Project Proposed |  | 12-EAI-021-CP | 2017-12-01 | Reconfigure Mayflower 500 kV bus to eliminate breaker failure impact on transformers
211413 | 15S | Approved | P2 | 44 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 335 | 166.2 | 266 | 125.9 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211414 | 15S | Approved | P2 | 44 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 300.3 | 128.2 | 266 | 112.9 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211415 | 15S | Approved | P2 | 44 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 151.5 | 72.6 | 148 | 102.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211416 | 15S | Approved | P2 | 44 | 336525 3SMITHDALE+ 115 336526 3ARLINGTON+ 115 1 | LN | 149.9 | 96.7 | 161 | 93.1 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336525 | 336526 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211417 | 15S | Approved | P2 | 44 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 158.5 | 103.9 | 161 | 98.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211418 | 15S | Approved | P2 | 44 | 336551 3MCCOMB! 115 336552 3NORFIELD+ 115 1 | LN | 187.6 | 102.3 | 199 | 94.3 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336551 | 336552 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211419 | 15S | Approved | P2 | 44 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 204.7 | 120.5 | 199 | 102.9 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211420 | 15S | Approved | P2 | 44 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 228.3 | 141.5 | 199 | 114.7 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211421 | 15S | Approved | P6 | 44 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | LN | 145.8 | 50.3 | 120 | 121.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336500 | 336785 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211422 | 15S | Approved | P6 | 44 | 336785 3FAYETTE 115 336786 3LORMAN+ 115 1 | LN | 164.8 | 63.8 | 161 | 102.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336785 | 336786 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211423 | 15S | Approved | P6 | 44 | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 | LN | 173.9 | 75.9 | 161 | 108 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336786 | 336788 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211424 | 15S | Approved | P6 | 44 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 209.7 | 104.3 | 161 | 130.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211425 | 15S | Approved | P6 | 44 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | LN | 230 | 126.2 | 199 | 115.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336790 | 336800 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211426 | 15S | Approved | P6 | 44 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 322.4 | 129.5 | 239 | 134.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
211427 | 15S | Approved | P6 | 44 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 196.1 | 85.6 | 161 | 121.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
211428 | 15S | Approved | P6 | 44 | 336804 3VICKSBURG! 115 336805 3WATERWAYS 115 1 | LN | 379 | 107.6 | 239 | 158.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336804 | 336805 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211429 | 15S | Approved | P6 | 44 | 336805 3WATERWAYS 115 336806 3E.VICKSBRG+ 115 1 | LN | 364 | 97 | 260 | 140 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336805 | 336806 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211430 | 15S | Approved | P6 | 44 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 339.4 | 77.8 | 161 | 210.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211431 | 15S | Approved | P6 | 44 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 325.3 | 67.7 | 161 | 202 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211432 | 15S | Approved | P6 | 44 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 301.7 | 33 | 161 | 187.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211433 | 15S | Approved | P6 | 44 | 336960 3SE.VICKSBRG 115 336961 3BOVINA 115 1 | LN | 182.7 | 75.9 | 176 | 103.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336960 | 336961 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211434 | 15S | Approved | P6 | 44 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 178.7 | 58.7 | 111 | 161 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211435 | 15S | Approved | P6 | 44 | 336967 3ONWARD+ 115 336968 3ROLING FRK! 115 1 | LN | 101.3 | 33.9 | 111 | 91.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336967 | 336968 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211436 | 15S | Approved | P6 | 44 | 336974 3TINSLEY+ 115 336976 3FLOWERS+ 115 1 | LN | 170.3 | 51.7 | 161 | 105.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211437 | 15S | Approved | P6 | 44 | 336974 3TINSLEY+ 115 336977 3YAZOO MUNI! 115 1 | LN | 154.3 | 32.2 | 161 | 95.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336977 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211438 | 15S | Approved | P6 | 44 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 113.6 | 70.8 | 115 | 98.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211439 | 15S | Approved | P3 | 44 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 289.7 | 209.2 | 320 | 90.5 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WAT U3! 25.0 Id:1 |  | No violation: below Rate A
211440 | 15S | Approved | P3 | 44 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 630.9 | 477 | 672 | 93.9 |  |  |  |  | 12 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211441 | 15S | Approved | P3 | 44 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 627.9 | 477 | 672 | 93.4 |  |  |  |  | 13 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211442 | 15S | Approved | P3 | 44 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 615.9 | 477 | 672 | 91.7 |  |  |  |  | 14 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211443 | 15S | Approved | P3 | 44 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 616.5 | 477 | 672 | 91.7 |  |  |  |  | 15 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211444 | 15S | Approved | P3 | 44 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1292.1 | 300.5 | 1069 | 120.9 |  |  |  |  | 16 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211445 | 15S | Approved | P3 | 44 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 658 | 477 | 672 | 97.9 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211446 | 15S | Approved | P3 | 44 | 335601 4WILLOW_GL2! 138 335618 8WILLOW_GL% 500 1 | TR | 515.8 | 376.7 | 560 | 92.1 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335601 | 335618 | 1 |  | 500 | 138 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 |  | No violation: below Rate A
211447 | 15S | Approved | P3 | 44 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1277.2 | 815.4 | 1186 | 107.7 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211448 | 15S | Approved | P3 | 44 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 202.5 | 86.1 | 206 | 98.3 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211449 | 15S | Approved | P3 | 44 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 202.4 | 86.1 | 206 | 98.2 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211450 | 15S | Approved | P3 | 44 | 334204 6CHINA% 230 334327 6AMELIA! 230 1 | LN | 722.9 | 363.6 | 797 | 90.7 |  |  |  |  | 26 | 6CHINA% - 6SABINE% 230 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334327 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6CHINA% - 6SABINE% 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211452 | 15S | Approved | P3 | 44 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 498.1 | 330.3 | 470 | 106 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Reduce PPG Plant
211453 | 15S | Approved | P3 | 44 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 288.9 | 163.9 | 288 | 100.3 |  |  |  |  | 28 | 4PNEC BK! - 4SABINE! 138 1 +1G4SABIN! 24.0 Id:1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4PNEC BK! - 4SABINE! 138 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
211454 | 15S | Approved | P1 | 44 | 334254 2QUALTY 69.0 334255 2BATSON! 69.0 NO | LN | 26.5 | 0 | 29.3 | 90.4 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334254 | 334255 | NO |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211455 | 15S | Approved | P1 | 44 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 35.8 | 12.3 | 29.3 | 122.1 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211456 | 15S | Approved | P1 | 44 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 36.4 | 12.3 | 29.3 | 124.3 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211457 | 15S | Approved | P1 | 44 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 36.9 | 12.4 | 29.3 | 126.1 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211458 | 15S | Approved | P1 | 44 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 37.4 | 12.3 | 29.3 | 127.7 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211459 | 15S | Approved | P1 | 44 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 26.9 | 12.3 | 29.3 | 91.7 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211460 | 15S | Approved | P1 | 44 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 27.6 | 12.4 | 29.3 | 94.3 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211461 | 15S | Approved | P1 | 44 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 28.3 | 12.3 | 29.3 | 96.7 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211463 | 15S | Approved | P3 | 44 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 751.5 | 232.7 | 560 | 134.2 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211477 | 23S | Approved | P6 | 45 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159.9 | 123.8 | 159 | 100.5 |  |  |  |  | 3 | 8SHERIDAN% - 8MABELVALE% 500 1+ 8MABELVALE% 500/11 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8MABELVALE% 500 1 | 8MABELVALE% 500/11 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
211478 | 23S | Approved | P2 | 45 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 145.5 | 123.8 | 159 | 91.5 |  |  |  |  | 4 | 8MABELVALE% - 8WRIGHTSVLE% 500 1+ 8MABELVALE% 500/ | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8WRIGHTSVLE% 500 1 | 8MABELVALE% 500/ | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
211479 | 23S | Approved | P2 | 45 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 417.9 | 295.9 | 448 | 93.3 |  |  |  |  | 4 | 8MABELVALE% - 8WRIGHTSVLE% 500 1+ 8MABELVALE% 500/ | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8WRIGHTSVLE% 500 1 | 8MABELVALE% 500/ | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211480 | 23S | Approved | P2 | 45 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 144.8 | 123.8 | 159 | 91 |  |  |  |  | 5 | 8MABELVALE% - 8ANO% 500 1+ 8MABELVALE% 500/115 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8ANO% 500 1 | 8MABELVALE% 500/115 | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
211481 | 23S | Approved | P2 | 45 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 413 | 295.9 | 448 | 92.2 |  |  |  |  | 5 | 8MABELVALE% - 8ANO% 500 1+ 8MABELVALE% 500/115 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8ANO% 500 1 | 8MABELVALE% 500/115 | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211482 | 23S | Approved | P2 | 45 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 149.6 | 123.8 | 159 | 94.1 |  |  |  |  | 6 | 8MABELVALE% - 8MAYFLOWER% 500 1 + 8MABELVALE% 500 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8MAYFLOWER% 500 1 | 8MABELVALE% 500 | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
211483 | 23S | Approved | P2 | 45 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 456.3 | 295.9 | 448 | 101.9 |  |  |  |  | 6 | 8MABELVALE% - 8MAYFLOWER% 500 1 + 8MABELVALE% 500 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8MAYFLOWER% 500 1 | 8MABELVALE% 500 | Project Proposed |  | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211484 | 23S | Approved | P2 | 45 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 482.5 | 229.8 | 420 | 114.9 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MAYFLOWER% 500/115 1 | 8MAYFLOWER% 500/115 2 | Project Proposed |  | 12-EAI-021-CP | 2017-12-01 | Reconfigure Mayflower 500 kV bus to eliminate breaker failure impact on transformers
211485 | 23S | Approved | P2 | 45 | 337996 3BRINKLEY.E! 115 338014 3BRINKLEY.W 115 1 | LN | 161.5 | 9.1 | 159 | 101.6 |  |  |  |  | 8 | ISES 161kV bus #1 | 337996 | 338014 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211486 | 23S | Approved | P2 | 45 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 433.2 | 202.2 | 266 | 162.9 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211487 | 23S | Approved | P2 | 45 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 388.5 | 162.4 | 266 | 146.1 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211488 | 23S | Approved | P2 | 45 | 338007 3BEEBE 115 338756 3WARD# 115 1 | LN | 261.7 | 52.7 | 266 | 98.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338007 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211489 | 23S | Approved | P2 | 45 | 338010 3SRCY PRICE! 115 338045 5SRCY PRICE! 161 1 | TR | 208.2 | 77.3 | 225 | 92.5 |  |  |  |  | 8 | ISES 161kV bus #1 | 338010 | 338045 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211490 | 23S | Approved | P2 | 45 | 338013 3COTTON PLNT 115 338014 3BRINKLEY.W 115 1 | LN | 150.9 | 12.3 | 159 | 94.9 |  |  |  |  | 8 | ISES 161kV bus #1 | 338013 | 338014 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211491 | 23S | Approved | P2 | 45 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.7 | 108.5 | 148 | 92.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211492 | 23S | Approved | P2 | 45 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145.2 | 115.6 | 160 | 90.7 |  |  |  |  | 8 | ISES 161kV bus #1 | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Approved | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211493 | 23S | Approved | P2 | 45 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 154.4 | 82.5 | 148 | 104.3 |  |  |  |  | 8 | ISES 161kV bus #1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211494 | 23S | Approved | P2 | 45 | 336525 3SMITHDALE+ 115 336526 3ARLINGTON+ 115 1 | LN | 152.2 | 103.1 | 161 | 94.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336525 | 336526 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211495 | 23S | Approved | P2 | 45 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 161.6 | 111.3 | 161 | 100.4 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211496 | 23S | Approved | P2 | 45 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 188.2 | 110.3 | 199 | 94.6 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211497 | 23S | Approved | P2 | 45 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 214 | 132.9 | 199 | 107.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211498 | 23S | Approved | P6 | 45 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | LN | 131.5 | 46.6 | 120 | 109.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336500 | 336785 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211499 | 23S | Approved | P6 | 45 | 336785 3FAYETTE 115 336786 3LORMAN+ 115 1 | LN | 151.4 | 59.7 | 161 | 94 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336785 | 336786 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211500 | 23S | Approved | P6 | 45 | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 | LN | 162.2 | 73.6 | 161 | 100.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336786 | 336788 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211501 | 23S | Approved | P6 | 45 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 198.7 | 103.7 | 161 | 123.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211502 | 23S | Approved | P6 | 45 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | LN | 220.3 | 126 | 199 | 110.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336790 | 336800 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211503 | 23S | Approved | P6 | 45 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 297.6 | 125.9 | 239 | 124.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
211504 | 23S | Approved | P6 | 45 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 184.6 | 86.5 | 161 | 114.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
211505 | 23S | Approved | P6 | 45 | 336804 3VICKSBURG! 115 336805 3WATERWAYS 115 1 | LN | 332.1 | 88.7 | 239 | 139 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336804 | 336805 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211506 | 23S | Approved | P6 | 45 | 336805 3WATERWAYS 115 336806 3E.VICKSBRG+ 115 1 | LN | 318.7 | 78.1 | 260 | 122.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336805 | 336806 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211507 | 23S | Approved | P6 | 45 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 294.7 | 57.7 | 161 | 183.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211508 | 23S | Approved | P6 | 45 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 282.7 | 48 | 161 | 175.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211509 | 23S | Approved | P6 | 45 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 252.5 | 23.1 | 161 | 156.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211510 | 23S | Approved | P6 | 45 | 336960 3SE.VICKSBRG 115 336961 3BOVINA 115 1 | LN | 171.3 | 76.3 | 176 | 97.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336960 | 336961 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211511 | 23S | Approved | P6 | 45 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 161 | 54 | 111 | 145.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211512 | 23S | Approved | P6 | 45 | 336967 3ONWARD+ 115 336968 3ROLING FRK! 115 1 | LN | 104.5 | 48 | 111 | 94.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336967 | 336968 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211513 | 23S | Approved | P6 | 45 | 336974 3TINSLEY+ 115 336976 3FLOWERS+ 115 1 | LN | 153.3 | 47 | 161 | 95.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211514 | 23S | Approved | P6 | 45 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 117.6 | 80.2 | 115 | 102.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211515 | 23S | Approved | P6 | 45 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 302.4 | 271.2 | 335 | 90.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE |  | No violation: CLECO facility, loading is less than rate B 360MVA
211516 | 23S | Approved | P3 | 45 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 294.8 | 216.8 | 320 | 92.1 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WAT U3! 25.0 Id:1 |  | No violation: below Rate A
211517 | 23S | Approved | P3 | 45 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 646 | 391.5 | 672 | 96.1 |  |  |  |  | 12 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211518 | 23S | Approved | P3 | 45 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 616.8 | 391.5 | 672 | 91.8 |  |  |  |  | 13 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211519 | 23S | Approved | P3 | 45 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1290 | 294.8 | 1069 | 120.7 |  |  |  |  | 16 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211520 | 23S | Approved | P3 | 45 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1323.1 | 857.2 | 1186 | 111.6 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211521 | 23S | Approved | P3 | 45 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 305.1 | 271.2 | 335 | 91.1 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
211523 | 23S | Approved | P3 | 45 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 234.2 | 181 | 243 | 96.4 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
211524 | 23S | Approved | P3 | 45 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 185.8 | 64.1 | 206 | 90.2 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211525 | 23S | Approved | P3 | 45 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 215.2 | 91.6 | 206 | 104.5 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211526 | 23S | Approved | P3 | 45 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 686.9 | 326.5 | 753 | 91.2 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211527 | 23S | Approved | P3 | 45 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 682.5 | 310.8 | 749 | 91.1 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211528 | 23S | Approved | P3 | 45 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 682.5 | 310.8 | 753 | 90.6 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211529 | 23S | Approved | P3 | 45 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 207.5 | 126.2 | 206 | 100.7 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211530 | 23S | Approved | P3 | 45 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 228 | 126.2 | 206 | 110.7 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211531 | 23S | Approved | P3 | 45 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 192.7 | 93.6 | 206 | 93.5 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211533 | 23S | Approved | P3 | 45 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 233.9 | 181 | 243 | 96.2 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
211534 | 23S | Approved | P3 | 45 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 185.8 | 64.1 | 206 | 90.2 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211535 | 23S | Approved | P3 | 45 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 215 | 91.6 | 206 | 104.4 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211536 | 23S | Approved | P3 | 45 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 686 | 326.5 | 753 | 91.1 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211537 | 23S | Approved | P3 | 45 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 682.6 | 310.8 | 749 | 91.1 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211538 | 23S | Approved | P3 | 45 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 682.6 | 310.8 | 753 | 90.6 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
211539 | 23S | Approved | P3 | 45 | 334360 6HELBIG! 230 334364 6GEOTOWN! 230 1 | LN | 324.5 | 158 | 351 | 92.4 |  |  |  |  | 24 | 6CHINA% - 6SABINE% 230 1 + 1FRNTR 1! 18.0 Id:1 | 334360 | 334364 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6CHINA% - 6SABINE% 230 1 | 1FRNTR 1! 18.0 Id:1 |  | No violation: below Rate A
211542 | 23S | Approved | P3 | 45 | 334360 6HELBIG! 230 334364 6GEOTOWN! 230 1 | LN | 331.2 | 158 | 351 | 94.4 |  |  |  |  | 26 | 6CHINA% - 6SABINE% 230 1 + 1G1LEWIS! 22.0 Id:1 | 334360 | 334364 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6CHINA% - 6SABINE% 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211544 | 23S | Approved | P3 | 45 | 334282 4RAYBURN% 138 334330 4JASPER 138 1 | LN | 126.6 | 45.5 | 137 | 92.4 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334282 | 334330 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211545 | 23S | Approved | P3 | 45 | 334325 8HARTBRG% 500 334363 6HARTBRG! 230 1 | TR | 748.8 | 291.5 | 801 | 93.5 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334325 | 334363 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211546 | 23S | Approved | P3 | 45 | 334333 4NEWTONB! 138 334334 4LEACH 138 1 | LN | 142.8 | 84.4 | 143 | 99.8 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334333 | 334334 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211547 | 23S | Approved | P3 | 45 | 334334 4LEACH 138 334335 4TOLEDO% 138 1 | LN | 146.1 | 87.2 | 145 | 100.7 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334334 | 334335 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed |  | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211548 | 23S | Approved | P3 | 45 | 334360 6HELBIG! 230 334361 6MCLEWIS 230 1 | LN | 635.5 | 219.6 | 681 | 93.3 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334360 | 334361 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211549 | 23S | Approved | P3 | 45 | 334412 4MID CO% 138 334413 4PNEC BK! 138 1 | LN | 255.5 | 189.1 | 282 | 90.6 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334412 | 334413 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211550 | 23S | Approved | P3 | 45 | 334434 6SABINE% 230 335071 6BIG_THREE 230 1 | LN | 536.1 | 188.1 | 595 | 90.1 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334434 | 335071 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
211551 | 23S | Approved | P3 | 45 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 423.6 | 256.4 | 470 | 90.1 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Reduce PPG Plant | No violation: below Rate A
211553 | 23S | Approved | P3 | 45 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 302.2 | 172.3 | 288 | 104.9 |  |  |  |  | 28 | 4PNEC BK! - 4SABINE! 138 1 +1G4SABIN! 24.0 Id:1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4PNEC BK! - 4SABINE! 138 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
211555 | 23S | Approved | P3 | 45 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 216.3 | 126.2 | 206 | 105 |  |  |  |  | 29 | 7GRIMES% - CROCKET7 345 1 +1FRNTR 1! 18.0 Id:1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 7GRIMES% - CROCKET7 345 1 | 1FRNTR 1! 18.0 Id:1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211556 | 23S | Approved | P1 | 45 | 334252 26L594TAP 69.0 334254 2QUALTY 69.0 1 | LN | 26.8 | 2.3 | 29.3 | 91.4 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334252 | 334254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211557 | 23S | Approved | P1 | 45 | 334254 2QUALTY 69.0 334255 2BATSON! 69.0 NO | LN | 27.6 | 0 | 29.3 | 94.1 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334254 | 334255 | NO |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211558 | 23S | Approved | P1 | 45 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 35.7 | 12.3 | 29.3 | 122 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211559 | 23S | Approved | P1 | 45 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 36.9 | 12.4 | 29.3 | 125.9 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211560 | 23S | Approved | P1 | 45 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 37.9 | 12.5 | 29.3 | 129.5 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211561 | 23S | Approved | P1 | 45 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 38.7 | 12.6 | 29.3 | 132.2 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211564 | 23S | Approved | P1 | 45 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 27.2 | 12.3 | 29.3 | 92.9 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211565 | 23S | Approved | P1 | 45 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 28.5 | 12.4 | 29.3 | 97.4 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211566 | 23S | Approved | P1 | 45 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 29.4 | 12.5 | 29.3 | 100.3 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211567 | 23S | Approved | P1 | 45 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 30.2 | 12.6 | 29.3 | 103.1 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211569 | 23S | Approved | P3 | 45 | 334333 4NEWTONB! 138 334334 4LEACH 138 1 | LN | 130 | 84.4 | 143 | 90.9 |  |  |  |  | 34 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4! | 334333 | 334334 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4! | Project Proposed | No violation: below Rate A | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211570 | 23S | Approved | P3 | 45 | 334334 4LEACH 138 334335 4TOLEDO% 138 1 | LN | 133.2 | 87.2 | 145 | 91.9 |  |  |  |  | 34 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4! | 334334 | 334335 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4! | Project Proposed | No violation: below Rate A | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211572 | 23S | Approved | P3 | 45 | 334333 4NEWTONB! 138 334334 4LEACH 138 1 | LN | 145.8 | 84.4 | 143 | 102 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 334333 | 334334 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211573 | 23S | Approved | P3 | 45 | 334334 4LEACH 138 334335 4TOLEDO% 138 1 | LN | 149.1 | 87.2 | 145 | 102.9 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 334334 | 334335 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211574 | 23S | Approved | P3 | 45 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 647.4 | 319.7 | 560 | 115.6 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211580 | 15S | Proposed | P2 | 46 | 337620 3WOODWARD-N! 115 337634 3DIERKS! 115 1 | LN | 95.6 | 39.8 | 98 | 97.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337620 | 337634 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211581 | 15S | Proposed | P2 | 46 | 337633 6WOODWARD! 230 337654 6WHT BLUFF% 230 1 | LN | 639.3 | 282.9 | 519 | 123.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337654 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211582 | 15S | Proposed | P2 | 46 | 337633 6WOODWARD! 230 337968 6RICUSKEY% 230 1 | LN | 379.5 | 165.3 | 342 | 111 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337968 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211583 | 15S | Proposed | P2 | 46 | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | LN | 259.1 | 69 | 253 | 102.4 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337649 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211584 | 15S | Proposed | P2 | 46 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 1 | TR | 537.7 | 187.1 | 420 | 128 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211585 | 15S | Proposed | P2 | 46 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 2 | TR | 537.7 | 187.1 | 420 | 128 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211586 | 15S | Proposed | P2 | 46 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 315.1 | 39.9 | 253 | 124.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211587 | 15S | Proposed | P2 | 46 | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | LN | 249.3 | 62.3 | 253 | 98.6 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337649 | 337855 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211588 | 15S | Proposed | P2 | 46 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | LN | 96.3 | 59 | 106 | 90.8 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337967 | 337969 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211589 | 15S | Proposed | P2 | 46 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 410.6 | 288.2 | 448 | 91.6 |  |  |  |  | 4 | 8MABELVALE% - 8WRIGHTSVLE% 500 1+ 8MABELVALE% 500/ | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8WRIGHTSVLE% 500 1 | 8MABELVALE% 500/ | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211590 | 15S | Proposed | P2 | 46 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 435.1 | 288.2 | 448 | 97.1 |  |  |  |  | 6 | 8MABELVALE% - 8MAYFLOWER% 500 1 + 8MABELVALE% 500 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MABELVALE% - 8MAYFLOWER% 500 1 | 8MABELVALE% 500 | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
211591 | 15S | Proposed | P2 | 46 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 474.9 | 225.7 | 420 | 113.1 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MAYFLOWER% 500/115 1 | 8MAYFLOWER% 500/115 2 | Project Proposed |  | 12-EAI-021-CP | 2017-12-01 | Reconfigure Mayflower 500 kV bus to eliminate breaker failure impact on transformers
211592 | 15S | Proposed | P2 | 46 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 323.5 | 160.1 | 266 | 121.6 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211593 | 15S | Proposed | P2 | 46 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 288.4 | 123.1 | 266 | 108.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211594 | 15S | Proposed | P2 | 46 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 151.5 | 72.4 | 148 | 102.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211595 | 15S | Proposed | P2 | 46 | 336525 3SMITHDALE+ 115 336526 3ARLINGTON+ 115 1 | LN | 150.5 | 96.4 | 161 | 93.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336525 | 336526 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211596 | 15S | Proposed | P2 | 46 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 159 | 103.5 | 161 | 98.8 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211597 | 15S | Proposed | P2 | 46 | 336551 3MCCOMB! 115 336552 3NORFIELD+ 115 1 | LN | 188.8 | 102.6 | 199 | 94.9 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336551 | 336552 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211598 | 15S | Proposed | P2 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 206 | 120.7 | 199 | 103.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211599 | 15S | Proposed | P2 | 46 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 229.7 | 141.8 | 199 | 115.4 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211600 | 15S | Proposed | P6 | 46 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | LN | 104.7 | 65.2 | 115 | 91.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 303325 | 337331 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211601 | 15S | Proposed | P6 | 46 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | LN | 143.6 | 50.8 | 120 | 119.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336500 | 336785 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211602 | 15S | Proposed | P6 | 46 | 336785 3FAYETTE 115 336786 3LORMAN+ 115 1 | LN | 162.5 | 65.1 | 161 | 100.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336785 | 336786 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211603 | 15S | Proposed | P6 | 46 | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 | LN | 172.3 | 76.6 | 161 | 107 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336786 | 336788 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211604 | 15S | Proposed | P6 | 46 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 208.5 | 104.8 | 161 | 129.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211605 | 15S | Proposed | P6 | 46 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | LN | 228.8 | 127.3 | 199 | 115 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336790 | 336800 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211606 | 15S | Proposed | P6 | 46 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 321.6 | 129.6 | 320 | 100.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
211607 | 15S | Proposed | P6 | 46 | 336804 3VICKSBURG! 115 336805 3WATERWAYS 115 1 | LN | 379 | 108.4 | 239 | 158.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336804 | 336805 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211608 | 15S | Proposed | P6 | 46 | 336805 3WATERWAYS 115 336806 3E.VICKSBRG+ 115 1 | LN | 364 | 97.8 | 260 | 140 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336805 | 336806 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211609 | 15S | Proposed | P6 | 46 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 339.2 | 78.5 | 161 | 210.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211610 | 15S | Proposed | P6 | 46 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 325.1 | 68.4 | 161 | 201.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211611 | 15S | Proposed | P6 | 46 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 301.6 | 33.3 | 161 | 187.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211612 | 15S | Proposed | P6 | 46 | 336960 3SE.VICKSBRG 115 336961 3BOVINA 115 1 | LN | 181.8 | 75.7 | 176 | 103.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336960 | 336961 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211613 | 15S | Proposed | P6 | 46 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 177.7 | 58.4 | 111 | 160.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211614 | 15S | Proposed | P6 | 46 | 336967 3ONWARD+ 115 336968 3ROLING FRK! 115 1 | LN | 100.1 | 33.3 | 111 | 90.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336967 | 336968 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211615 | 15S | Proposed | P6 | 46 | 336974 3TINSLEY+ 115 336976 3FLOWERS+ 115 1 | LN | 169.4 | 51.4 | 161 | 105.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211616 | 15S | Proposed | P6 | 46 | 336974 3TINSLEY+ 115 336977 3YAZOO MUNI! 115 1 | LN | 153.6 | 32 | 161 | 95.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336977 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211617 | 15S | Proposed | P6 | 46 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 119.3 | 77.2 | 115 | 103.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211618 | 15S | Proposed | P3 | 46 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 289.6 | 209.1 | 320 | 90.5 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WAT U3! 25.0 Id:1 |  | No violation: below Rate A
211619 | 15S | Proposed | P3 | 46 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 632.6 | 479.8 | 672 | 94.1 |  |  |  |  | 12 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211620 | 15S | Proposed | P3 | 46 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 629.2 | 479.8 | 672 | 93.6 |  |  |  |  | 13 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211621 | 15S | Proposed | P3 | 46 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 617.5 | 479.8 | 672 | 91.9 |  |  |  |  | 14 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211622 | 15S | Proposed | P3 | 46 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 618 | 479.8 | 672 | 92 |  |  |  |  | 15 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211623 | 15S | Proposed | P3 | 46 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1293.8 | 300.9 | 1069 | 121 |  |  |  |  | 16 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211624 | 15S | Proposed | P3 | 46 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 658 | 479.8 | 672 | 97.9 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211625 | 15S | Proposed | P3 | 46 | 335601 4WILLOW_GL2! 138 335618 8WILLOW_GL% 500 1 | TR | 515.5 | 376.3 | 560 | 92.1 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335601 | 335618 | 1 |  | 500 | 138 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
211626 | 15S | Proposed | P3 | 46 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1276.7 | 814 | 1186 | 107.6 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
211627 | 15S | Proposed | P3 | 46 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 195.3 | 124.5 | 206 | 94.8 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211628 | 15S | Proposed | P3 | 46 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 187.9 | 117.6 | 206 | 91.2 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id | Project Proposed | No violation: below Rate A | 13-ETI-014-CP | 2019-06-01 | Reconductor Panorama-Longmire 138 kV
211629 | 15S | Proposed | P3 | 46 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 204.1 | 124.5 | 206 | 99.1 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
211630 | 15S | Proposed | P3 | 46 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 196.9 | 117.6 | 206 | 95.6 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed | No violation: below Rate A | 13-ETI-014-CP | 2019-06-01 | Reconductor Panorama-Longmire 138 kV
211631 | 15S | Proposed | P3 | 46 | 334204 6CHINA% 230 334327 6AMELIA! 230 1 | LN | 724.6 | 363.1 | 797 | 90.9 |  |  |  |  | 26 | 6CHINA% - 6SABINE% 230 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334327 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6CHINA% - 6SABINE% 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211632 | 15S | Proposed | P3 | 46 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 496.1 | 330 | 470 | 105.5 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Reduce PPG Plant
211633 | 15S | Proposed | P3 | 46 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 287.2 | 162.9 | 288 | 99.7 |  |  |  |  | 28 | 4PNEC BK! - 4SABINE! 138 1 +1G4SABIN! 24.0 Id:1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4PNEC BK! - 4SABINE! 138 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
211634 | 15S | Proposed | P1 | 46 | 334254 2QUALTY 69.0 334255 2BATSON! 69.0 NO | LN | 26.5 | 0 | 29.3 | 90.6 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334254 | 334255 | NO |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211635 | 15S | Proposed | P1 | 46 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 35.9 | 12.3 | 29.3 | 122.4 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211636 | 15S | Proposed | P1 | 46 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 36.5 | 12.3 | 29.3 | 124.5 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211637 | 15S | Proposed | P1 | 46 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 37 | 12.4 | 29.3 | 126.3 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211638 | 15S | Proposed | P1 | 46 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 37.5 | 12.4 | 29.3 | 127.9 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1 | Batson - Quality Mills clos | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211639 | 15S | Proposed | P1 | 46 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 26.9 | 12.3 | 29.3 | 91.7 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211640 | 15S | Proposed | P1 | 46 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 27.6 | 12.4 | 29.3 | 94.4 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211641 | 15S | Proposed | P1 | 46 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 28.4 | 12.4 | 29.3 | 96.8 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211643 | 15S | Proposed | P3 | 46 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 757.7 | 223.8 | 560 | 135.3 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
211649 | 18L | Proposed | P2 | 47 | 337633 6WOODWARD! 230 337654 6WHT BLUFF% 230 1 | LN | 488.3 | 193.1 | 519 | 94.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337654 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
211650 | 18L | Proposed | P2 | 47 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 1 | TR | 407.9 | 122.7 | 420 | 97.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
211651 | 18L | Proposed | P2 | 47 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 2 | TR | 407.9 | 122.7 | 420 | 97.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
211652 | 18L | Proposed | P2 | 47 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 231.9 | 8.9 | 253 | 91.6 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
211653 | 18L | Proposed | P6 | 47 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 181.9 | 22.2 | 161 | 113 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211654 | 18L | Proposed | P6 | 47 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 178.6 | 18 | 161 | 110.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211655 | 18L | Proposed | P6 | 47 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 158.5 | 21.1 | 161 | 98.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211667 | 18W | Proposed | P2 | 48 | 337620 3WOODWARD% 115 337647 3ARSENAL D 115 1 | LN | 220.5 | 110.4 | 239 | 92.3 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337620 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211668 | 18W | Proposed | P2 | 48 | 337633 6WOODWARD! 230 337654 6WHT BLUFF% 230 1 | LN | 622.4 | 239.6 | 519 | 119.9 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337654 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211669 | 18W | Proposed | P2 | 48 | 337633 6WOODWARD! 230 337968 6RICUSKEY% 230 1 | LN | 342.9 | 116.6 | 342 | 100.3 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337968 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211670 | 18W | Proposed | P2 | 48 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 227.9 | 116 | 253 | 90.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211671 | 18W | Proposed | P2 | 48 | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | LN | 247.2 | 37.1 | 253 | 97.7 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337649 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211672 | 18W | Proposed | P2 | 48 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 1 | TR | 525.9 | 152.1 | 420 | 125.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211673 | 18W | Proposed | P2 | 48 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 2 | TR | 525.9 | 152.1 | 420 | 125.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211674 | 18W | Proposed | P2 | 48 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 304.8 | 17.9 | 253 | 120.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211675 | 18W | Proposed | P2 | 48 | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | LN | 241.1 | 32.3 | 253 | 95.3 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337649 | 337855 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211676 | 18W | Proposed | P2 | 48 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 298.8 | 141.6 | 266 | 112.3 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP |  | 2018-06-01 | Reconfigure ISES 161 kV Bus
211677 | 18W | Proposed | P2 | 48 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 266.9 | 111.7 | 266 | 100.3 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211678 | 18W | Proposed | P2 | 48 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 196.4 | 112.3 | 199 | 98.7 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211679 | 18W | Proposed | P2 | 48 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 217.3 | 129.6 | 199 | 109.2 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211680 | 18W | Proposed | P3 | 48 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 187.3 | 98.2 | 206 | 90.9 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed | No violation: below Rate A | 13-ETI-014-CP | 2019-06-01 | Reconductor Panorama-Longmire 138 kV
211685 | 18W | Proposed | P1 | 48 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 27.6 | 12 | 29.3 | 94.1 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi |  | No violation: below Rate A
211686 | 18W | Proposed | P1 | 48 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 28.4 | 12 | 29.3 | 97 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi |  | No violation: below Rate A
211687 | 18W | Proposed | P1 | 48 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 29 | 12.1 | 29.3 | 99 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi |  | No violation: below Rate A
211688 | 18W | Proposed | P1 | 48 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 29.7 | 12.1 | 29.3 | 101.2 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed |  | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
211700 | 23S | Proposed | P2 | 49 | 337633 6WOODWARD! 230 337654 6WHT BLUFF% 230 1 | LN | 641.3 | 278.8 | 519 | 123.6 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337654 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211701 | 23S | Proposed | P2 | 49 | 337633 6WOODWARD! 230 337968 6RICUSKEY% 230 1 | LN | 384.6 | 167.6 | 342 | 112.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337968 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211702 | 23S | Proposed | P2 | 49 | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | LN | 253.9 | 55.4 | 253 | 100.4 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337649 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211703 | 23S | Proposed | P2 | 49 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 1 | TR | 533.4 | 176.7 | 420 | 127 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211704 | 23S | Proposed | P2 | 49 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 2 | TR | 533.4 | 176.7 | 420 | 127 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211705 | 23S | Proposed | P2 | 49 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 314.4 | 34.9 | 253 | 124.3 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211706 | 23S | Proposed | P2 | 49 | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | LN | 245.6 | 49.2 | 253 | 97.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337649 | 337855 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211707 | 23S | Proposed | P2 | 49 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | LN | 104.3 | 62.9 | 106 | 98.4 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337967 | 337969 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211708 | 23S | Proposed | P6 | 49 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 146.9 | 109.6 | 159 | 92.4 |  |  |  |  | 3 | 8SHERIDAN% - 8MABELVALE% 500 1+ 8MABELVALE% 500/11 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8MABELVALE% 500 1 | 8MABELVALE% 500/11 | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
211709 | 23S | Proposed | P2 | 49 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 452 | 215.9 | 420 | 107.6 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MAYFLOWER% 500/115 1 | 8MAYFLOWER% 500/115 2 |  | Contingency: invalid after proposed project 12-EAI-021-CP
211710 | 23S | Proposed | P2 | 49 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 424.4 | 260.7 | 450 | 94.3 |  |  |  |  | 8 | ISES 161kV bus #1 | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211712 | 23S | Proposed | P6 | 49 | 336967 3ONWARD+ 115 336968 3ROLING FRK! 115 1 | LN | 104 | 43 | 111 | 93.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336967 | 336968 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE |  | No violation: below Rate A
211713 | 23S | Proposed | P6 | 49 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 106.3 | 79.1 | 115 | 92.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211714 | 23S | Proposed | P3 | 49 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 293.1 | 213.3 | 320 | 91.6 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WAT U3! 25.0 Id:1 |  | No violation: below Rate A
211716 | 23S | Proposed | P3 | 49 | 334113 4EASTGAT 138 334115 46L533TP8 138 1 | LN | 249.6 | 114.4 | 272 | 91.7 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334113 | 334115 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211717 | 23S | Proposed | P3 | 49 | 334115 46L533TP8 138 334210 4ADAYTON! 138 1 | LN | 249.6 | 114.4 | 272 | 91.8 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334115 | 334210 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211718 | 23S | Proposed | P3 | 49 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 688.9 | 327.3 | 753 | 91.5 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211719 | 23S | Proposed | P3 | 49 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 686.6 | 308.3 | 749 | 91.7 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211720 | 23S | Proposed | P3 | 49 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 686.6 | 308.3 | 753 | 91.2 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211722 | 23S | Proposed | P3 | 49 | 334113 4EASTGAT 138 334115 46L533TP8 138 1 | LN | 249.7 | 114.4 | 272 | 91.8 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334113 | 334115 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211723 | 23S | Proposed | P3 | 49 | 334115 46L533TP8 138 334210 4ADAYTON! 138 1 | LN | 249.7 | 114.4 | 272 | 91.8 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334115 | 334210 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211724 | 23S | Proposed | P3 | 49 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 688.5 | 327.3 | 753 | 91.4 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211725 | 23S | Proposed | P3 | 49 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 687.1 | 308.3 | 749 | 91.7 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211726 | 23S | Proposed | P3 | 49 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 687.1 | 308.3 | 753 | 91.3 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
211729 | 23S | Proposed | P3 | 49 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 343.1 | 333.3 | 360 | 95.3 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 |  | No violation: below Rate A
211742 | 18S | Proposed | P2 | 50 | 337620 3WOODWARD% 115 337634 3DIERKS! 115 1 | LN | 93.8 | 38 | 98 | 95.7 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337620 | 337634 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211743 | 18S | Proposed | P2 | 50 | 337620 3WOODWARD% 115 337647 3ARSENAL D 115 1 | LN | 215.8 | 114 | 239 | 90.3 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337620 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211744 | 18S | Proposed | P2 | 50 | 337633 6WOODWARD! 230 337654 6WHT BLUFF% 230 1 | LN | 639.5 | 276.1 | 519 | 123.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337654 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211745 | 18S | Proposed | P2 | 50 | 337633 6WOODWARD! 230 337968 6RICUSKEY% 230 1 | LN | 373.1 | 156.1 | 342 | 109.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337633 | 337968 | 1 |  | 230 | 230 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211746 | 18S | Proposed | P2 | 50 | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | LN | 251 | 51.5 | 253 | 99.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337649 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211747 | 18S | Proposed | P2 | 50 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 1 | TR | 536.4 | 178.3 | 420 | 127.7 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211748 | 18S | Proposed | P2 | 50 | 337648 3WHT BLUFF! 115 337651 8WHT BLUFF% 500 2 | TR | 536.4 | 178.3 | 420 | 127.7 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337651 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211749 | 18S | Proposed | P2 | 50 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 315.3 | 37.6 | 253 | 124.6 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211750 | 18S | Proposed | P2 | 50 | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | LN | 242.8 | 45.3 | 253 | 96 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337649 | 337855 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211751 | 18S | Proposed | P2 | 50 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | LN | 101.9 | 64.3 | 106 | 96.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337967 | 337969 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8SHERIDAN% - 8WHT BLUFF% 500 1 | 8WHT BLUFF% - 8KE |  | Contingency: invalid after proposed project 11-EAI-017-CP
211752 | 18S | Proposed | P2 | 50 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 462.5 | 220.5 | 420 | 110.1 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8MAYFLOWER% 500/115 1 | 8MAYFLOWER% 500/115 2 |  | Contingency: invalid after proposed project 12-EAI-021-CP
211753 | 18S | Proposed | P2 | 50 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 377 | 174.8 | 266 | 141.7 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP |  | 2018-06-01 | Reconfigure ISES 161 kV Bus
211754 | 18S | Proposed | P2 | 50 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 339.1 | 135.4 | 266 | 127.5 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211755 | 18S | Proposed | P2 | 50 | 338010 3SRCY PRICE! 115 338045 5SRCY PRICE! 161 1 | TR | 210.2 | 69.7 | 225 | 93.4 |  |  |  |  | 8 | ISES 161kV bus #1 | 338010 | 338045 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211756 | 18S | Proposed | P2 | 50 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 420.8 | 248.8 | 450 | 93.5 |  |  |  |  | 8 | ISES 161kV bus #1 | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211757 | 18S | Proposed | P2 | 50 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 151.9 | 100.6 | 161 | 94.4 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211758 | 18S | Proposed | P2 | 50 | 336551 3MCCOMB! 115 336552 3NORFIELD+ 115 1 | LN | 181.7 | 103 | 199 | 91.3 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336551 | 336552 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211759 | 18S | Proposed | P2 | 50 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 200.1 | 120.8 | 199 | 100.5 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211760 | 18S | Proposed | P2 | 50 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 224.5 | 141.9 | 199 | 112.8 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211761 | 18S | Proposed | P6 | 50 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 145.3 | 51.4 | 161 | 90.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211762 | 18S | Proposed | P3 | 50 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 289.9 | 208.5 | 320 | 90.6 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WAT U3! 25.0 Id:1 |  | No violation: below Rate A
211763 | 18S | Proposed | P3 | 50 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.8 | 167.7 | 243 | 92.1 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
211764 | 18S | Proposed | P3 | 50 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 196.1 | 103.5 | 206 | 95.2 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2 | Project Proposed | No violation: below Rate A | 13-ETI-014-CP | 2019-06-01 | Reconductor Panorama-Longmire 138 kV
211765 | 18S | Proposed | P3 | 50 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.7 | 167.7 | 243 | 92.1 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
211770 | 18S | Proposed | P1 | 50 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 27.4 | 12.3 | 29.3 | 93.5 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211771 | 18S | Proposed | P1 | 50 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 28.4 | 12.4 | 29.3 | 96.8 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211772 | 18S | Proposed | P1 | 50 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 29 | 12.4 | 29.3 | 99.1 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1 | Batson - Quality Mi | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
211776 | 15S | Approved | P2 | 44 | 3BEEBE | VL |  |  |  |  | 0.9125 | 0.9886 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211777 | 15S | Approved | P2 | 44 | 3GARNER+ | VL |  |  |  |  | 0.8961 | 0.9932 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211778 | 15S | Approved | P2 | 44 | 3T.E.P/S-MC | VL |  |  |  |  | 0.8959 | 0.9931 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211779 | 15S | Approved | P2 | 44 | 3SRCY PRICE! | VL |  |  |  |  | 0.8814 | 0.9994 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211780 | 15S | Approved | P2 | 44 | 3GRIFFITHVLE | VL |  |  |  |  | 0.8931 | 0.9972 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338011 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211781 | 15S | Approved | P2 | 44 | 3DES ARC | VL |  |  |  |  | 0.9134 | 0.9962 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338012 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211782 | 15S | Approved | P2 | 44 | 5SRCY PRICE! | VL |  |  |  |  | 0.8682 | 0.9912 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211783 | 15S | Approved | P2 | 44 | 5SEARCY.S | VL |  |  |  |  | 0.8635 | 0.9907 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211784 | 15S | Approved | P2 | 44 | 5PANGBURN | VL |  |  |  |  | 0.8538 | 1.0062 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338047 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211785 | 15S | Approved | P2 | 44 | 5BALD KNOB | VL |  |  |  |  | 0.8654 | 0.9899 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211786 | 15S | Approved | P2 | 44 | 5T.E.P/S-6 | VL |  |  |  |  | 0.8653 | 0.9901 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211787 | 15S | Approved | P2 | 44 | 3T.E.P/S-6 | VL |  |  |  |  | 0.8428 | 0.9657 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211788 | 15S | Approved | P2 | 44 | 5NEWARK AR | VL |  |  |  |  | 0.8291 | 0.9997 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338147 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211789 | 15S | Approved | P2 | 44 | 5RUTHERFORD! | VL |  |  |  |  | 0.8294 | 0.9994 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338148 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211790 | 15S | Approved | P2 | 44 | 5SOUTHSIDE! | VL |  |  |  |  | 0.8325 | 0.9985 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338149 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211791 | 15S | Approved | P2 | 44 | 5CEDARGROVE | VL |  |  |  |  | 0.842 | 1.0016 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338150 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211792 | 15S | Approved | P2 | 44 | 5COPPERSPRG# | VL |  |  |  |  | 0.8583 | 0.9955 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211793 | 15S | Approved | P2 | 44 | 5COFFEEVLE# | VL |  |  |  |  | 0.8656 | 0.9938 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338759 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211794 | 15S | Approved | P6 | 44 | 3GGNS | VL |  |  |  |  | 0.9678 | 1.0035 | 0.975 | 1.05 | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
211795 | 15S | Approved | P3 | 44 | 4STALEY! | VL |  |  |  |  | 0.9102 | 0.9904 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211796 | 15S | Approved | P3 | 44 | 4MAGROVE | VL |  |  |  |  | 0.9196 | 0.9904 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211798 | 23S | Approved | P2 | 45 | 3CABOT | VL |  |  |  |  | 0.9118 | 0.9999 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338006 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211799 | 23S | Approved | P2 | 45 | 3BEEBE | VL |  |  |  |  | 0.7661 | 0.9882 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211800 | 23S | Approved | P2 | 45 | 3GARNER+ | VL |  |  |  |  | 0.7137 | 0.9911 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211801 | 23S | Approved | P2 | 45 | 3T.E.P/S-MC | VL |  |  |  |  | 0.7135 | 0.991 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211802 | 23S | Approved | P2 | 45 | 3SRCY PRICE! | VL |  |  |  |  | 0.6576 | 0.9951 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211803 | 23S | Approved | P2 | 45 | 3GRIFFITHVLE | VL |  |  |  |  | 0.699 | 0.9924 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338011 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211804 | 23S | Approved | P2 | 45 | 3DES ARC | VL |  |  |  |  | 0.7651 | 0.9915 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338012 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211805 | 23S | Approved | P2 | 45 | 3COTTON PLNT | VL |  |  |  |  | 0.8636 | 0.9961 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338013 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211806 | 23S | Approved | P2 | 45 | 5BRINKLEY.E | VL |  |  |  |  | 0.9148 | 0.9585 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338020 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211807 | 23S | Approved | P2 | 45 | 5SRCY PRICE! | VL |  |  |  |  | 0.6184 | 0.9866 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211808 | 23S | Approved | P2 | 45 | 5SEARCY.S | VL |  |  |  |  | 0.6054 | 0.9857 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211809 | 23S | Approved | P2 | 45 | 5PANGBURN | VL |  |  |  |  | 0.5515 | 1.0015 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338047 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211810 | 23S | Approved | P2 | 45 | 5BALD KNOB | VL |  |  |  |  | 0.6138 | 0.9858 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211811 | 23S | Approved | P2 | 45 | 5T.E.P/S-6 | VL |  |  |  |  | 0.6136 | 0.9862 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211812 | 23S | Approved | P2 | 45 | 3T.E.P/S-6 | VL |  |  |  |  | 0.5944 | 0.9619 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211813 | 23S | Approved | P2 | 45 | 5NEWARK AR | VL |  |  |  |  | 0.5086 | 0.9992 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338147 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211814 | 23S | Approved | P2 | 45 | 5RUTHERFORD! | VL |  |  |  |  | 0.509 | 0.9981 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338148 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211815 | 23S | Approved | P2 | 45 | 5SOUTHSIDE! | VL |  |  |  |  | 0.5138 | 0.9955 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338149 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211816 | 23S | Approved | P2 | 45 | 5CEDARGROVE | VL |  |  |  |  | 0.5301 | 0.9976 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338150 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211817 | 23S | Approved | P2 | 45 | 2WARD | VL |  |  |  |  | 0.8787 | 1.0159 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211818 | 23S | Approved | P2 | 45 | 5COPPERSPRG# | VL |  |  |  |  | 0.5821 | 0.9905 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211819 | 23S | Approved | P2 | 45 | 3WARD# | VL |  |  |  |  | 0.8567 | 0.9905 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211820 | 23S | Approved | P2 | 45 | 5COFFEEVLE# | VL |  |  |  |  | 0.6137 | 0.9914 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338759 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211821 | 23S | Approved | P6 | 45 | 3GGNS | VL |  |  |  |  | 0.9733 | 0.9975 | 0.975 | 1.05 | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211822 | 23S | Approved | P3 | 45 | 4ALDEN! | VL |  |  |  |  | 0.9179 | 0.9684 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211823 | 23S | Approved | P3 | 45 | 4GOSLIN2! | VL |  |  |  |  | 0.9195 | 0.9674 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211824 | 23S | Approved | P3 | 45 | 4METRO2! | VL |  |  |  |  | 0.9189 | 0.965 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211825 | 23S | Approved | P3 | 45 | 4GOSLIN1! | VL |  |  |  |  | 0.9195 | 0.9674 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211826 | 23S | Approved | P3 | 45 | 4HICKORY | VL |  |  |  |  | 0.9173 | 0.964 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211827 | 23S | Approved | P3 | 45 | 4HUFFMAN | VL |  |  |  |  | 0.9195 | 0.9649 | 0.92 | 1.05 | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211828 | 23S | Approved | P3 | 45 | 4ALDEN! | VL |  |  |  |  | 0.9169 | 0.9684 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211829 | 23S | Approved | P3 | 45 | 4GOSLIN2! | VL |  |  |  |  | 0.9186 | 0.9674 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211830 | 23S | Approved | P3 | 45 | 4METRO2! | VL |  |  |  |  | 0.9181 | 0.965 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211831 | 23S | Approved | P3 | 45 | 4GOSLIN1! | VL |  |  |  |  | 0.9186 | 0.9674 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211832 | 23S | Approved | P3 | 45 | 4NEWCANY! | VL |  |  |  |  | 0.9197 | 0.9642 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211833 | 23S | Approved | P3 | 45 | 4HICKORY | VL |  |  |  |  | 0.9164 | 0.964 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211834 | 23S | Approved | P3 | 45 | 4HUFFMAN | VL |  |  |  |  | 0.9185 | 0.9649 | 0.92 | 1.05 | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | 6PORTER% - 6CHPTSR2 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
211835 | 23S | Approved | P3 | 45 | 4STALEY! | VL |  |  |  |  | 0.8949 | 0.9838 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211836 | 23S | Approved | P3 | 45 | 4MAGROVE | VL |  |  |  |  | 0.9054 | 0.9843 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211837 | 23S | Approved | P3 | 45 | 4L111T411 | VL |  |  |  |  | 0.9145 | 0.9855 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211838 | 23S | Approved | P3 | 45 | 4KICKAPO | VL |  |  |  |  | 0.9144 | 0.9854 | 0.92 | 1.05 | 22 | 4RIVTRIN% - 4STALEY! 138 1 + 4RAYBURN% 138 Id:1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 4RIVTRIN% - 4STALEY! 138 1 | 4RAYBURN% 138 Id:1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
211839 | 23S | Approved | P3 | 45 | 6KEITHLAKE% | VL |  |  |  |  | 0.9195 | 0.9857 | 0.92 | 1.05 | 31 | 6MID CO% - 6P AC BK% 230 1 + 1G4SABIN! 24.0 Id:1 | 334444 |  |  |  | 230 | 230 | 351 | EES |  |  | 6MID CO% - 6P AC BK% 230 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed |  | 12-ETI-006-CP | 2018-06-01 | Install capacitor bank at Kolbs 230 kV
211843 | 15S | Proposed | P2 | 46 | 3SRCY PRICE! | VL |  |  |  |  | 0.9192 | 1.0083 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211844 | 15S | Proposed | P2 | 46 | 5SRCY PRICE! | VL |  |  |  |  | 0.9082 | 0.9978 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211845 | 15S | Proposed | P2 | 46 | 5SEARCY.S | VL |  |  |  |  | 0.9043 | 0.997 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211846 | 15S | Proposed | P2 | 46 | 5PANGBURN | VL |  |  |  |  | 0.899 | 1.01 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338047 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211847 | 15S | Proposed | P2 | 46 | 5BALD KNOB | VL |  |  |  |  | 0.9056 | 0.9951 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211848 | 15S | Proposed | P2 | 46 | 5T.E.P/S-6 | VL |  |  |  |  | 0.9056 | 0.995 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211849 | 15S | Proposed | P2 | 46 | 3T.E.P/S-6 | VL |  |  |  |  | 0.8825 | 0.9706 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211850 | 15S | Proposed | P2 | 46 | 5COFER RD | VL |  |  |  |  | 0.9003 | 1.0033 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338052 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211851 | 15S | Proposed | P2 | 46 | 5NEWARK AR | VL |  |  |  |  | 0.876 | 0.9999 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338147 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211852 | 15S | Proposed | P2 | 46 | 5RUTHERFORD! | VL |  |  |  |  | 0.8763 | 1.0001 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338148 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211853 | 15S | Proposed | P2 | 46 | 5SOUTHSIDE! | VL |  |  |  |  | 0.8792 | 1 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338149 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211854 | 15S | Proposed | P2 | 46 | 5CEDARGROVE | VL |  |  |  |  | 0.8881 | 1.0043 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338150 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211855 | 15S | Proposed | P2 | 46 | 5COPPERSPRG# | VL |  |  |  |  | 0.9008 | 1.0009 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211856 | 15S | Proposed | P2 | 46 | 5COFFEEVLE# | VL |  |  |  |  | 0.9059 | 0.9965 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338759 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
211857 | 15S | Proposed | P6 | 46 | 3GGNS | VL |  |  |  |  | 0.965 | 1.009 | 0.975 | 1.05 | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWE | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
211895 | 18W | Proposed | P2 | 48 | 8BOGALUS | VL |  |  |  |  | 0.9196 | 0.9813 | 0.92 | 1.05 | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336130 |  |  |  | 500 | 500 | 351 | EES |  |  | 8MCKNIGHT% - 8FRANKLIN% 500 1 | 8BOGALUS - 8FRANKL | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
211900 | 18S | Proposed | P2 | 50 | 3BEEBE | VL |  |  |  |  | 0.8581 | 1.0008 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211901 | 18S | Proposed | P2 | 50 | 3GARNER+ | VL |  |  |  |  | 0.8237 | 1.0024 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211902 | 18S | Proposed | P2 | 50 | 3T.E.P/S-MC | VL |  |  |  |  | 0.8235 | 1.0022 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211903 | 18S | Proposed | P2 | 50 | 3SRCY PRICE! | VL |  |  |  |  | 0.7879 | 1.0044 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211904 | 18S | Proposed | P2 | 50 | 3GRIFFITHVLE | VL |  |  |  |  | 0.8121 | 1.0025 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338011 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211905 | 18S | Proposed | P2 | 50 | 3DES ARC | VL |  |  |  |  | 0.8514 | 1.002 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338012 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211906 | 18S | Proposed | P2 | 50 | 3COTTON PLNT | VL |  |  |  |  | 0.913 | 1.0064 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338013 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211907 | 18S | Proposed | P2 | 50 | 5SRCY PRICE! | VL |  |  |  |  | 0.7616 | 0.9938 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211908 | 18S | Proposed | P2 | 50 | 5SEARCY.S | VL |  |  |  |  | 0.7524 | 0.9927 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211909 | 18S | Proposed | P2 | 50 | 5PANGBURN | VL |  |  |  |  | 0.719 | 1.005 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338047 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211910 | 18S | Proposed | P2 | 50 | 5BALD KNOB | VL |  |  |  |  | 0.7581 | 0.9918 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211911 | 18S | Proposed | P2 | 50 | 5T.E.P/S-6 | VL |  |  |  |  | 0.758 | 0.9919 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211912 | 18S | Proposed | P2 | 50 | 3T.E.P/S-6 | VL |  |  |  |  | 0.7369 | 0.9675 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211913 | 18S | Proposed | P2 | 50 | 5COFER RD | VL |  |  |  |  | 0.7307 | 0.9973 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338052 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211914 | 18S | Proposed | P2 | 50 | 5NEWARK AR | VL |  |  |  |  | 0.6856 | 0.9995 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338147 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211915 | 18S | Proposed | P2 | 50 | 5RUTHERFORD! | VL |  |  |  |  | 0.6859 | 0.9991 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338148 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211916 | 18S | Proposed | P2 | 50 | 5SOUTHSIDE! | VL |  |  |  |  | 0.69 | 0.9976 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338149 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211917 | 18S | Proposed | P2 | 50 | 5CEDARGROVE | VL |  |  |  |  | 0.7028 | 1.0005 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338150 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211918 | 18S | Proposed | P2 | 50 | 5COPPERSPRG# | VL |  |  |  |  | 0.7362 | 0.9954 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211919 | 18S | Proposed | P2 | 50 | 3WARD# | VL |  |  |  |  | 0.9093 | 0.9945 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
211920 | 18S | Proposed | P2 | 50 | 5COFFEEVLE# | VL |  |  |  |  | 0.7582 | 0.9947 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338759 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  |  | Contingency: invalid after proposed project 11-EAI-016-CP
212001 | 15S | Approved | P1 | 51 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 196.8 | 129.4 | 191 | 103 |  |  |  |  | 1379 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
212002 | 15S | Approved | P1 | 51 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 196.8 | 129.4 | 191 | 103 |  |  |  |  | 2482 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
212003 | 15S | Approved | P1 | 52 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 196.8 | 129.4 | 191 | 103 |  |  |  |  | 784 | P1_2-559 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
212004 | 15S | Approved | P1 | 52 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 196.8 | 129.4 | 191 | 103 |  |  |  |  | 785 | P1_2-560 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-560 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment

## runs
MISO ICT Steady State Analysis [2013-08-20]
MUST run summary table
run_id | model_short | projects | cont_file | model vintage
1 | 15S | Approved | P1 Auto | u2
2 | 15S | Approved | P1 | u2
3 | 18L | Approved | P1 Auto | u2
4 | 18L | Approved | P1 | u2
5 | 18S | Approved | P1 Auto | u2
6 | 18S | Approved | P1 | u2
7 | 18W | Approved | P1 Auto | u2
8 | 18W | Approved | P1 | u2
9 | 23S | Approved | P1 Auto | u2
10 | 23S | Approved | P1 | u2
11 | 15S | Proposed | P1 | u2
12 | 15S | Proposed | P1 Auto | u2
13 | 15S | Proposed | P1 | u2
14 | 18L | Proposed | P1 | u2
15 | 18L | Proposed | P1 Auto | u2
16 | 18L | Proposed | P1 | u2
17 | 18S | Proposed | P1 | u2
18 | 18S | Proposed | P1 Auto | u2
19 | 18S | Proposed | P1 | u2
20 | 18W | Proposed | P1 | u2
21 | 18W | Proposed | P1 Auto | u2
22 | 18W | Proposed | P1 | u2
23 | 23S | Proposed | P1 | u2
24 | 23S | Proposed | P1 Auto | u2
25 | 23S | Proposed | P1 | u2
31 | 18S | Approved | P3 | u2
32 | 18W | Approved | P3 | u2
33 | 18L | Approved | P3 | u2
34 | 18S | Approved | P2+ | u2
35 | 18W | Approved | P2+ | u2
36 | 18L | Approved | P2+ | u2
37 | 15S | Approved | P3 | u2a
38 | 23S | Approved | P3 | u2a
39 | 15S | Proposed | P3 | u2a
40 | 18L | Proposed | P3 | u2a
41 | 18W | Proposed | P3 | u2a
42 | 23S | Proposed | P3 | u2a
43 | 18S | Proposed | P3 | u2a
44 | 15S | Approved | P2+ | u2a
45 | 23S | Approved | P2+ | u2a
46 | 15S | Proposed | P2+ | u2a
47 | 18L | Proposed | P2+ | u2a
48 | 18W | Proposed | P2+ | u2a
49 | 23S | Proposed | P2+ | u2a
50 | 18S | Proposed | P2+ | u2a
51 | 15S | Approved | P1 Auto | u2a
52 | 15S | Approved | P1 | u2a
53 | 18W | Approved | P1 Auto | u2a
54 | 18W | Approved | P1 | u2a
55 | 15S | Proposed | P1 Auto | u2a
56 | 15S | Proposed | P1 | u2a
57 | 18L | Proposed | P1 Auto | u2a
58 | 18L | Proposed | P1 | u2a
59 | 18S | Proposed | P1 Auto | u2a
60 | 18S | Proposed | P1 | u2a