## tResults_Thermal_&_Voltage
MISO ICT Steady State Analysis [2013-08-20]
Combined Thermal and Voltage Tables
[7 empty] | Thermal |  |  |  | Voltage
Need_ID | model short | projects included | cont type | Run_ID | Limiting_Facility | Type_Viol | Cont_MVA | Base_Flow | Rating | Loading % | Cont_Level | Base_Level | LV_Limit | HV_Limit | NCont | Cont_Label | Limiter_Bus1 | Limiter_Bus2 | Limiter_Ckt | TX_Name | kV_H | kV_L | area1 | name1 | area2 | name2 | P1/P2 outage | P3/P6 prior outage | mitigation | invalid_reason | CP_ID | Proposed_ISD | CP_Name
100000 | 15S | Approved | P0 | 1 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 331.8 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100001 | 15S | Approved | P0 | 1 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.2 | 34.2 | 38 | 90 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100001 | 15S | Approved | P0 | 1 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.2 | 34.2 | 38 | 90 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100002 | 15S | Approved | P0 | 1 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 87.1 | 87.1 | 93 | 93.7 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100003 | 15S | Approved | P0 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101 | 101 | 112 | 90.2 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100004 | 15S | Approved | P0 | 1 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105.1 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
100005 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.2 | 101 | 112 | 91.2 |  |  |  |  | 40 | 337539 3EL DORADO! 115 337561 8EL DORADO% 500 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337539 3EL DORADO! 115 337561 8EL DORADO% 500 1 |  |  | Facility: Radial
100006 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102 | 101 | 112 | 91.1 |  |  |  |  | 69 | 337577 3WILMAR 115 337578 3MONTCELO.S 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337577 3WILMAR 115 337578 3MONTCELO.S 115 1 |  |  | Facility: Radial
100007 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.5 | 101 | 112 | 91.5 |  |  |  |  | 75 | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 |  |  | Facility: Radial
100008 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.8 | 101 | 112 | 91.8 |  |  |  |  | 78 | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100009 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.8 | 101 | 112 | 91.8 |  |  |  |  | 79 | 337590 3HAMBURG 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337590 3HAMBURG 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100010 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.7 | 101 | 112 | 92.6 |  |  |  |  | 80 | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100011 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.9 | 101 | 112 | 91.9 |  |  |  |  | 81 | 337591 3MONTROSE 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100012 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101 | 112 | 91.7 |  |  |  |  | 82 | 337592 3BAGBY! 115 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 337594 6BAGBY 230 1 |  |  | Facility: Radial
100013 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.8 | 101 | 112 | 92.7 |  |  |  |  | 85 | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100014 | 15S | Approved | P1 | 1 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 246.1 | 181 | 266 | 92.5 |  |  |  |  | 108 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 |  |  | No violation: below Rate A
100015 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.3 | 101 | 112 | 91.3 |  |  |  |  | 110 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  |  | Facility: Radial
100016 | 15S | Approved | P1 | 1 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 222.1 | 161.1 | 239 | 92.9 |  |  |  |  | 136 | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100017 | 15S | Approved | P1 | 1 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 228.9 | 167.7 | 253 | 90.5 |  |  |  |  | 136 | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100018 | 15S | Approved | P1 | 1 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 230.3 | 161.1 | 239 | 96.4 |  |  |  |  | 137 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100019 | 15S | Approved | P1 | 1 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 237.1 | 167.7 | 253 | 93.7 |  |  |  |  | 137 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100020 | 15S | Approved | P1 | 1 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 234.3 | 161.1 | 239 | 98 |  |  |  |  | 138 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100021 | 15S | Approved | P1 | 1 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 241.1 | 167.7 | 253 | 95.3 |  |  |  |  | 138 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100022 | 15S | Approved | P1 | 1 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 248.9 | 181 | 266 | 93.6 |  |  |  |  | 139 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 |  |  | No violation: below Rate A
100023 | 15S | Approved | P1 | 1 | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 | TR | 515.3 | 308 | 550 | 93.7 |  |  |  |  | 169 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | 337740 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 |  |  | No violation: below Rate A
100024 | 15S | Approved | P2 | 1 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 152.9 | 81 | 159 | 96.2 |  |  |  |  | 188 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 |  | Project Approved | No violation: below Rate A | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100025 | 15S | Approved | P2 | 1 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | LN | 151.9 | 68.3 | 159 | 95.6 |  |  |  |  | 193 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337710 | 337713 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | No violation: below Rate A | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100026 | 15S | Approved | P1 | 1 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 293.8 | 79.5 | 239 | 122.9 |  |  |  |  | 202 | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100027 | 15S | Approved | P1 | 1 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 507 | 297 | 550 | 92.2 |  |  |  |  | 202 | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 |  |  | No violation: below Rate A
100028 | 15S | Approved | P1 | 1 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 421.5 | 295.7 | 448 | 94.1 |  |  |  |  | 216 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100029 | 15S | Approved | P1 | 1 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | TR | 422.2 | 296.6 | 448 | 94.3 |  |  |  |  | 223 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | 337799 | 337808 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100030 | 15S | Approved | P1 | 1 | 337815 3MANN RD 115 337816 3LR CHICOT 115 1 | LN | 274.3 | 182.9 | 298 | 92 |  |  |  |  | 225 | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 | 337815 | 337816 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 |  |  | No violation: below Rate A
100031 | 15S | Approved | P1 | 1 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 256.6 | 227.9 | 283 | 90.7 |  |  |  |  | 248 | 337826 3PINNACLE! 115 337827 3NATURAL STP 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337826 3PINNACLE! 115 337827 3NATURAL STP 115 1 |  |  | No violation: below Rate A
100032 | 15S | Approved | P1 | 1 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 257.9 | 227.9 | 283 | 91.1 |  |  |  |  | 252 | 337827 3NATURAL STP 115 337930 3MAYFLOWER% 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337827 3NATURAL STP 115 337930 3MAYFLOWER% 115 1 |  |  | No violation: below Rate A
100033 | 15S | Approved | P1 | 1 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 104.2 | 43 | 106 | 98.3 |  |  |  |  | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100034 | 15S | Approved | P1 | 1 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 100.5 | 40.3 | 106 | 94.8 |  |  |  |  | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100035 | 15S | Approved | P1 | 1 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 100.8 | 57.6 | 106 | 95.1 |  |  |  |  | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100036 | 15S | Approved | P1 | 1 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 259.3 | 227.9 | 283 | 91.6 |  |  |  |  | 379 | 338016 3HOLND BTM! 115 338140 8HOLND BTM% 500 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338016 3HOLND BTM! 115 338140 8HOLND BTM% 500 1 |  |  | No violation: below Rate A
100037 | 15S | Approved | P1 | 1 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 149.3 | 71.4 | 148 | 100.9 |  |  |  |  | 440 | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 |  | Project Proposed |  | 11-EAI-025-CP | 2016-06-01 | Upgrade Norfork-Calico Rock 161 kV
100038 | 15S | Approved | P2 | 1 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 142.9 | 76 | 148 | 96.6 |  |  |  |  | 457 | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100039 | 15S | Approved | P1 | 1 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 135.5 | 76 | 148 | 91.5 |  |  |  |  | 472 | 338171 5CASH 161 338172 5NEWPORT AB 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338171 5CASH 161 338172 5NEWPORT AB 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100040 | 15S | Approved | P1 | 1 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 141.4 | 76 | 148 | 95.6 |  |  |  |  | 473 | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100041 | 15S | Approved | P1 | 1 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 82 | 35.8 | 70 | 117.1 |  |  |  |  | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100042 | 15S | Approved | P1 | 1 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 89.5 | 41.7 | 70 | 127.8 |  |  |  |  | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100043 | 15S | Approved | P1 | 1 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 65.7 | 35.8 | 70 | 93.8 |  |  |  |  | 518 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100044 | 15S | Approved | P1 | 1 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 72.4 | 41.7 | 70 | 103.5 |  |  |  |  | 518 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100045 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101 | 112 | 91.7 |  |  |  |  | 613 | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 |  |  | Facility: Radial
100046 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.9 | 101 | 112 | 91.8 |  |  |  |  | 621 | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100047 | 15S | Approved | P1 | 1 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.3 | 101 | 112 | 91.3 |  |  |  |  | 624 | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 |  |  | Facility: Radial
100048 | 15S | Approved | P1 | 1 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 82 | 35.8 | 70 | 117.1 |  |  |  |  | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100049 | 15S | Approved | P1 | 1 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 89.4 | 41.7 | 70 | 127.8 |  |  |  |  | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100050 | 15S | Approved | P1 | 1 | 334043 4TUBULAR 138 334044 4DOBBIN 138 1 | LN | 148.9 | 25.5 | 112 | 133 |  |  |  |  | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334043 | 334044 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
100051 | 15S | Approved | P1 | 1 | 334044 4DOBBIN 138 334046 4SPRINGBRNCH 138 1 | LN | 115.6 | 19 | 112 | 103.2 |  |  |  |  | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334044 | 334046 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
100052 | 15S | Approved | P1 | 1 | 334045 4FISHCRK 138 334046 4SPRINGBRNCH 138 1 | LN | 104.8 | 28.1 | 112 | 93.5 |  |  |  |  | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334045 | 334046 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed | No violation: below Rate A | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
100053 | 15S | Approved | P1 | 1 | 334043 4TUBULAR 138 334044 4DOBBIN 138 1 | LN | 113.2 | 25.5 | 112 | 101.1 |  |  |  |  | 750 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | 334043 | 334044 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334073 4EGYPT 138 334074 4PANORAM 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
100054 | 15S | Approved | P1 | 1 | 334043 4TUBULAR 138 334044 4DOBBIN 138 1 | LN | 106.5 | 25.5 | 112 | 95.1 |  |  |  |  | 751 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | 334043 | 334044 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 |  | Project Proposed | No violation: below Rate A | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
100055 | 15S | Approved | P1 | 1 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 228.8 | 101.7 | 243 | 94.2 |  |  |  |  | 767 | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
100056 | 15S | Approved | P1 | 1 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.7 | 86.7 | 206 | 91.6 |  |  |  |  | 778 | 3Wnd: OPEN B$1594 PORTER 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 3Wnd: OPEN B$1594 PORTER 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100057 | 15S | Approved | P1 | 1 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.7 | 86.7 | 206 | 91.6 |  |  |  |  | 822 | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100058 | 15S | Approved | P1 | 1 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.6 | 86.7 | 206 | 91.5 |  |  |  |  | 823 | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100059 | 15S | Approved | P1 | 1 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.6 | 86.7 | 206 | 91.5 |  |  |  |  | 824 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100060 | 15S | Approved | P1 | 1 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 35.9 | 16.4 | 39 | 92.1 |  |  |  |  | 851 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100061 | 15S | Approved | P1 | 1 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 36.4 | 16.4 | 39 | 93.2 |  |  |  |  | 854 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100062 | 15S | Approved | P1 | 1 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 37.2 | 16.4 | 39 | 95.4 |  |  |  |  | 855 | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100063 | 15S | Approved | P1 | 1 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 36.7 | 14 | 39 | 94.2 |  |  |  |  | 856 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100064 | 15S | Approved | P1 | 1 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39 | 16.4 | 39 | 100 |  |  |  |  | 856 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100065 | 15S | Approved | P1 | 1 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 260.8 | 164.2 | 288 | 90.5 |  |  |  |  | 987 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
100066 | 15S | Approved | P1 | 1 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 269.4 | 173.7 | 287 | 93.9 |  |  |  |  | 991 | 334414 4LINDE 138 334430 4SABINE! 138 1 | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334414 4LINDE 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
100067 | 15S | Approved | P1 | 1 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 65.8 | 20.3 | 72 | 91.4 |  |  |  |  | 1196 | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 |  |  | No violation: below Rate A
100068 | 15S | Approved | P1 | 1 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 67.6 | 20.3 | 72 | 93.9 |  |  |  |  | 1201 | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 |  |  | No violation: below Rate A
100069 | 15S | Approved | P1 | 1 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 456.5 | 324.1 | 470 | 97.1 |  |  |  |  | 1230 | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 |  | Reduce PPG Plant | No violation: below Rate A
100070 | 15S | Approved | P1 | 1 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224 | 118.1 | 200 | 112 |  |  |  |  | 1267 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
100071 | 15S | Approved | P1 | 1 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224 | 118.1 | 200 | 112 |  |  |  |  | 1268 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
100072 | 15S | Approved | P1 | 1 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 334.1 | 331.8 | 360 | 92.8 |  |  |  |  | 1269 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 335190 6NELSON% 230 335192 8NELSON% 500 1 |  |  | Facility: GSU
100073 | 15S | Approved | P1 | 1 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30.1 | 22.6 | 33 | 91.2 |  |  |  |  | 1280 | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100074 | 15S | Approved | P1 | 1 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.6 | 173.6 | 225 | 92.3 |  |  |  |  | 1371 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100075 | 15S | Approved | P1 | 1 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 216.4 | 173.6 | 225 | 96.2 |  |  |  |  | 1372 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100076 | 15S | Approved | P1 | 1 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 207.8 | 165.1 | 225 | 92.4 |  |  |  |  | 1372 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100077 | 15S | Approved | P1 | 1 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 181.9 | 114.4 | 191 | 95.2 |  |  |  |  | 1379 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100078 | 15S | Approved | P1 | 1 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.1 | 114.4 | 191 | 103.2 |  |  |  |  | 1381 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100079 | 15S | Approved | P1 | 1 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 40.2 | 18.7 | 39 | 103 |  |  |  |  | 1385 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100080 | 15S | Approved | P1 | 1 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 36.4 | 15.4 | 39 | 93.4 |  |  |  |  | 1385 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100081 | 15S | Approved | P1 | 1 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 37.9 | 23.9 | 39 | 97.2 |  |  |  |  | 1385 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100082 | 15S | Approved | P1 | 1 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 39.8 | 18.7 | 39 | 102 |  |  |  |  | 1392 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100083 | 15S | Approved | P1 | 1 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 35.9 | 15.4 | 39 | 92.1 |  |  |  |  | 1392 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100084 | 15S | Approved | P1 | 1 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 36.5 | 23.9 | 39 | 93.5 |  |  |  |  | 1394 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100085 | 15S | Approved | P1 | 1 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.7 | 23.9 | 39 | 99.2 |  |  |  |  | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100085 | 15S | Approved | P1 | 1 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.7 | 23.9 | 39 | 99.2 |  |  |  |  | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon | No violation: below Rate A | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100086 | 15S | Approved | P1 | 1 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 37.8 | 16.7 | 39 | 97 |  |  |  |  | 1401 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100086 | 15S | Approved | P1 | 1 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 37.8 | 16.7 | 39 | 97 |  |  |  |  | 1401 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Horizon | No violation: below Rate A | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100087 | 15S | Approved | P1 | 1 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | LN | 116.8 | 61.9 | 121 | 96.6 |  |  |  |  | 1566 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | 335699 | 335710 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100088 | 15S | Approved | P1 | 1 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 116.4 | 52.2 | 121 | 96.2 |  |  |  |  | 1570 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100089 | 15S | Approved | P1 | 1 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 114.7 | 52.2 | 121 | 94.8 |  |  |  |  | 1575 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100090 | 15S | Approved | P1 | 1 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 614.8 | 478.7 | 672 | 91.5 |  |  |  |  | 1610 | 335771 6COLY% 230 335837 8COLY% 500 1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 335771 6COLY% 230 335837 8COLY% 500 1 |  |  | No violation: below Rate A
100091 | 15S | Approved | P1 | 1 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 95.2 | 46.3 | 100 | 95.2 |  |  |  |  | 1620 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100092 | 15S | Approved | P1 | 1 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 94 | 45.7 | 100 | 94 |  |  |  |  | 1620 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100093 | 15S | Approved | P1 | 1 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 270.6 | 157.2 | 300 | 90.2 |  |  |  |  | 1636 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100094 | 15S | Approved | P1 | 1 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 271.4 | 158.9 | 300 | 90.5 |  |  |  |  | 1637 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100095 | 15S | Approved | P1 | 1 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | LN | 543 | 313.8 | 593 | 91.6 |  |  |  |  | 1642 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | 335815 | 335825 | 2 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100096 | 15S | Approved | P1 | 1 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 546.2 | 320.4 | 593 | 92.1 |  |  |  |  | 1643 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100097 | 15S | Approved | P1 | 1 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 632.8 | 478.7 | 672 | 94.2 |  |  |  |  | 1655 | 336000 6IBERVIL% 230 336011 6BYULABUTTE! 230 1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 336000 6IBERVIL% 230 336011 6BYULABUTTE! 230 1 |  |  | No violation: below Rate A
100098 | 15S | Approved | P1 | 1 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 632.7 | 478.7 | 672 | 94.2 |  |  |  |  | 1665 | 336010 8BYULABUTTE% 500 336011 6BYULABUTTE! 230 1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 336010 8BYULABUTTE% 500 336011 6BYULABUTTE! 230 1 |  |  | No violation: below Rate A
100099 | 15S | Approved | P1 | 1 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 124 | 75.2 | 115 | 107.8 |  |  |  |  | 1709 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100100 | 15S | Approved | P1 | 1 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194.1 | 142.8 | 199 | 97.5 |  |  |  |  | 1731 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100101 | 15S | Approved | P1 | 1 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194 | 142.8 | 199 | 97.5 |  |  |  |  | 1732 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100102 | 15S | Approved | P1 | 1 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 214.4 | 134.7 | 229 | 93.6 |  |  |  |  | 1807 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336284 3WSTWGO! 115 1 |  |  | No violation: below Rate A
100103 | 15S | Approved | P1 | 1 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 223.2 | 160.2 | 229 | 97.5 |  |  |  |  | 1808 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100104 | 15S | Approved | P1 | 1 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 181.9 | 115.1 | 199 | 91.4 |  |  |  |  | 1901 | 336556 3W.BROOKHAVN 115 336557 3CALIFORNIA 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336556 3W.BROOKHAVN 115 336557 3CALIFORNIA 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100105 | 15S | Approved | P1 | 1 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 188.4 | 115.1 | 199 | 94.7 |  |  |  |  | 1902 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100106 | 15S | Approved | P1 | 1 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 213.5 | 139.6 | 231 | 92.4 |  |  |  |  | 1902 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100107 | 15S | Approved | P1 | 1 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 194.2 | 115.1 | 199 | 97.6 |  |  |  |  | 1903 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100108 | 15S | Approved | P1 | 1 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 219.5 | 139.6 | 231 | 95 |  |  |  |  | 1903 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100109 | 15S | Approved | P1 | 1 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.9 | 34.5 | 39 | 91.9 |  |  |  |  | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | Facility: Radial
100110 | 15S | Approved | P1 | 1 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 104 | 80.6 | 115 | 90.5 |  |  |  |  | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100111 | 15S | Approved | P1 | 1 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 221.9 | 128.2 | 239 | 92.9 |  |  |  |  | 1942 | 336800 3BXTRWILSON% 115 336802 3SPEN.POTASH 115 1 | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336800 3BXTRWILSON% 115 336802 3SPEN.POTASH 115 1 |  | Project Proposed | No violation: below Rate A | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
100112 | 15S | Approved | P2 | 1 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 157.4 | 84.6 | 161 | 97.7 |  |  |  |  | 1951 | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100113 | 15S | Approved | P1 | 1 | 336906 3MONUMENT! 115 336907 3MIAMI ST 115 1 | LN | 298 | 223.6 | 320 | 93.1 |  |  |  |  | 1976 | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 | 336906 | 336907 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
100114 | 15S | Approved | P1 | 1 | 336907 3MIAMI ST 115 336938 3REX BRWN-W! 115 1 | LN | 311.7 | 237.1 | 320 | 97.4 |  |  |  |  | 1976 | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 | 336907 | 336938 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
100115 | 15S | Approved | P1 | 1 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 145.1 | 84.6 | 161 | 90.1 |  |  |  |  | 2053 | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100116 | 15S | Approved | P2 | 1 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 103.5 | 54.9 | 108 | 95.9 |  |  |  |  | 2059 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
100117 | 15S | Approved | P1 | 1 | 337040 6ANDRUS% 230 337042 3ANDRUS! 115 1 | TR | 370.4 | 267.7 | 392 | 94.5 |  |  |  |  | 2108 | 337040 6ANDRUS% 230 337050 6INDIANOLA! 230 1 | 337040 | 337042 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337040 6ANDRUS% 230 337050 6INDIANOLA! 230 1 |  | None | No violation: below Rate A
100118 | 15S | Approved | P1 | 1 | 337044 3GREENVILLE! 115 337076 3E.GREENVL 115 1 | LN | 112.2 | 46.9 | 120 | 93.5 |  |  |  |  | 2115 | 337044 3GREENVILLE! 115 337075 3GREENVL MID 115 1 | 337044 | 337076 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337044 3GREENVILLE! 115 337075 3GREENVL MID 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
100119 | 15S | Approved | P1 | 1 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 289.9 | 217.1 | 278 | 104.3 |  |  |  |  | 2166 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
100120 | 15S | Approved | P1 | 1 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 217.1 | 278 | 107 |  |  |  |  | 2167 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
100121 | 15S | Approved | P1 | 1 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 295.6 | 75.5 | 278 | 106.3 |  |  |  |  | 2169 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100122 | 15S | Approved | P1 | 1 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 306.1 | 82.4 | 250 | 122.4 |  |  |  |  | 2169 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100123 | 15S | Approved | P1 | 1 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 104.2 | 80.6 | 115 | 90.6 |  |  |  |  | 2226 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100124 | 15S | Approved | P1 | 1 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 242.2 | 186.5 | 262 | 92.5 |  |  |  |  | 2271 | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100125 | 15S | Approved | P1 | 1 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83.6 | 42.7 | 80 | 104.5 |  |  |  |  | 2274 | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100126 | 15S | Approved | P1 | 1 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 236 | 186.5 | 262 | 90.1 |  |  |  |  | 2277 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100127 | 15S | Approved | P1 | 1 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 85.2 | 42.7 | 80 | 106.5 |  |  |  |  | 2277 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100128 | 15S | Approved | P1 | 1 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.7 | 173.6 | 225 | 91.4 |  |  |  |  | 2414 | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 |  |  | No violation: below Rate A
100129 | 15S | Approved | P1 | 1 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.5 | 34.5 | 39 | 91 |  |  |  |  | 2456 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Facility: Radial
100130 | 15S | Approved | P1 | 1 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.8 | 34.5 | 39 | 91.7 |  |  |  |  | 2461 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Facility: Radial
100131 | 15S | Approved | P1 | 1 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 182.3 | 114.4 | 191 | 95.4 |  |  |  |  | 2483 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100132 | 15S | Approved | P1 | 1 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 1 | LN | 75.4 | 17.5 | 80 | 94.3 |  |  |  |  | 2535 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 | 337371 | 337372 | 1 |  | 115 | 115 | 351 | EES | 338 | DERS | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 |  | Project Horizon | No violation: below Rate A | 13-ELL-005-HZ | 2020-06-01 | Vienna to Ruston Frazier Road 115 kV Line 173: Upgrade metering CTs at Ruston
100133 | 15S | Approved | P1 | 1 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 649.8 | 99.9 | 700 | 92.8 |  |  |  |  | 2722 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100134 | 15S | Approved | P1 | 1 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239.5 | 90.3 | 204 | 117.4 |  |  |  |  | 2722 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100135 | 15S | Approved | P1 | 1 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 216.4 | 67.1 | 188 | 115.1 |  |  |  |  | 2722 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100136 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 150.4 | 91.4 | 150 | 100.3 |  |  |  |  | 2731 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1
100137 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 153.9 | 93.6 | 150 | 102.6 |  |  |  |  | 2731 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1
100138 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 155.9 | 93.6 | 150 | 103.9 |  |  |  |  | 2737 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502404 BONIN 4 138 502405 BONIN 2 69.0 1
100139 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 154.9 | 91.4 | 150 | 103.3 |  |  |  |  | 2738 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502404 BONIN 4 138 502405 BONIN 2 69.0 2
100140 | 15S | Approved | P1 | 1 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | LN | 113.3 | 62.6 | 115 | 98.5 |  |  |  |  | 2740 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | 502407 | 502413 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 |  |  | No violation: below Rate A
100141 | 15S | Approved | P1 | 1 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | LN | 86.7 | 40.2 | 95 | 91.3 |  |  |  |  | 2741 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | 502426 | 502442 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 |  |  | No violation: below Rate A
100142 | 15S | Approved | P1 | 1 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 113.5 | 49.6 | 115 | 98.7 |  |  |  |  | 2745 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 |  |  | No violation: below Rate A
100143 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 136 | 93.6 | 150 | 90.7 |  |  |  |  | 2752 | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 |  |  | No violation: below Rate A
100144 | 15S | Approved | P1 | 1 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 136 | 93.6 | 150 | 90.7 |  |  |  |  | 2755 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | No violation: below Rate A
100145 | 15S | Approved | P1 | 1 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 87.1 | 46 | 95 | 91.6 |  |  |  |  | 2756 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 |  |  | No violation: below Rate A
100146 | 15S | Approved | P1 | 1 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 232.3 | 112.2 | 226 | 102.8 |  |  |  |  | 3883 | 3Wnd: OPEN B$0241 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0241 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
100147 | 15S | Approved | P1 | 1 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | LN | 1175.5 | 618.7 | 1195 | 98.4 |  |  |  |  | 4680 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | 514908 | 514909 | 2 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 |  |  | No violation: below Rate A
100148 | 15S | Approved | P1 | 1 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | LN | 1172.3 | 579.9 | 1195 | 98.1 |  |  |  |  | 4681 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | 514908 | 514909 | 1 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 |  |  | No violation: below Rate A
100149 | 15S | Approved | P0 | 2 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 331.8 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100150 | 15S | Approved | P0 | 2 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.2 | 34.2 | 38 | 90 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100150 | 15S | Approved | P0 | 2 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.2 | 34.2 | 38 | 90 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100151 | 15S | Approved | P0 | 2 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 87.1 | 87.1 | 93 | 93.7 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100152 | 15S | Approved | P0 | 2 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101 | 101 | 112 | 90.2 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100153 | 15S | Approved | P0 | 2 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105.1 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
100155 | 15S | Approved | P1 | 2 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 228.8 | 101.7 | 243 | 94.2 |  |  |  |  | 397 | P1_2-170 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-170 |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
100156 | 15S | Approved | P1 | 2 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.7 | 86.7 | 206 | 91.6 |  |  |  |  | 406 | P1_2-179 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-179 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100157 | 15S | Approved | P1 | 2 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.7 | 86.7 | 206 | 91.6 |  |  |  |  | 425 | P1_2-198 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100158 | 15S | Approved | P1 | 2 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 35.9 | 16.4 | 39 | 92.1 |  |  |  |  | 441 | P1_2-214 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-214 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100159 | 15S | Approved | P1 | 2 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 36.4 | 16.4 | 39 | 93.2 |  |  |  |  | 444 | P1_2-217 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-217 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100160 | 15S | Approved | P1 | 2 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 36.7 | 14 | 39 | 94.2 |  |  |  |  | 445 | P1_2-218 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100161 | 15S | Approved | P1 | 2 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39 | 16.4 | 39 | 100 |  |  |  |  | 445 | P1_2-218 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100162 | 15S | Approved | P1 | 2 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 260.8 | 164.2 | 288 | 90.6 |  |  |  |  | 525 | P1_2-298 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-298_4CENTRAL-TX!,4UNION! |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
100163 | 15S | Approved | P1 | 2 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 459.4 | 324.1 | 470 | 97.7 |  |  |  |  | 679 | P1_2-452 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452 |  | Reduce PPG Plant | No violation: below Rate A
100164 | 15S | Approved | P1 | 2 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 334.1 | 331.8 | 360 | 92.8 |  |  |  |  | 704 | P1_2-477 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-477 |  |  | Facility: GSU
100165 | 15S | Approved | P1 | 2 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 203.3 | 173.6 | 225 | 90.3 |  |  |  |  | 765 | P1_2-538 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-538 |  |  | No violation: below Rate A
100166 | 15S | Approved | P1 | 2 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.6 | 173.6 | 225 | 92.3 |  |  |  |  | 766 | P1_2-539 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-539 |  |  | No violation: below Rate A
100167 | 15S | Approved | P1 | 2 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 216.4 | 173.6 | 225 | 96.2 |  |  |  |  | 769 | P1_2-542 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-542 |  |  | No violation: below Rate A
100168 | 15S | Approved | P1 | 2 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 207.8 | 165.1 | 225 | 92.4 |  |  |  |  | 769 | P1_2-542 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-542 |  |  | No violation: below Rate A
100169 | 15S | Approved | P1 | 2 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 181.9 | 114.4 | 191 | 95.2 |  |  |  |  | 786 | P1_2-559 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100170 | 15S | Approved | P1 | 2 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 181.9 | 114.4 | 191 | 95.2 |  |  |  |  | 787 | P1_2-560 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-560 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100171 | 15S | Approved | P1 | 2 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 39.8 | 18.7 | 39 | 102.1 |  |  |  |  | 790 | P1_2-563 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-563 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100172 | 15S | Approved | P1 | 2 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 36.1 | 15.4 | 39 | 92.5 |  |  |  |  | 790 | P1_2-563 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-563 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100173 | 15S | Approved | P1 | 2 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.2 | 23.9 | 39 | 97.9 |  |  |  |  | 790 | P1_2-563 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-563 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100174 | 15S | Approved | P1 | 2 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 36.5 | 23.9 | 39 | 93.6 |  |  |  |  | 800 | P1_2-573 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-573 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100175 | 15S | Approved | P1 | 2 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 614.8 | 478.7 | 672 | 91.5 |  |  |  |  | 973 | P1_2-746 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-746 |  |  | No violation: below Rate A
100176 | 15S | Approved | P1 | 2 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 95.2 | 46.3 | 100 | 95.2 |  |  |  |  | 982 | P1_2-755 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-755 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100177 | 15S | Approved | P1 | 2 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 93.9 | 45.7 | 100 | 93.9 |  |  |  |  | 982 | P1_2-755 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-755 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100178 | 15S | Approved | P1 | 2 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 270.6 | 157.2 | 300 | 90.2 |  |  |  |  | 990 | P1_2-763 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-763 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100179 | 15S | Approved | P1 | 2 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 271.5 | 158.9 | 300 | 90.5 |  |  |  |  | 991 | P1_2-764 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-764 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100182 | 15S | Approved | P1 | 2 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 632.7 | 478.7 | 672 | 94.2 |  |  |  |  | 1002 | P1_2-775 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6FANCY_PT%,8FANCY_PT% |  |  | No violation: below Rate A
100183 | 15S | Approved | P1 | 2 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 632.7 | 478.7 | 672 | 94.2 |  |  |  |  | 1012 | P1_2-785 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785 |  |  | No violation: below Rate A
100185 | 15S | Approved | P1 | 2 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194 | 142.8 | 199 | 97.5 |  |  |  |  | 1087 | P1_2-860 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100186 | 15S | Approved | P1 | 2 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 214.4 | 134.7 | 229 | 93.6 |  |  |  |  | 1173 | P1_2-946 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-946 |  |  | No violation: below Rate A
100187 | 15S | Approved | P1 | 2 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 210.8 | 160.2 | 229 | 92.1 |  |  |  |  | 1174 | P1_2-947 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-947 |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100191 | 15S | Approved | P1 | 2 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101 | 112 | 91.7 |  |  |  |  | 1337 | P1_2-1110 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1110 |  |  | Facility: Radial
100192 | 15S | Approved | P1 | 2 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 289.9 | 217.1 | 278 | 104.3 |  |  |  |  | 1356 | P1_2-1129 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1129 |  | SPS: Clarksdale
100193 | 15S | Approved | P1 | 2 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 217.1 | 278 | 107 |  |  |  |  | 1357 | P1_2-1130 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1130 |  | SPS: Clarksdale
100194 | 15S | Approved | P1 | 2 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 295.6 | 75.5 | 278 | 106.3 |  |  |  |  | 1361 | P1_2-1134 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
100195 | 15S | Approved | P1 | 2 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 306.1 | 82.4 | 250 | 122.4 |  |  |  |  | 1361 | P1_2-1134 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
100196 | 15S | Approved | P1 | 2 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 104.2 | 80.6 | 115 | 90.6 |  |  |  |  | 1397 | P1_2-1170 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1170 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100197 | 15S | Approved | P1 | 2 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.7 | 34.5 | 39 | 91.7 |  |  |  |  | 1400 | P1_2-1173 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | Facility: Radial
100198 | 15S | Approved | P1 | 2 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 242.3 | 186.5 | 262 | 92.5 |  |  |  |  | 1435 | P1_2-1208 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1208 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100199 | 15S | Approved | P1 | 2 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83.4 | 42.7 | 80 | 104.3 |  |  |  |  | 1436 | P1_2-1209 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100200 | 15S | Approved | P1 | 2 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.3 | 101 | 112 | 91.4 |  |  |  |  | 1472 | P1_2-1245 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1245 |  |  | Facility: Radial
100201 | 15S | Approved | P1 | 2 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.2 | 101 | 112 | 91.2 |  |  |  |  | 1497 | P1_2-1270 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1270 |  |  | Facility: Radial
100202 | 15S | Approved | P1 | 2 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.5 | 101 | 112 | 91.6 |  |  |  |  | 1506 | P1_2-1279 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1279_3EL DORADO!,3MONTCELO.E! |  |  | Facility: Radial
100203 | 15S | Approved | P1 | 2 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 246.9 | 181 | 266 | 92.8 |  |  |  |  | 1513 | P1_2-1286 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1286 |  |  | No violation: below Rate A
100204 | 15S | Approved | P1 | 2 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 216.1 | 161.1 | 239 | 90.4 |  |  |  |  | 1517 | P1_2-1290 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1290 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100205 | 15S | Approved | P1 | 2 | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 | TR | 515.3 | 308 | 550 | 93.7 |  |  |  |  | 1548 | P1_2-1321 | 337740 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1321_8WHT BLUFF%,8KEO% |  |  | No violation: below Rate A
100206 | 15S | Approved | P1 | 2 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 293.7 | 79.5 | 239 | 122.9 |  |  |  |  | 1567 | P1_2-1340 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100207 | 15S | Approved | P1 | 2 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 507 | 297 | 550 | 92.2 |  |  |  |  | 1567 | P1_2-1340 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340 |  |  | No violation: below Rate A
100210 | 15S | Approved | P1 | 2 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 257.2 | 227.9 | 283 | 90.9 |  |  |  |  | 1608 | P1_2-1381 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1381 |  |  | No violation: below Rate A
100213 | 15S | Approved | P1 | 2 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 101.2 | 57.6 | 106 | 95.5 |  |  |  |  | 1670 | P1_2-1443 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100214 | 15S | Approved | P1 | 2 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 259.3 | 227.9 | 283 | 91.6 |  |  |  |  | 1681 | P1_2-1455 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1455 |  |  | No violation: below Rate A
100215 | 15S | Approved | P1 | 2 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 232.3 | 112.2 | 226 | 102.8 |  |  |  |  | 1782 | P1_2-1558 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
100216 | 15S | Approved | P1 | 2 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 649.8 | 99.9 | 700 | 92.8 |  |  |  |  | 1880 | P1_2-1656 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_COUGH 4!,PNPRARIE 4% |  |  | No violation: below Rate A
100217 | 15S | Approved | P1 | 2 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239.5 | 90.3 | 204 | 117.4 |  |  |  |  | 1880 | P1_2-1656 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_COUGH 4!,PNPRARIE 4%
100218 | 15S | Approved | P1 | 2 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 216.4 | 67.1 | 188 | 115.1 |  |  |  |  | 1880 | P1_2-1656 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_COUGH 4!,PNPRARIE 4%
100219 | 15S | Approved | P1 | 2 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 144.8 | 26.8 | 159 | 91.1 |  |  |  |  | 1951 | P1_2-1727 | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1727 |  |  | No violation: below Rate A
100220 | 15S | Approved | P1 | 2 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 149.7 | 31.6 | 157 | 95.4 |  |  |  |  | 1951 | P1_2-1727 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1727 |  |  | No violation: below Rate A
100221 | 18L | Approved | P0 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 333.1 | 360 | 92.5 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100222 | 18L | Approved | P0 | 3 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.2 | 35.2 | 39 | 90.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
100223 | 18L | Approved | P0 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101.5 | 101.5 | 112 | 90.7 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100224 | 18L | Approved | P1 | 3 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 256.3 | 225.6 | 278 | 92.2 |  |  |  |  | 302 | 337085 3DELTA SES% 115 337095 3SHELBY MS+ 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337085 3DELTA SES% 115 337095 3SHELBY MS+ 115 1 |  | SPS: Clarksdale | No violation: below Rate A
100225 | 18L | Approved | P1 | 3 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 261.5 | 225.6 | 278 | 94.1 |  |  |  |  | 311 | 337095 3SHELBY MS+ 115 337096 3ROUNDAWAY+ 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337095 3SHELBY MS+ 115 337096 3ROUNDAWAY+ 115 1 |  | SPS: Clarksdale | No violation: below Rate A
100226 | 18L | Approved | P1 | 3 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 262.4 | 225.6 | 278 | 94.4 |  |  |  |  | 313 | 337096 3ROUNDAWAY+ 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337096 3ROUNDAWAY+ 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale | No violation: below Rate A
100227 | 18L | Approved | P1 | 3 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 309.3 | 225.6 | 278 | 111.3 |  |  |  |  | 314 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
100228 | 18L | Approved | P1 | 3 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 305.3 | 225.6 | 278 | 109.8 |  |  |  |  | 315 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
100229 | 18L | Approved | P1 | 3 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 305.6 | 92.3 | 278 | 109.9 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100230 | 18L | Approved | P1 | 3 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 302.8 | 85.1 | 250 | 121.1 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100231 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101.5 | 112 | 91.7 |  |  |  |  | 395 | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 |  |  | Facility: Radial
100232 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.2 | 101.5 | 112 | 92.1 |  |  |  |  | 473 | 337579 3MONTCELO.E! 115 338656 3LACEY# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337579 3MONTCELO.E! 115 338656 3LACEY# 115 1 |  |  | Facility: Radial
100233 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.9 | 101.5 | 112 | 91.9 |  |  |  |  | 477 | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 |  |  | Facility: Radial
100234 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.1 | 101.5 | 112 | 92.1 |  |  |  |  | 478 | 337581 3CROSSETT.N! 115 338640 3CROSSETT.X# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 338640 3CROSSETT.X# 115 1 |  |  | Facility: Radial
100235 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.1 | 101.5 | 112 | 92 |  |  |  |  | 481 | 337590 3HAMBURG 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337590 3HAMBURG 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100236 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.6 | 101.5 | 112 | 92.5 |  |  |  |  | 482 | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100237 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.1 | 101.5 | 112 | 92 |  |  |  |  | 483 | 337591 3MONTROSE 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100238 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101.5 | 112 | 91.7 |  |  |  |  | 484 | 337592 3BAGBY! 115 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 337594 6BAGBY 230 1 |  |  | Facility: Radial
100239 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.6 | 101.5 | 112 | 92.5 |  |  |  |  | 487 | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100240 | 18L | Approved | P1 | 3 | 337602 3DUMAS% 115 338514 3L&D#2! 115 1 | LN | 104 | 102.3 | 114 | 91.2 |  |  |  |  | 528 | 337627 3PB IP SS% 115 337630 3PB ENERGY! 115 1 | 337602 | 338514 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337627 3PB IP SS% 115 337630 3PB ENERGY! 115 1 |  |  | No violation: below Rate A
100241 | 18L | Approved | P1 | 3 | 337602 3DUMAS% 115 338514 3L&D#2! 115 1 | LN | 104 | 102.3 | 114 | 91.2 |  |  |  |  | 529 | 337628 3PB IP! 115 337630 3PB ENERGY! 115 Z1 | 337602 | 338514 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337628 3PB IP! 115 337630 3PB ENERGY! 115 Z1 |  |  | No violation: below Rate A
100242 | 18L | Approved | P1 | 3 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.2 | 101.5 | 112 | 92.1 |  |  |  |  | 949 | 338640 3CROSSETT.X# 115 338656 3LACEY# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338640 3CROSSETT.X# 115 338656 3LACEY# 115 1 |  |  | Facility: Radial
100243 | 18L | Approved | P1 | 3 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 192.2 | 131.6 | 206 | 93.3 |  |  |  |  | 1199 | 334144 4SHEPERD! 138 334229 4COLEYCREEK 138 1 | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334144 4SHEPERD! 138 334229 4COLEYCREEK 138 1 |  |  | No violation: below Rate A
100244 | 18L | Approved | P1 | 3 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 1244 | 334229 4COLEYCREEK 138 334231 4PELCNRD! 138 1 | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334229 4COLEYCREEK 138 334231 4PELCNRD! 138 1 |  |  | No violation: below Rate A
100245 | 18L | Approved | P1 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 333.1 | 360 | 92.2 |  |  |  |  | 1307 | 334320 8CYPRESS% 500 334325 8HARTBRG% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 334320 8CYPRESS% 500 334325 8HARTBRG% 500 1 |  |  | Facility: GSU
100246 | 18L | Approved | P1 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 333.1 | 360 | 92.2 |  |  |  |  | 1311 | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 |  |  | Facility: GSU
100247 | 18L | Approved | P1 | 3 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.4 | 323.7 | 470 | 95.6 |  |  |  |  | 1617 | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 |  | Reduce PPG Plant | No violation: below Rate A
100248 | 18L | Approved | P1 | 3 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224.8 | 118.6 | 200 | 112.4 |  |  |  |  | 1654 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
100249 | 18L | Approved | P1 | 3 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224.8 | 118.6 | 200 | 112.4 |  |  |  |  | 1655 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
100250 | 18L | Approved | P1 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 337.7 | 333.1 | 360 | 93.8 |  |  |  |  | 1656 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 335190 6NELSON% 230 335192 8NELSON% 500 1 |  |  | Facility: GSU
100251 | 18L | Approved | P1 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.1 | 333.1 | 360 | 92.2 |  |  |  |  | 1658 | 335192 8NELSON% 500 335367 8RICHARD% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 335192 8NELSON% 500 335367 8RICHARD% 500 1 |  |  | Facility: GSU
100252 | 18L | Approved | P1 | 3 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 2095 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100253 | 18L | Approved | P1 | 3 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 2336 | Unit:334440 1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | Unit:334440 1G4SABIN! 24.0 Id:1 |  |  | Facility: GSU
100254 | 18L | Approved | P1 | 3 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 645.1 | 75 | 700 | 92.2 |  |  |  |  | 2686 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100255 | 18L | Approved | P1 | 3 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 229.1 | 77.3 | 204 | 112.3 |  |  |  |  | 2686 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100256 | 18L | Approved | P0 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 333.1 | 360 | 92.5 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100257 | 18L | Approved | P0 | 4 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.2 | 35.2 | 39 | 90.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
100258 | 18L | Approved | P0 | 4 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101.5 | 101.5 | 112 | 90.7 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100259 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 26 | G-334440-1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | G-334440-1 |  |  | Facility: GSU
100260 | 18L | Approved | P1 | 4 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 356 | P1_2-198 | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! |  |  | No violation: below Rate A
100261 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 333.1 | 360 | 92.2 |  |  |  |  | 417 | P1_2-259 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-259_8CYPRESS%,8HARTBRG% |  |  | Facility: GSU
100262 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 333.1 | 360 | 92.2 |  |  |  |  | 421 | P1_2-263 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-263 |  |  | Facility: GSU
100263 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 475 | P1_2-317 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-317_6SABINE%,1G4SABIN! |  |  | Facility: GSU
100264 | 18L | Approved | P1 | 4 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.4 | 323.7 | 470 | 95.6 |  |  |  |  | 616 | P1_2-458 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% |  | Reduce PPG Plant | No violation: below Rate A
100265 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 337.7 | 333.1 | 360 | 93.8 |  |  |  |  | 641 | P1_2-483 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-483_6NELSON%,8NELSON% |  |  | Facility: GSU
100266 | 18L | Approved | P1 | 4 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.1 | 333.1 | 360 | 92.2 |  |  |  |  | 646 | P1_2-488 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-488 |  |  | Facility: GSU
100267 | 18L | Approved | P1 | 4 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 993 | P1_2-835 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! |  | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100268 | 18L | Approved | P1 | 4 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101.5 | 112 | 91.7 |  |  |  |  | 1273 | P1_2-1115 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1115_6ANDRUS%,3BAGBY! |  |  | Facility: Radial
100269 | 18L | Approved | P1 | 4 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 262.4 | 225.6 | 278 | 94.4 |  |  |  |  | 1293 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale | No violation: below Rate A
100270 | 18L | Approved | P1 | 4 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 309.3 | 225.6 | 278 | 111.3 |  |  |  |  | 1295 | P1_2-1137 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! |  | SPS: Clarksdale
100271 | 18L | Approved | P1 | 4 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 305.3 | 225.6 | 278 | 109.8 |  |  |  |  | 1296 | P1_2-1138 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! |  | SPS: Clarksdale
100272 | 18L | Approved | P1 | 4 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 305.6 | 92.3 | 278 | 109.9 |  |  |  |  | 1300 | P1_2-1142 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
100273 | 18L | Approved | P1 | 4 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 302.8 | 85.1 | 250 | 121.1 |  |  |  |  | 1300 | P1_2-1142 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
100274 | 18L | Approved | P1 | 4 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.1 | 101.5 | 112 | 92.1 |  |  |  |  | 1442 | P1_2-1284 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1284 |  |  | Facility: Radial
100275 | 18L | Approved | P1 | 4 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.9 | 101.5 | 112 | 91.9 |  |  |  |  | 1445 | P1_2-1287 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1287 |  |  | Facility: Radial
100276 | 18L | Approved | P1 | 4 | 337602 3DUMAS% 115 338514 3L&D#2! 115 1 | LN | 104 | 102.3 | 114 | 91.2 |  |  |  |  | 1466 | P1_2-1308 | 337602 | 338514 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1308_3PB IP SS%,3PB ENERGY! |  |  | No violation: below Rate A
100277 | 18L | Approved | P1 | 4 | 337602 3DUMAS% 115 338514 3L&D#2! 115 1 | LN | 104 | 102.3 | 114 | 91.2 |  |  |  |  | 1467 | P1_2-1309 | 337602 | 338514 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1309_3PB IP!,3PB ENERGY! |  |  | No violation: below Rate A
100278 | 18L | Approved | P1 | 4 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 645.1 | 75 | 700 | 92.2 |  |  |  |  | 1819 | P1_2-1664 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
100279 | 18L | Approved | P1 | 4 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 229.1 | 77.3 | 204 | 112.3 |  |  |  |  | 1819 | P1_2-1664 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7
100280 | 18S | Approved | P0 | 5 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 331.8 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100281 | 18S | Approved | P0 | 5 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 36.3 | 36.3 | 38 | 95.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100281 | 18S | Approved | P0 | 5 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 36.3 | 36.3 | 38 | 95.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100282 | 18S | Approved | P0 | 5 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 94.8 | 94.8 | 93 | 102 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100283 | 18S | Approved | P0 | 5 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 18.3 | 18.3 | 20 | 91.5 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
100284 | 18S | Approved | P0 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 178.7 | 178.7 | 193 | 92.6 |  |  |  |  | 0 | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | Facility: Radial
100285 | 18S | Approved | P0 | 5 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.6 | 35.6 | 39 | 91.2 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
100286 | 18S | Approved | P0 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 104.3 | 104.3 | 112 | 93.1 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100287 | 18S | Approved | P0 | 5 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
100288 | 18S | Approved | P1 | 5 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 180.9 | 114.4 | 199 | 90.9 |  |  |  |  | 51 | 336556 3W.BROOKHAVN 115 336557 3CALIFORNIA 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336556 3W.BROOKHAVN 115 336557 3CALIFORNIA 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100289 | 18S | Approved | P1 | 5 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 187.3 | 114.4 | 199 | 94.1 |  |  |  |  | 52 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100290 | 18S | Approved | P1 | 5 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 212.5 | 139 | 231 | 92 |  |  |  |  | 52 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100291 | 18S | Approved | P1 | 5 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 193.3 | 114.4 | 199 | 97.1 |  |  |  |  | 53 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100292 | 18S | Approved | P1 | 5 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 218.7 | 139 | 231 | 94.7 |  |  |  |  | 53 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100293 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 57 | 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 |  |  | Facility: Radial
100294 | 18S | Approved | P1 | 5 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38.4 | 35.6 | 39 | 98.5 |  |  |  |  | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | Facility: Radial
100295 | 18S | Approved | P1 | 5 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 105.6 | 82.5 | 115 | 91.8 |  |  |  |  | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100296 | 18S | Approved | P2 | 5 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 159.2 | 83 | 161 | 98.9 |  |  |  |  | 100 | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100297 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 178.7 | 193 | 93.7 |  |  |  |  | 112 | 336830 8BXTRWILSON% 500 336839 8R.BRASWELL% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336830 8BXTRWILSON% 500 336839 8R.BRASWELL% 500 1 |  |  | Facility: Radial
100298 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.2 |  |  |  |  | 113 | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 1 |  |  | Facility: Radial
100299 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 114 | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 2 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 2 |  |  | Facility: Radial
100300 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.1 | 178.7 | 193 | 93.3 |  |  |  |  | 115 | 336839 8R.BRASWELL% 500 336880 3R.BRASWELL% 115 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336880 3R.BRASWELL% 115 1 |  |  | Facility: Radial
100301 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 178.7 | 193 | 93.4 |  |  |  |  | 120 | 336840 6R.BRASWELL% 230 336856 6NORTHSIDE 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336840 6R.BRASWELL% 230 336856 6NORTHSIDE 230 1 |  |  | Facility: Radial
100302 | 18S | Approved | P1 | 5 | 336906 3MONUMENT! 115 336907 3MIAMI ST 115 1 | LN | 290.8 | 213.1 | 320 | 90.9 |  |  |  |  | 124 | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 | 336906 | 336907 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
100303 | 18S | Approved | P1 | 5 | 336907 3MIAMI ST 115 336938 3REX BRWN-W! 115 1 | LN | 304.3 | 226.5 | 320 | 95.1 |  |  |  |  | 124 | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 | 336907 | 336938 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
100304 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.7 | 178.7 | 193 | 93.7 |  |  |  |  | 132 | 336848 6LAKEOVER% 230 336852 6HINDS-1 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336848 6LAKEOVER% 230 336852 6HINDS-1 230 1 |  |  | Facility: Radial
100305 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 175.7 | 178.7 | 193 | 91.1 |  |  |  |  | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  |  | Facility: Radial
100306 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 137 | 336855 6REX BROWN! 230 336856 6NORTHSIDE 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336855 6REX BROWN! 230 336856 6NORTHSIDE 230 1 |  |  | Facility: Radial
100307 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 177.2 | 178.7 | 193 | 91.8 |  |  |  |  | 138 | 336855 6REX BROWN! 230 336939 3REX BRWN-C! 115 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336855 6REX BROWN! 230 336939 3REX BRWN-C! 115 1 |  |  | Facility: Radial
100308 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.2 | 178.7 | 193 | 91.3 |  |  |  |  | 140 | 336860 6CHARITY CH 230 336861 6HOY RD 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336860 6CHARITY CH 230 336861 6HOY RD 230 1 |  |  | Facility: Radial
100309 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.1 | 178.7 | 193 | 91.3 |  |  |  |  | 141 | 336861 6HOY RD 230 336862 6YANDELL RD! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336861 6HOY RD 230 336862 6YANDELL RD! 230 1 |  |  | Facility: Radial
100310 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 178.7 | 193 | 93.4 |  |  |  |  | 146 | 336864 6S.CANTON! 230 336866 6CANTON 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336864 6S.CANTON! 230 336866 6CANTON 230 1 |  |  | Facility: Radial
100311 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181.4 | 178.7 | 193 | 94 |  |  |  |  | 147 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336866 6CANTON 230 337015 6PICKENS! 230 1 |  |  | Facility: Radial
100312 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.2 |  |  |  |  | 192 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 |  |  | Facility: Radial
100313 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.6 | 178.7 | 193 | 93.6 |  |  |  |  | 200 | 336945 8LAKEOVER% 500 337009 8MCADAMS% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336945 8LAKEOVER% 500 337009 8MCADAMS% 500 1 |  |  | Facility: Radial
100314 | 18S | Approved | P1 | 5 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 147 | 83 | 161 | 91.3 |  |  |  |  | 201 | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100315 | 18S | Approved | P2 | 5 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 105.8 | 49.7 | 108 | 98 |  |  |  |  | 207 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
100316 | 18S | Approved | P1 | 5 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 543.7 | 323 | 561 | 96.9 |  |  |  |  | 232 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
100317 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 178.7 | 193 | 93.7 |  |  |  |  | 235 | 337000 6MCADAMS% 230 337015 6PICKENS! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337000 6MCADAMS% 230 337015 6PICKENS! 230 1 |  |  | Facility: Radial
100318 | 18S | Approved | P1 | 5 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 288.6 | 211 | 278 | 103.8 |  |  |  |  | 314 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
100319 | 18S | Approved | P1 | 5 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 211 | 278 | 107 |  |  |  |  | 315 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
100320 | 18S | Approved | P1 | 5 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 293.6 | 80.2 | 278 | 105.6 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100321 | 18S | Approved | P1 | 5 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 304.9 | 88.5 | 250 | 121.9 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100322 | 18S | Approved | P1 | 5 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 178.7 | 193 | 93.4 |  |  |  |  | 367 | Unit:336853 1HINDS G1 18.0 Id:1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | Unit:336853 1HINDS G1 18.0 Id:1 |  |  | Facility: Radial
100323 | 18S | Approved | P1 | 5 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 192.1 | 142.2 | 199 | 96.5 |  |  |  |  | 391 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100324 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.8 | 104.3 | 112 | 94.5 |  |  |  |  | 400 | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 |  |  | Facility: Radial
100325 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.6 | 104.3 | 112 | 94.3 |  |  |  |  | 482 | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 |  |  | Facility: Radial
100326 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.4 | 104.3 | 112 | 94.1 |  |  |  |  | 485 | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100327 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.9 | 104.3 | 112 | 94.6 |  |  |  |  | 486 | 337590 3HAMBURG 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337590 3HAMBURG 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100328 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 106.4 | 104.3 | 112 | 95 |  |  |  |  | 487 | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100329 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.9 | 104.3 | 112 | 94.6 |  |  |  |  | 488 | 337591 3MONTROSE 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100330 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.8 | 104.3 | 112 | 94.5 |  |  |  |  | 489 | 337592 3BAGBY! 115 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 337594 6BAGBY 230 1 |  |  | Facility: Radial
100331 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 106.5 | 104.3 | 112 | 95.1 |  |  |  |  | 492 | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100332 | 18S | Approved | P1 | 5 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 243 | 178.9 | 266 | 91.3 |  |  |  |  | 515 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 |  |  | No violation: below Rate A
100333 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.5 | 104.3 | 112 | 94.2 |  |  |  |  | 517 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  |  | Facility: Radial
100334 | 18S | Approved | P1 | 5 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 219.1 | 159 | 239 | 91.7 |  |  |  |  | 543 | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100335 | 18S | Approved | P1 | 5 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 227.2 | 159 | 239 | 95 |  |  |  |  | 544 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100336 | 18S | Approved | P1 | 5 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 233.9 | 165.7 | 253 | 92.5 |  |  |  |  | 544 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100337 | 18S | Approved | P1 | 5 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 231.1 | 159 | 239 | 96.7 |  |  |  |  | 545 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100338 | 18S | Approved | P1 | 5 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 237.9 | 165.7 | 253 | 94 |  |  |  |  | 545 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100339 | 18S | Approved | P1 | 5 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 245.7 | 178.9 | 266 | 92.4 |  |  |  |  | 546 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 |  |  | No violation: below Rate A
100340 | 18S | Approved | P1 | 5 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 168.7 | 92 | 176 | 95.9 |  |  |  |  | 581 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
100341 | 18S | Approved | P1 | 5 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 167.7 | 91.1 | 176 | 95.3 |  |  |  |  | 581 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
100342 | 18S | Approved | P2 | 5 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 156.4 | 87.2 | 159 | 98.4 |  |  |  |  | 595 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 |  | Project Approved | No violation: below Rate A | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100343 | 18S | Approved | P2 | 5 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | LN | 156.4 | 68.3 | 159 | 98.4 |  |  |  |  | 600 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337710 | 337713 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | No violation: below Rate A | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100344 | 18S | Approved | P2 | 5 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 149.3 | 74.2 | 159 | 93.9 |  |  |  |  | 607 | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 |  | Project Horizon | No violation: below Rate A | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100345 | 18S | Approved | P1 | 5 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 145.4 | 74.2 | 159 | 91.5 |  |  |  |  | 610 | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 |  | Project Horizon | Contingency: invalid, no breakers | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100346 | 18S | Approved | P1 | 5 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 419.5 | 294.3 | 448 | 93.6 |  |  |  |  | 623 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100347 | 18S | Approved | P1 | 5 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | TR | 420.3 | 295.2 | 448 | 93.8 |  |  |  |  | 630 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | 337799 | 337808 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100348 | 18S | Approved | P1 | 5 | 337815 3MANN RD 115 337816 3LR CHICOT 115 1 | LN | 281.8 | 187.7 | 298 | 94.5 |  |  |  |  | 632 | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 | 337815 | 337816 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 |  |  | No violation: below Rate A
100349 | 18S | Approved | P1 | 5 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 261.3 | 232.7 | 283 | 92.3 |  |  |  |  | 655 | 337826 3PINNACLE! 115 337827 3NATURAL STP 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337826 3PINNACLE! 115 337827 3NATURAL STP 115 1 |  |  | No violation: below Rate A
100350 | 18S | Approved | P1 | 5 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 262.5 | 232.7 | 283 | 92.8 |  |  |  |  | 659 | 337827 3NATURAL STP 115 337930 3MAYFLOWER% 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337827 3NATURAL STP 115 337930 3MAYFLOWER% 115 1 |  |  | No violation: below Rate A
100351 | 18S | Approved | P1 | 5 | 337921 5MORILTON.E! 161 337927 5GLEASON 161 1 | LN | 202.5 | 131.7 | 223 | 90.8 |  |  |  |  | 706 | 337929 3LAKE CONWAY 115 337930 3MAYFLOWER% 115 1 | 337921 | 337927 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 337929 3LAKE CONWAY 115 337930 3MAYFLOWER% 115 1 |  |  | No violation: below Rate A
100352 | 18S | Approved | P1 | 5 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 257.5 | 232.7 | 283 | 91 |  |  |  |  | 711 | 337930 3MAYFLOWER% 115 338760 3OLMSTEAD# 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337930 3MAYFLOWER% 115 338760 3OLMSTEAD# 115 1 |  |  | No violation: below Rate A
100353 | 18S | Approved | P1 | 5 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 256 | 232.7 | 283 | 90.5 |  |  |  |  | 717 | 337936 3SYLVAN HLS! 115 338760 3OLMSTEAD# 115 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337936 3SYLVAN HLS! 115 338760 3OLMSTEAD# 115 1 |  |  | No violation: below Rate A
100354 | 18S | Approved | P1 | 5 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 106.6 | 46.2 | 106 | 100.5 |  |  |  |  | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100355 | 18S | Approved | P1 | 5 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 102.9 | 43.3 | 106 | 97.1 |  |  |  |  | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100356 | 18S | Approved | P1 | 5 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 97.4 | 40 | 106 | 91.9 |  |  |  |  | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100357 | 18S | Approved | P1 | 5 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 96.4 | 59.1 | 106 | 90.9 |  |  |  |  | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100358 | 18S | Approved | P1 | 5 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 102.9 | 59.1 | 106 | 97.1 |  |  |  |  | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100359 | 18S | Approved | P1 | 5 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 265.8 | 232.7 | 283 | 93.9 |  |  |  |  | 786 | 338016 3HOLND BTM! 115 338140 8HOLND BTM% 500 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338016 3HOLND BTM! 115 338140 8HOLND BTM% 500 1 |  |  | No violation: below Rate A
100360 | 18S | Approved | P1 | 5 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 150.4 | 77.5 | 148 | 101.6 |  |  |  |  | 847 | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 |  | Project Proposed |  | 11-EAI-025-CP | 2016-06-01 | Upgrade Norfork-Calico Rock 161 kV
100361 | 18S | Approved | P2 | 5 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 148.6 | 82 | 148 | 100.4 |  |  |  |  | 864 | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 |  | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100362 | 18S | Approved | P1 | 5 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 133.9 | 107.7 | 148 | 90.5 |  |  |  |  | 869 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 |  |  | No violation: below Rate A
100363 | 18S | Approved | P2 | 5 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 134.7 | 82 | 148 | 91 |  |  |  |  | 876 | 338170 5JONESBORO! 161 338171 5CASH 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338170 5JONESBORO! 161 338171 5CASH 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100364 | 18S | Approved | P1 | 5 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 140.2 | 82 | 148 | 94.7 |  |  |  |  | 879 | 338171 5CASH 161 338172 5NEWPORT AB 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338171 5CASH 161 338172 5NEWPORT AB 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100365 | 18S | Approved | P1 | 5 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 147 | 82 | 148 | 99.3 |  |  |  |  | 880 | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100366 | 18S | Approved | P1 | 5 | 338202 5JIM HILL% 161 338230 3JIM HILL! 115 1 | TR | 101.6 | 51.5 | 112 | 90.7 |  |  |  |  | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338202 | 338230 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100367 | 18S | Approved | P1 | 5 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 86.1 | 37.8 | 70 | 123 |  |  |  |  | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100368 | 18S | Approved | P1 | 5 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 93.8 | 44.2 | 70 | 134 |  |  |  |  | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100369 | 18S | Approved | P1 | 5 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 67.4 | 37.8 | 70 | 96.3 |  |  |  |  | 925 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100370 | 18S | Approved | P1 | 5 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 74.3 | 44.2 | 70 | 106.2 |  |  |  |  | 925 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100371 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.5 | 104.3 | 112 | 94.2 |  |  |  |  | 1024 | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100372 | 18S | Approved | P1 | 5 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.5 | 104.3 | 112 | 94.2 |  |  |  |  | 1027 | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 |  |  | Facility: Radial
100373 | 18S | Approved | P1 | 5 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 201 | 111.8 | 223 | 90.1 |  |  |  |  | 1068 | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 |  |  | No violation: below Rate A
100374 | 18S | Approved | P1 | 5 | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 | LN | 205.6 | 110.4 | 223 | 92.2 |  |  |  |  | 1069 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | 338161 | 338412 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 |  |  | No violation: below Rate A
100375 | 18S | Approved | P1 | 5 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 134.8 | 107.7 | 148 | 91.1 |  |  |  |  | 1075 | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 |  |  | No violation: below Rate A
100376 | 18S | Approved | P1 | 5 | 338202 5JIM HILL% 161 338230 3JIM HILL! 115 1 | TR | 101.2 | 51.5 | 112 | 90.4 |  |  |  |  | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338202 | 338230 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100377 | 18S | Approved | P1 | 5 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 85.8 | 37.8 | 70 | 122.5 |  |  |  |  | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100378 | 18S | Approved | P1 | 5 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 93.5 | 44.2 | 70 | 133.6 |  |  |  |  | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100379 | 18S | Approved | P1 | 5 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 200.9 | 143.8 | 206 | 97.5 |  |  |  |  | 1153 | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100380 | 18S | Approved | P1 | 5 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 193.8 | 143.8 | 206 | 94.1 |  |  |  |  | 1154 | 334072 4LEWIS% 138 334090 4ALDEN! 138 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334090 4ALDEN! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100381 | 18S | Approved | P1 | 5 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 194.7 | 143.8 | 206 | 94.5 |  |  |  |  | 1167 | 334086 4CANEYCREEK! 138 334106 4CONAIR 138 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334086 4CANEYCREEK! 138 334106 4CONAIR 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100382 | 18S | Approved | P1 | 5 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 231.7 | 99.8 | 243 | 95.4 |  |  |  |  | 1176 | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
100383 | 18S | Approved | P1 | 5 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.1 | 86.5 | 206 | 91.3 |  |  |  |  | 1187 | 3Wnd: OPEN B$1601 PORTER 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 3Wnd: OPEN B$1601 PORTER 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100384 | 18S | Approved | P1 | 5 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.2 | 86.5 | 206 | 91.4 |  |  |  |  | 1230 | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100385 | 18S | Approved | P1 | 5 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.2 | 86.5 | 206 | 91.4 |  |  |  |  | 1231 | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100386 | 18S | Approved | P1 | 5 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.2 | 86.5 | 206 | 91.4 |  |  |  |  | 1232 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100387 | 18S | Approved | P1 | 5 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 36.8 | 17 | 39 | 94.3 |  |  |  |  | 1260 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100388 | 18S | Approved | P1 | 5 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 37.2 | 17 | 39 | 95.5 |  |  |  |  | 1263 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100389 | 18S | Approved | P1 | 5 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 35.8 | 14.4 | 39 | 91.7 |  |  |  |  | 1264 | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100390 | 18S | Approved | P1 | 5 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 38.1 | 17 | 39 | 97.8 |  |  |  |  | 1264 | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100391 | 18S | Approved | P1 | 5 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.6 | 14.4 | 39 | 96.3 |  |  |  |  | 1265 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100392 | 18S | Approved | P1 | 5 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40 | 17 | 39 | 102.6 |  |  |  |  | 1265 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100393 | 18S | Approved | P1 | 5 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 265.1 | 167.1 | 288 | 92 |  |  |  |  | 1396 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
100394 | 18S | Approved | P1 | 5 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 273.5 | 176.1 | 287 | 95.3 |  |  |  |  | 1400 | 334414 4LINDE 138 334430 4SABINE! 138 1 | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334414 4LINDE 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
100395 | 18S | Approved | P1 | 5 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 66 | 20.4 | 72 | 91.6 |  |  |  |  | 1605 | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 |  |  | No violation: below Rate A
100396 | 18S | Approved | P1 | 5 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 67.8 | 20.4 | 72 | 94.1 |  |  |  |  | 1610 | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 |  |  | No violation: below Rate A
100397 | 18S | Approved | P1 | 5 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30 | 23.8 | 33 | 91 |  |  |  |  | 1642 | 335074 6CALCASIEU% 230 335077 6PECAN_GRV! 230 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335074 6CALCASIEU% 230 335077 6PECAN_GRV! 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100398 | 18S | Approved | P1 | 5 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30.1 | 23.8 | 33 | 91.1 |  |  |  |  | 1644 | 335078 6VINCENT 230 335079 6GRAYWOOD% 230 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335078 6VINCENT 230 335079 6GRAYWOOD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100399 | 18S | Approved | P1 | 5 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.7 | 36.3 | 38 | 91.4 |  |  |  |  | 1661 | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 |  |  | Delta: No worse than P0
100400 | 18S | Approved | P1 | 5 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 225.9 | 121.2 | 200 | 112.9 |  |  |  |  | 1676 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
100401 | 18S | Approved | P1 | 5 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 225.9 | 121.2 | 200 | 112.9 |  |  |  |  | 1677 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
100402 | 18S | Approved | P1 | 5 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 334.2 | 331.8 | 360 | 92.8 |  |  |  |  | 1678 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 335190 6NELSON% 230 335192 8NELSON% 500 1 |  |  | Facility: GSU
100403 | 18S | Approved | P1 | 5 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 212.2 | 177.6 | 225 | 94.3 |  |  |  |  | 1780 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100404 | 18S | Approved | P1 | 5 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 203.8 | 169.1 | 225 | 90.6 |  |  |  |  | 1780 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100405 | 18S | Approved | P1 | 5 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 216.3 | 177.6 | 225 | 96.1 |  |  |  |  | 1781 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100406 | 18S | Approved | P1 | 5 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 207.7 | 169.1 | 225 | 92.3 |  |  |  |  | 1781 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100407 | 18S | Approved | P1 | 5 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 195.5 | 123.1 | 191 | 102.3 |  |  |  |  | 1788 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100408 | 18S | Approved | P1 | 5 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 211.4 | 123.1 | 191 | 110.7 |  |  |  |  | 1790 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100409 | 18S | Approved | P1 | 5 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 223.6 | 104 | 233 | 96 |  |  |  |  | 1791 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon | No violation: below Rate A | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
100409 | 18S | Approved | P1 | 5 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 223.6 | 104 | 233 | 96 |  |  |  |  | 1791 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon | No violation: below Rate A | 14-EGL-015-HZ | 2022-06-01 | Meaux to Abbeville - Reconductor Line
100410 | 18S | Approved | P1 | 5 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 42.6 | 20 | 39 | 109.4 |  |  |  |  | 1794 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100411 | 18S | Approved | P1 | 5 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 38.9 | 16.7 | 39 | 99.6 |  |  |  |  | 1794 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100412 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 40.2 | 25.2 | 39 | 103.1 |  |  |  |  | 1794 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100413 | 18S | Approved | P1 | 5 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 42.6 | 20 | 39 | 109.2 |  |  |  |  | 1801 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100414 | 18S | Approved | P1 | 5 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 38.7 | 16.7 | 39 | 99.3 |  |  |  |  | 1801 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100415 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.5 | 25.2 | 39 | 98.7 |  |  |  |  | 1803 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100416 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 40.5 | 25.2 | 39 | 103.9 |  |  |  |  | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100416 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 40.5 | 25.2 | 39 | 103.9 |  |  |  |  | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100417 | 18S | Approved | P1 | 5 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 39.6 | 17.7 | 39 | 101.7 |  |  |  |  | 1810 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100417 | 18S | Approved | P1 | 5 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 39.6 | 17.7 | 39 | 101.7 |  |  |  |  | 1810 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100418 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 36.1 | 25.2 | 39 | 92.5 |  |  |  |  | 1816 | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100419 | 18S | Approved | P1 | 5 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 35.5 | 25.2 | 39 | 90.9 |  |  |  |  | 1817 | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100420 | 18S | Approved | P1 | 5 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | LN | 130.1 | 51.6 | 141 | 92.2 |  |  |  |  | 1968 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335712 | 335713 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100421 | 18S | Approved | P1 | 5 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | LN | 122.2 | 68.3 | 121 | 101 |  |  |  |  | 1974 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | 335699 | 335710 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100422 | 18S | Approved | P1 | 5 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 121.8 | 58.4 | 121 | 100.6 |  |  |  |  | 1978 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100423 | 18S | Approved | P1 | 5 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 184.7 | 130.2 | 200 | 92.3 |  |  |  |  | 1979 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 1 |  |  | Model: does not represent split configuration
100424 | 18S | Approved | P1 | 5 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 181.9 | 130.2 | 200 | 91 |  |  |  |  | 1980 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 2 |  |  | Model: does not represent split configuration
100425 | 18S | Approved | P1 | 5 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 120 | 58.4 | 121 | 99.2 |  |  |  |  | 1983 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100426 | 18S | Approved | P1 | 5 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.8 | 159.8 | 200 | 90.4 |  |  |  |  | 2027 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100427 | 18S | Approved | P1 | 5 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 96.4 | 46.2 | 100 | 96.4 |  |  |  |  | 2028 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100428 | 18S | Approved | P1 | 5 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 95.1 | 45.6 | 100 | 95.1 |  |  |  |  | 2028 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100429 | 18S | Approved | P1 | 5 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.5 | 159.8 | 200 | 90.2 |  |  |  |  | 2042 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100430 | 18S | Approved | P1 | 5 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 181.7 | 159.8 | 200 | 90.8 |  |  |  |  | 2044 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100431 | 18S | Approved | P1 | 5 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 290.4 | 168.3 | 300 | 96.8 |  |  |  |  | 2044 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100432 | 18S | Approved | P1 | 5 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 181.3 | 159.8 | 200 | 90.6 |  |  |  |  | 2045 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100433 | 18S | Approved | P1 | 5 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 291.2 | 170 | 300 | 97.1 |  |  |  |  | 2045 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100434 | 18S | Approved | P1 | 5 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | LN | 561 | 323.7 | 593 | 94.6 |  |  |  |  | 2050 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | 335815 | 335825 | 2 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100435 | 18S | Approved | P1 | 5 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 564.3 | 330.6 | 593 | 95.2 |  |  |  |  | 2051 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100436 | 18S | Approved | P1 | 5 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 126.8 | 75.1 | 115 | 110.3 |  |  |  |  | 2116 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100437 | 18S | Approved | P1 | 5 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 192.2 | 142.2 | 199 | 96.6 |  |  |  |  | 2135 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100438 | 18S | Approved | P1 | 5 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 217.5 | 136.6 | 229 | 95 |  |  |  |  | 2210 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336284 3WSTWGO! 115 1 |  |  | No violation: below Rate A
100439 | 18S | Approved | P1 | 5 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 226.4 | 162.4 | 229 | 98.9 |  |  |  |  | 2211 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100440 | 18S | Approved | P1 | 5 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.7 | 35.6 | 39 | 94.2 |  |  |  |  | 2263 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 |  |  | Facility: Radial
100441 | 18S | Approved | P1 | 5 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 106.2 | 82.5 | 115 | 92.4 |  |  |  |  | 2263 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100442 | 18S | Approved | P1 | 5 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 238.9 | 192.4 | 262 | 91.2 |  |  |  |  | 2300 | 337382 3DREW_LA 115 337414 3STERL2% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337382 3DREW_LA 115 337414 3STERL2% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100443 | 18S | Approved | P1 | 5 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 249.3 | 192.4 | 262 | 95.1 |  |  |  |  | 2308 | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100444 | 18S | Approved | P1 | 5 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 241.6 | 192.4 | 262 | 92.2 |  |  |  |  | 2311 | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100445 | 18S | Approved | P1 | 5 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 79.8 | 37 | 80 | 99.8 |  |  |  |  | 2311 | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 |  | Project Approved | No violation: below Rate A | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100446 | 18S | Approved | P1 | 5 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.7 | 192.4 | 262 | 93 |  |  |  |  | 2314 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100447 | 18S | Approved | P1 | 5 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.6 | 37 | 80 | 102 |  |  |  |  | 2314 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100448 | 18S | Approved | P1 | 5 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30 | 23.8 | 33 | 91 |  |  |  |  | 2437 | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100449 | 18S | Approved | P1 | 5 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 210.5 | 177.6 | 225 | 93.6 |  |  |  |  | 2441 | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 |  |  | No violation: below Rate A
100450 | 18S | Approved | P1 | 5 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.1 | 177.6 | 225 | 91.6 |  |  |  |  | 2442 | 303130 4N_CROWLEY 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303130 4N_CROWLEY 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100451 | 18S | Approved | P1 | 5 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 183.9 | 123.1 | 191 | 96.3 |  |  |  |  | 2449 | 303150 4LEBLANC! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303150 4LEBLANC! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100452 | 18S | Approved | P1 | 5 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.7 | 35.6 | 39 | 94.1 |  |  |  |  | 2483 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Facility: Radial
100453 | 18S | Approved | P1 | 5 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.1 | 35.6 | 39 | 95 |  |  |  |  | 2488 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Facility: Radial
100454 | 18S | Approved | P1 | 5 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 195.9 | 123.1 | 191 | 102.6 |  |  |  |  | 2506 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100455 | 18S | Approved | P1 | 5 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 1 | LN | 78.6 | 18.2 | 80 | 98.2 |  |  |  |  | 2549 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 | 337371 | 337372 | 1 |  | 115 | 115 | 351 | EES | 338 | DERS | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 |  | Project Horizon | No violation: below Rate A | 13-ELL-005-HZ | 2020-06-01 | Vienna to Ruston Frazier Road 115 kV Line 173: Upgrade metering CTs at Ruston
100456 | 18S | Approved | P1 | 5 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.2 | 177.6 | 225 | 90.7 |  |  |  |  | 2649 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 500230 COUGH 4 138 500720 PLAISAN4 138 1 |  |  | No violation: below Rate A
100457 | 18S | Approved | P1 | 5 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | LN | 133.5 | 66.4 | 148 | 90.2 |  |  |  |  | 2653 | 500265 DTOWN 138 500420 HUNTER4 138 1 | 500735 | 500816 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500265 DTOWN 138 500420 HUNTER4 138 1 |  |  | No violation: below Rate A
100458 | 18S | Approved | P1 | 5 | 500265 DTOWN 138 500420 HUNTER4 138 1 | LN | 133.5 | 66 | 148 | 90.2 |  |  |  |  | 2697 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | 500265 | 500420 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 |  |  | No violation: below Rate A
100459 | 18S | Approved | P1 | 5 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 649.6 | 118.8 | 700 | 92.8 |  |  |  |  | 2732 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100460 | 18S | Approved | P1 | 5 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 228.7 | 86.4 | 204 | 112.1 |  |  |  |  | 2732 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100461 | 18S | Approved | P1 | 5 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 205.7 | 63.3 | 188 | 109.4 |  |  |  |  | 2732 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100462 | 18S | Approved | P1 | 5 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.7 | 60.7 | 115 | 90.2 |  |  |  |  | 2741 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  |  | No violation: below Rate A
100463 | 18S | Approved | P1 | 5 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 88 | 53.2 | 95 | 92.7 |  |  |  |  | 2750 | 502405 BONIN 2 69.0 502408 STGEORG2 69.0 1 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502408 STGEORG2 69.0 1 |  |  | No violation: below Rate A
100464 | 18S | Approved | P1 | 5 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | LN | 119.7 | 58.1 | 115 | 104.1 |  |  |  |  | 2751 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | 502407 | 502413 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1
100465 | 18S | Approved | P1 | 5 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | LN | 91.5 | 38.4 | 95 | 96.3 |  |  |  |  | 2752 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | 502426 | 502442 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 |  |  | No violation: below Rate A
100466 | 18S | Approved | P1 | 5 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 120.5 | 60.7 | 115 | 104.8 |  |  |  |  | 2756 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1
100467 | 18S | Approved | P1 | 5 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.5 | 99.8 | 95 | 107.9 |  |  |  |  | 2763 | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 |  |  | Facility: Radial
100468 | 18S | Approved | P1 | 5 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.6 | 99.8 | 95 | 108 |  |  |  |  | 2766 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
100469 | 18S | Approved | P1 | 5 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 92 | 53.2 | 95 | 96.9 |  |  |  |  | 2767 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 |  |  | No violation: below Rate A
100470 | 18S | Approved | P1 | 5 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 228.3 | 107.4 | 226 | 101 |  |  |  |  | 3905 | 3Wnd: OPEN B$0231 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0231 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
100471 | 18S | Approved | P1 | 5 | 360581 8PIN HOOK TN 500 990071 1.00 1 | TR | 1133.4 | 871.8 | 1253.7 | 90.4 |  |  |  |  | 3949 | 3Wnd: OPEN B$0053 1 | 360581 | 990071 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0053 1 |  |  | No violation: below Rate A
100472 | 18S | Approved | P1 | 5 | 514880 NORTWST7 345 991455 NORTWST2 1.00 1 | TR | 484 | 341.4 | 493 | 98.2 |  |  |  |  | 4705 | 3Wnd: OPEN B$1456 NORTWST3 1 | 514880 | 991455 | 1 |  | 345 | 1 | 524 | OKGE | 524 | OKGE | 3Wnd: OPEN B$1456 NORTWST3 1 |  |  | No violation: below Rate A
100473 | 18S | Approved | P1 | 5 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | LN | 1279.2 | 673.2 | 1195 | 107 |  |  |  |  | 4710 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | 514908 | 514909 | 2 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 1
100474 | 18S | Approved | P1 | 5 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | LN | 1275.8 | 630.9 | 1195 | 106.8 |  |  |  |  | 4711 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | 514908 | 514909 | 1 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 2
100475 | 18S | Approved | P0 | 6 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 331.8 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100476 | 18S | Approved | P0 | 6 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 36.3 | 36.3 | 38 | 95.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100476 | 18S | Approved | P0 | 6 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 36.3 | 36.3 | 38 | 95.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100477 | 18S | Approved | P0 | 6 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 94.8 | 94.8 | 93 | 102 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100478 | 18S | Approved | P0 | 6 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 18.3 | 18.3 | 20 | 91.5 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
100479 | 18S | Approved | P0 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 178.7 | 178.7 | 193 | 92.6 |  |  |  |  | 0 | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | Facility: Radial
100480 | 18S | Approved | P0 | 6 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.6 | 35.6 | 39 | 91.2 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
100481 | 18S | Approved | P0 | 6 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 104.3 | 104.3 | 112 | 93.1 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100482 | 18S | Approved | P0 | 6 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
100483 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 178.7 | 193 | 93.4 |  |  |  |  | 99 | G-336853-1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | G-336853-1 |  |  | Facility: Radial
100484 | 18S | Approved | P1 | 6 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 183.5 | 123.1 | 191 | 96.1 |  |  |  |  | 348 | P1_2-112 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-112 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100485 | 18S | Approved | P1 | 6 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.2 | 35.6 | 39 | 95.4 |  |  |  |  | 352 | P1_2-116 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | Facility: Radial
100487 | 18S | Approved | P1 | 6 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 193.8 | 143.8 | 206 | 94.1 |  |  |  |  | 396 | P1_2-160 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100488 | 18S | Approved | P1 | 6 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 231.7 | 99.8 | 243 | 95.3 |  |  |  |  | 411 | P1_2-175 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
100489 | 18S | Approved | P1 | 6 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.1 | 86.5 | 206 | 91.3 |  |  |  |  | 420 | P1_2-184 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100490 | 18S | Approved | P1 | 6 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 188.2 | 86.5 | 206 | 91.4 |  |  |  |  | 439 | P1_2-203 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100491 | 18S | Approved | P1 | 6 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 36.8 | 17 | 39 | 94.3 |  |  |  |  | 456 | P1_2-220 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100492 | 18S | Approved | P1 | 6 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 37.2 | 17 | 39 | 95.5 |  |  |  |  | 459 | P1_2-223 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! |  | Project Proposed | No violation: below Rate A | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100493 | 18S | Approved | P1 | 6 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.5 | 14.4 | 39 | 96.3 |  |  |  |  | 460 | P1_2-224 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100494 | 18S | Approved | P1 | 6 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40 | 17 | 39 | 102.5 |  |  |  |  | 460 | P1_2-224 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100495 | 18S | Approved | P1 | 6 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 261.1 | 176.1 | 287 | 91 |  |  |  |  | 539 | P1_2-303 | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-303_4PNEC BK!,4SABINE! |  | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
100496 | 18S | Approved | P1 | 6 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 265.1 | 167.1 | 288 | 92.1 |  |  |  |  | 540 | P1_2-304 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-304_4PNEC BK!,4SABINE! |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
100497 | 18S | Approved | P1 | 6 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30.6 | 23.8 | 33 | 92.7 |  |  |  |  | 699 | P1_2-463 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-463 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100498 | 18S | Approved | P1 | 6 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 334.2 | 331.8 | 360 | 92.8 |  |  |  |  | 719 | P1_2-483 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-483_6NELSON%,8NELSON% |  |  | Facility: GSU
100499 | 18S | Approved | P1 | 6 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30 | 23.8 | 33 | 90.9 |  |  |  |  | 736 | P1_2-500 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100500 | 18S | Approved | P1 | 6 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.8 | 177.6 | 225 | 92.4 |  |  |  |  | 780 | P1_2-544 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-544_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
100501 | 18S | Approved | P1 | 6 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 212.3 | 177.6 | 225 | 94.3 |  |  |  |  | 781 | P1_2-545 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
100502 | 18S | Approved | P1 | 6 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 203.8 | 169.1 | 225 | 90.6 |  |  |  |  | 781 | P1_2-545 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
100503 | 18S | Approved | P1 | 6 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 216.3 | 177.6 | 225 | 96.1 |  |  |  |  | 784 | P1_2-548 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% |  |  | No violation: below Rate A
100504 | 18S | Approved | P1 | 6 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 207.7 | 169.1 | 225 | 92.3 |  |  |  |  | 784 | P1_2-548 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% |  |  | No violation: below Rate A
100505 | 18S | Approved | P1 | 6 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 195.9 | 123.1 | 191 | 102.6 |  |  |  |  | 801 | P1_2-565 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100506 | 18S | Approved | P1 | 6 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 195.9 | 123.1 | 191 | 102.6 |  |  |  |  | 802 | P1_2-566 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100507 | 18S | Approved | P1 | 6 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 42.7 | 20 | 39 | 109.4 |  |  |  |  | 805 | P1_2-569 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100508 | 18S | Approved | P1 | 6 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 38.9 | 16.7 | 39 | 99.6 |  |  |  |  | 805 | P1_2-569 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100509 | 18S | Approved | P1 | 6 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 40.2 | 25.2 | 39 | 103.1 |  |  |  |  | 805 | P1_2-569 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100510 | 18S | Approved | P1 | 6 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.5 | 25.2 | 39 | 98.7 |  |  |  |  | 815 | P1_2-579 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-579 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100511 | 18S | Approved | P1 | 6 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 184.6 | 130.2 | 200 | 92.3 |  |  |  |  | 963 | P1_2-727 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727 |  |  | Model: does not represent split configuration
100512 | 18S | Approved | P1 | 6 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 181.9 | 130.2 | 200 | 91 |  |  |  |  | 964 | P1_2-728 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-728 |  |  | Model: does not represent split configuration
100513 | 18S | Approved | P1 | 6 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.8 | 159.8 | 200 | 90.4 |  |  |  |  | 995 | P1_2-759 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-759 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100514 | 18S | Approved | P1 | 6 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 96.4 | 46.2 | 100 | 96.4 |  |  |  |  | 996 | P1_2-760 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100515 | 18S | Approved | P1 | 6 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 95.1 | 45.6 | 100 | 95.1 |  |  |  |  | 996 | P1_2-760 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100516 | 18S | Approved | P1 | 6 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.5 | 159.8 | 200 | 90.2 |  |  |  |  | 1001 | P1_2-765 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100517 | 18S | Approved | P1 | 6 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 181.6 | 159.8 | 200 | 90.8 |  |  |  |  | 1004 | P1_2-768 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-768 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100518 | 18S | Approved | P1 | 6 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 290.4 | 168.3 | 300 | 96.8 |  |  |  |  | 1004 | P1_2-768 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-768 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100519 | 18S | Approved | P1 | 6 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 181.3 | 159.8 | 200 | 90.6 |  |  |  |  | 1005 | P1_2-769 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100520 | 18S | Approved | P1 | 6 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 291.2 | 170 | 300 | 97.1 |  |  |  |  | 1005 | P1_2-769 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100524 | 18S | Approved | P1 | 6 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 192.1 | 142.2 | 199 | 96.5 |  |  |  |  | 1101 | P1_2-865 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100525 | 18S | Approved | P1 | 6 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 217.5 | 136.6 | 229 | 95 |  |  |  |  | 1187 | P1_2-951 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! |  |  | No violation: below Rate A
100526 | 18S | Approved | P1 | 6 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 213.4 | 162.4 | 229 | 93.2 |  |  |  |  | 1188 | P1_2-952 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-952_39MILE%,3GRETNA! |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100527 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 1240 | P1_2-1004 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1004 |  |  | Facility: Radial
100528 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 178.7 | 193 | 93.7 |  |  |  |  | 1272 | P1_2-1036 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1036 |  |  | Facility: Radial
100529 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 1274 | P1_2-1038 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1038 |  |  | Facility: Radial
100530 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 1275 | P1_2-1039 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1039 |  |  | Facility: Radial
100531 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.1 | 178.7 | 193 | 93.3 |  |  |  |  | 1276 | P1_2-1040 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1040 |  |  | Facility: Radial
100532 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179.9 | 178.7 | 193 | 93.2 |  |  |  |  | 1280 | P1_2-1044 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1044 |  |  | Facility: Radial
100535 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176 | 178.7 | 193 | 91.2 |  |  |  |  | 1285 | P1_2-1049 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1049 |  |  | Facility: Radial
100536 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.7 | 178.7 | 193 | 93.7 |  |  |  |  | 1288 | P1_2-1052 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1052 |  |  | Facility: Radial
100537 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 175.7 | 178.7 | 193 | 91.1 |  |  |  |  | 1291 | P1_2-1055 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1055 |  |  | Facility: Radial
100538 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 177.2 | 178.7 | 193 | 91.8 |  |  |  |  | 1292 | P1_2-1056 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1056 |  |  | Facility: Radial
100539 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 178.7 | 193 | 93.4 |  |  |  |  | 1296 | P1_2-1060 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1060_6S.CANTON!,6PICKENS! |  |  | Facility: Radial
100540 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.5 | 178.7 | 193 | 91.5 |  |  |  |  | 1302 | P1_2-1066 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1066 |  |  | Facility: Radial
100541 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 177.2 | 178.7 | 193 | 91.8 |  |  |  |  | 1308 | P1_2-1072 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1072_3MONUMENT!,3E.JACKSON! |  |  | Facility: Radial
100542 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.2 |  |  |  |  | 1317 | P1_2-1081 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1081 |  |  | Facility: Radial
100543 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.6 | 178.7 | 193 | 93.6 |  |  |  |  | 1324 | P1_2-1088 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% |  |  | Facility: Radial
100544 | 18S | Approved | P1 | 6 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 543.7 | 323 | 561 | 96.9 |  |  |  |  | 1333 | P1_2-1097 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
100545 | 18S | Approved | P1 | 6 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 178.7 | 193 | 93.7 |  |  |  |  | 1335 | P1_2-1099 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1099 |  |  | Facility: Radial
100546 | 18S | Approved | P1 | 6 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.8 | 104.3 | 112 | 94.5 |  |  |  |  | 1351 | P1_2-1115 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1115_6ANDRUS%,3BAGBY! |  |  | Facility: Radial
100547 | 18S | Approved | P1 | 6 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 288.6 | 211 | 278 | 103.8 |  |  |  |  | 1370 | P1_2-1134 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
100548 | 18S | Approved | P1 | 6 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 211 | 278 | 107 |  |  |  |  | 1371 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale
100549 | 18S | Approved | P1 | 6 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 293.6 | 80.2 | 278 | 105.6 |  |  |  |  | 1375 | P1_2-1139 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
100550 | 18S | Approved | P1 | 6 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 304.9 | 88.5 | 250 | 121.9 |  |  |  |  | 1375 | P1_2-1139 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
100551 | 18S | Approved | P1 | 6 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.7 | 35.6 | 39 | 94.2 |  |  |  |  | 1411 | P1_2-1175 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1175 |  |  | Facility: Radial
100552 | 18S | Approved | P1 | 6 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 106.2 | 82.5 | 115 | 92.3 |  |  |  |  | 1411 | P1_2-1175 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100553 | 18S | Approved | P1 | 6 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.1 | 35.6 | 39 | 95.2 |  |  |  |  | 1414 | P1_2-1178 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1178_3WINNSBORO!,3SWARTZ! |  |  | Facility: Radial
100554 | 18S | Approved | P1 | 6 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 249.3 | 192.4 | 262 | 95.1 |  |  |  |  | 1449 | P1_2-1213 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1213 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100555 | 18S | Approved | P1 | 6 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 242 | 192.4 | 262 | 92.4 |  |  |  |  | 1450 | P1_2-1214 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100556 | 18S | Approved | P1 | 6 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 79.7 | 37 | 80 | 99.6 |  |  |  |  | 1450 | P1_2-1214 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% |  | Project Approved | No violation: below Rate A | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100557 | 18S | Approved | P1 | 6 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 103.3 | 104.3 | 112 | 92.2 |  |  |  |  | 1469 | P1_2-1233 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1233 |  |  | Facility: Radial
100558 | 18S | Approved | P1 | 6 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.6 | 104.3 | 112 | 94.3 |  |  |  |  | 1486 | P1_2-1250 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1250 |  |  | Facility: Radial
100559 | 18S | Approved | P1 | 6 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.6 | 104.3 | 112 | 94.3 |  |  |  |  | 1520 | P1_2-1284 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1284 |  |  | Facility: Radial
100560 | 18S | Approved | P1 | 6 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 243.8 | 178.9 | 266 | 91.6 |  |  |  |  | 1527 | P1_2-1291 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1291_3FORDYCE!,3WOODWARD-S! |  |  | No violation: below Rate A
100561 | 18S | Approved | P1 | 6 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 168.7 | 92 | 176 | 95.9 |  |  |  |  | 1569 | P1_2-1333 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Proposed | No violation: below Rate A | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
100562 | 18S | Approved | P1 | 6 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 167.7 | 91.1 | 176 | 95.3 |  |  |  |  | 1569 | P1_2-1333 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Proposed | No violation: below Rate A | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
100565 | 18S | Approved | P1 | 6 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 261.8 | 232.7 | 283 | 92.5 |  |  |  |  | 1622 | P1_2-1386 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1386 |  |  | No violation: below Rate A
100566 | 18S | Approved | P1 | 6 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 256.6 | 232.7 | 283 | 90.7 |  |  |  |  | 1653 | P1_2-1417 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1417_5QUITMAN!,5HAMLET% |  |  | No violation: below Rate A
100567 | 18S | Approved | P1 | 6 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 256.6 | 232.7 | 283 | 90.7 |  |  |  |  | 1654 | P1_2-1418 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1418_5QUITMAN!,5HILLTOP% |  |  | No violation: below Rate A
100571 | 18S | Approved | P1 | 6 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 103.5 | 59.1 | 106 | 97.6 |  |  |  |  | 1684 | P1_2-1448 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100572 | 18S | Approved | P1 | 6 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 265.8 | 232.7 | 283 | 93.9 |  |  |  |  | 1695 | P1_2-1460 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1460_3SRCY PRICE!,3HOLND BTM! |  |  | No violation: below Rate A
100573 | 18S | Approved | P1 | 6 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 135.8 | 82 | 148 | 91.8 |  |  |  |  | 1729 | P1_2-1496 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
100574 | 18S | Approved | P1 | 6 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 133.9 | 107.7 | 148 | 90.5 |  |  |  |  | 1736 | P1_2-1503 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% |  |  | No violation: below Rate A
100575 | 18S | Approved | P1 | 6 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 134.8 | 107.7 | 148 | 91.1 |  |  |  |  | 1754 | P1_2-1521 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1521 |  |  | No violation: below Rate A
100576 | 18S | Approved | P1 | 6 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 228.3 | 107.4 | 226 | 101 |  |  |  |  | 1796 | P1_2-1563 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
100577 | 18S | Approved | P1 | 6 | 500265 DTOWN 138 500420 HUNTER4 138 1 | LN | 134.8 | 66 | 148 | 91.1 |  |  |  |  | 1848 | P1_2-1615 | 500265 | 500420 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1615 |  |  | No violation: below Rate A
100578 | 18S | Approved | P1 | 6 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.2 | 177.6 | 225 | 90.7 |  |  |  |  | 1887 | P1_2-1654 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! |  |  | No violation: below Rate A
100579 | 18S | Approved | P1 | 6 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 649.6 | 118.8 | 700 | 92.8 |  |  |  |  | 1894 | P1_2-1661 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
100580 | 18S | Approved | P1 | 6 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 228.7 | 86.4 | 204 | 112.1 |  |  |  |  | 1894 | P1_2-1661 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7
100581 | 18S | Approved | P1 | 6 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 205.7 | 63.3 | 188 | 109.4 |  |  |  |  | 1894 | P1_2-1661 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7
100582 | 18S | Approved | P1 | 6 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | LN | 133.5 | 66.4 | 148 | 90.2 |  |  |  |  | 1896 | P1_2-1663 | 500735 | 500816 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1663 |  |  | No violation: below Rate A
100583 | 18W | Approved | P0 | 7 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 331.9 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100584 | 18W | Approved | P0 | 7 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.1 | 35.1 | 39 | 90 |  |  |  |  | 0 | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
100585 | 18W | Approved | P0 | 7 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 44.7 | 44.7 | 38 | 117.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100585 | 18W | Approved | P0 | 7 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 44.7 | 44.7 | 38 | 117.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100586 | 18W | Approved | P0 | 7 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 85.4 | 85.4 | 93 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100587 | 18W | Approved | P0 | 7 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 19.9 | 19.9 | 20 | 99.4 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
100588 | 18W | Approved | P0 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 335.4 | 335.4 | 360 | 93.2 |  |  |  |  | 0 | ** Base Case ** | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100589 | 18W | Approved | P0 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100590 | 18W | Approved | P0 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100591 | 18W | Approved | P0 | 7 | 500120 B.BRID 2 69.0 500620 NICKTAP2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500120 | 500620 | 1 |  | 69 | 69 | 502 | CLEC | 502 | CLEC | ** Base Case ** |  |  | No violation: below Rate A
100592 | 18W | Approved | P0 | 7 | 500620 NICKTAP2 69.0 502413 ELKS 2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500620 | 502413 | 1 |  | 69 | 69 | 502 | CLEC | 503 | LAFA | ** Base Case ** |  |  | No violation: below Rate A
100593 | 18W | Approved | P1 | 7 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 257.8 | 212.1 | 278 | 92.7 |  |  |  |  | 311 | 337095 3SHELBY MS+ 115 337096 3ROUNDAWAY+ 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337095 3SHELBY MS+ 115 337096 3ROUNDAWAY+ 115 1 |  | SPS: Clarksdale | No violation: below Rate A
100594 | 18W | Approved | P1 | 7 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 259.1 | 212.1 | 278 | 93.2 |  |  |  |  | 313 | 337096 3ROUNDAWAY+ 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337096 3ROUNDAWAY+ 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale | No violation: below Rate A
100595 | 18W | Approved | P1 | 7 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 302.2 | 212.1 | 278 | 108.7 |  |  |  |  | 314 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
100596 | 18W | Approved | P1 | 7 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.6 | 212.1 | 278 | 107.4 |  |  |  |  | 315 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
100597 | 18W | Approved | P1 | 7 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 303.9 | 92.8 | 278 | 109.3 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100598 | 18W | Approved | P1 | 7 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 303.2 | 88.1 | 250 | 121.3 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100599 | 18W | Approved | P1 | 7 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 179.8 | 128 | 199 | 90.3 |  |  |  |  | 390 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100600 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338 | 335.4 | 360 | 93.9 |  |  |  |  | 888 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | Facility: GSU
100601 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 888 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | Facility: GSU
100602 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 888 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | Facility: GSU
100603 | 18W | Approved | P1 | 7 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 67.2 | 36.6 | 70 | 96 |  |  |  |  | 922 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100604 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.7 | 335.4 | 360 | 93.5 |  |  |  |  | 990 | Unit:338143 1ISES U1 26.0 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:338143 1ISES U1 26.0 Id:1 |  |  | Facility: GSU
100605 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 337.4 | 335.4 | 360 | 93.7 |  |  |  |  | 991 | Unit:338146 1ISES U2 26.0 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:338146 1ISES U2 26.0 Id:1 |  |  | Facility: GSU
100606 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.1 | 335.4 | 360 | 92.8 |  |  |  |  | 1073 | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 |  |  | Facility: GSU
100607 | 18W | Approved | P1 | 7 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 67.4 | 36.6 | 70 | 96.3 |  |  |  |  | 1077 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
100608 | 18W | Approved | P1 | 7 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.3 | 133 | 206 | 91.4 |  |  |  |  | 1151 | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100609 | 18W | Approved | P1 | 7 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 119.4 | 59.9 | 120 | 99.5 |  |  |  |  | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100610 | 18W | Approved | P1 | 7 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 126.9 | 67.2 | 127 | 99.9 |  |  |  |  | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100611 | 18W | Approved | P1 | 7 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.4 |  |  |  |  | 1312 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334307 4BUNA! 138 334308 4JNE EVA 138 1 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
100612 | 18W | Approved | P1 | 7 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 123.5 | 52.7 | 120 | 102.9 |  |  |  |  | 1313 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
100613 | 18W | Approved | P1 | 7 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.9 | 331.9 | 360 | 92.5 |  |  |  |  | 1331 | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 |  |  | Facility: GSU
100614 | 18W | Approved | P1 | 7 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 65.8 | 21 | 72 | 91.4 |  |  |  |  | 1603 | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 |  |  | No violation: below Rate A
100615 | 18W | Approved | P1 | 7 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 67.6 | 21 | 72 | 93.9 |  |  |  |  | 1608 | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 |  |  | No violation: below Rate A
100616 | 18W | Approved | P1 | 7 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 431.2 | 314.6 | 470 | 91.7 |  |  |  |  | 1637 | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 |  | Reduce PPG Plant | No violation: below Rate A
100617 | 18W | Approved | P1 | 7 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 43 | 44.7 | 38 | 113.2 |  |  |  |  | 1659 | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 |  |  | Delta: No worse than P0
100618 | 18W | Approved | P1 | 7 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224.6 | 118.3 | 200 | 112.3 |  |  |  |  | 1674 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
100619 | 18W | Approved | P1 | 7 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224.6 | 118.3 | 200 | 112.3 |  |  |  |  | 1675 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
100620 | 18W | Approved | P1 | 7 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.8 |  |  |  |  | 1687 | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100621 | 18W | Approved | P1 | 7 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.1 | 171.5 | 225 | 90.7 |  |  |  |  | 1778 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100622 | 18W | Approved | P1 | 7 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211 | 171.5 | 225 | 93.8 |  |  |  |  | 1779 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100623 | 18W | Approved | P1 | 7 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 202.8 | 163.5 | 225 | 90.1 |  |  |  |  | 1779 | 335367 8RICHARD% 500 335368 8WELLS% 500 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335367 8RICHARD% 500 335368 8WELLS% 500 1 |  |  | No violation: below Rate A
100624 | 18W | Approved | P1 | 7 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.3 | 113.5 | 191 | 97.5 |  |  |  |  | 1786 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100625 | 18W | Approved | P1 | 7 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.6 | 113.5 | 191 | 97.7 |  |  |  |  | 1788 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100626 | 18W | Approved | P1 | 7 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 40.3 | 16.8 | 39 | 103.4 |  |  |  |  | 1792 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100627 | 18W | Approved | P1 | 7 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 36.9 | 13.6 | 39 | 94.6 |  |  |  |  | 1792 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100628 | 18W | Approved | P1 | 7 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 39.1 | 16.8 | 39 | 100.1 |  |  |  |  | 1799 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100629 | 18W | Approved | P1 | 7 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 35.5 | 13.6 | 39 | 91 |  |  |  |  | 1799 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100630 | 18W | Approved | P1 | 7 | 335792 2MARYDALE 69.0 335793 2FRANCIS! 69.0 1 | LN | 64 | 18.2 | 70 | 91.4 |  |  |  |  | 2024 | 335782 2PORT_HUD_A!69.0 335783 2SANDY_CREEK69.0 1 | 335792 | 335793 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335783 2SANDY_CREEK69.0 1 |  |  | No violation: below Rate A
100631 | 18W | Approved | P1 | 7 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 92.5 | 44.6 | 100 | 92.5 |  |  |  |  | 2027 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100632 | 18W | Approved | P1 | 7 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 91.3 | 44 | 100 | 91.3 |  |  |  |  | 2027 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100633 | 18W | Approved | P1 | 7 | 335792 2MARYDALE 69.0 335793 2FRANCIS! 69.0 1 | LN | 63.2 | 18.2 | 70 | 90.2 |  |  |  |  | 2028 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335792 | 335793 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | No violation: below Rate A
100634 | 18W | Approved | P1 | 7 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 18.3 | 19.9 | 20 | 91.7 |  |  |  |  | 2034 | 335788 2BRADY_HGHTS69.0 335789 2CLINTON 69.0 1 | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335788 2BRADY_HGHTS69.0 335789 2CLINTON 69.0 1 |  |  | Delta: No worse than P0
100635 | 18W | Approved | P1 | 7 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 20.9 | 19.9 | 20 | 104.6 |  |  |  |  | 2040 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | Delta: No worse than P0
100636 | 18W | Approved | P1 | 7 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 535 | 313.9 | 593 | 90.2 |  |  |  |  | 2050 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100637 | 18W | Approved | P1 | 7 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 117.7 | 71.6 | 115 | 102.4 |  |  |  |  | 2115 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100638 | 18W | Approved | P1 | 7 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 179.8 | 128 | 199 | 90.3 |  |  |  |  | 2134 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100639 | 18W | Approved | P1 | 7 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 207.2 | 148.3 | 229 | 90.5 |  |  |  |  | 2210 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100640 | 18W | Approved | P1 | 7 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.3 | 331.9 | 360 | 92.6 |  |  |  |  | 2422 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 |  |  | Facility: GSU
100641 | 18W | Approved | P1 | 7 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.3 | 113.5 | 191 | 97.5 |  |  |  |  | 2493 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100642 | 18W | Approved | P1 | 7 | 500510 MADISON6 230 500520 MANDEV 6 230 1 | LN | 415.6 | 249.6 | 449 | 92.6 |  |  |  |  | 2518 | 336462 6MICHO% 230 500360 FRONTST6 230 1 | 500510 | 500520 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | 336462 6MICHO% 230 500360 FRONTST6 230 1 |  |  | No violation: below Rate A
100643 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333.7 | 335.4 | 360 | 92.7 |  |  |  |  | 2538 | Unit:338388 1PLUM PT U1 23.0 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:338388 1PLUM PT U1 23.0 Id:1 |  |  | Facility: GSU
100644 | 18W | Approved | P1 | 7 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.6 | 331.9 | 360 | 92.7 |  |  |  |  | 2550 | 303028 8COTNWOOD1! 500 303030 8XFMRINT2 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 303028 8COTNWOOD1! 500 303030 8XFMRINT2 500 1 |  |  | Facility: GSU
100645 | 18W | Approved | P1 | 7 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646 | 101.8 | 700 | 92.3 |  |  |  |  | 2718 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100646 | 18W | Approved | P1 | 7 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 236.3 | 90.1 | 204 | 115.9 |  |  |  |  | 2718 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100647 | 18W | Approved | P1 | 7 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 213.3 | 66.9 | 233 | 91.6 |  |  |  |  | 2718 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
100648 | 18W | Approved | P1 | 7 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 150.6 | 113.6 | 150 | 100.4 |  |  |  |  | 2727 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1
100649 | 18W | Approved | P1 | 7 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 105.2 | 49 | 115 | 91.5 |  |  |  |  | 2727 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  |  | No violation: below Rate A
100650 | 18W | Approved | P1 | 7 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 140.6 | 113.6 | 150 | 93.7 |  |  |  |  | 2749 | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 |  |  | No violation: below Rate A
100651 | 18W | Approved | P1 | 7 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 140.6 | 113.6 | 150 | 93.7 |  |  |  |  | 2752 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | No violation: below Rate A
100652 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.3 | 335.4 | 360 | 92.9 |  |  |  |  | 3827 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 |  |  | Facility: GSU
100653 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 3829 | 3Wnd: OPEN B$0071 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0071 1 |  |  | Facility: GSU
100654 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338.6 | 335.4 | 360 | 94 |  |  |  |  | 3839 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 |  |  | Facility: GSU
100655 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 3839 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 |  |  | Facility: GSU
100656 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 3839 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 |  |  | Facility: GSU
100657 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333 | 335.4 | 360 | 92.5 |  |  |  |  | 3844 | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100658 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 333.2 | 334.8 | 360 | 92.6 |  |  |  |  | 3844 | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100659 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 333.2 | 334.8 | 360 | 92.6 |  |  |  |  | 3844 | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360025 8CORDOVA TN 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100660 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333.1 | 335.4 | 360 | 92.5 |  |  |  |  | 3850 | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 |  |  | Facility: GSU
100661 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 333.5 | 334.8 | 360 | 92.6 |  |  |  |  | 3850 | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 |  |  | Facility: GSU
100662 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 333.5 | 334.8 | 360 | 92.6 |  |  |  |  | 3850 | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360033 8UNION MS 500 360052 8BR FERRY NP 500 1 |  |  | Facility: GSU
100663 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.2 | 335.4 | 360 | 92.8 |  |  |  |  | 3851 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | Facility: GSU
100664 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.2 | 335.4 | 360 | 92.8 |  |  |  |  | 3869 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 |  |  | Facility: GSU
100665 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 332.9 | 335.4 | 360 | 92.5 |  |  |  |  | 3907 | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100666 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 333.3 | 334.8 | 360 | 92.6 |  |  |  |  | 3907 | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100667 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 333.3 | 334.8 | 360 | 92.6 |  |  |  |  | 3907 | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360541 8PLEASANT HL 500 360612 8BENTON MS 500 1 |  |  | Facility: GSU
100668 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338.4 | 335.4 | 360 | 94 |  |  |  |  | 3910 | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 |  |  | Facility: GSU
100669 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 3910 | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 |  |  | Facility: GSU
100670 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 3910 | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 |  |  | Facility: GSU
100671 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 337 | 334.8 | 360 | 93.6 |  |  |  |  | 3924 | 360612 8BENTON MS 500 360613 8MAGNOL CC1 500 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360612 8BENTON MS 500 360613 8MAGNOL CC1 500 1 |  |  | Facility: GSU
100672 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 337 | 334.8 | 360 | 93.6 |  |  |  |  | 3924 | 360612 8BENTON MS 500 360613 8MAGNOL CC1 500 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360612 8BENTON MS 500 360613 8MAGNOL CC1 500 1 |  |  | Facility: GSU
100673 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 345.3 | 335.4 | 360 | 95.9 |  |  |  |  | 3925 | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 |  |  | Facility: GSU
100674 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 337 | 334.8 | 360 | 93.6 |  |  |  |  | 3926 | 3Wnd: OPEN B$0204 1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0204 1 |  |  | Facility: GSU
100675 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 337 | 334.8 | 360 | 93.6 |  |  |  |  | 3926 | 3Wnd: OPEN B$0204 1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0204 1 |  |  | Facility: GSU
100676 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 337.4 | 335.4 | 360 | 93.7 |  |  |  |  | 3927 | 3Wnd: OPEN B$0014 2 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0014 2 |  |  | Facility: GSU
100677 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 337.4 | 334.8 | 360 | 93.7 |  |  |  |  | 3927 | 3Wnd: OPEN B$0014 2 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0014 2 |  |  | Facility: GSU
100678 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 337.4 | 335.4 | 360 | 93.7 |  |  |  |  | 3928 | 3Wnd: OPEN B$0199 3 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0199 3 |  |  | Facility: GSU
100679 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 337.4 | 334.8 | 360 | 93.7 |  |  |  |  | 3928 | 3Wnd: OPEN B$0199 3 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0199 3 |  |  | Facility: GSU
100680 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 3995 | Unit:364301 1LAG CRK CT116.5 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364301 1LAG CRK CT116.5 Id:1 |  |  | Facility: GSU
100681 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 3996 | Unit:364302 1LAG CRK CT216.5 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364302 1LAG CRK CT216.5 Id:1 |  |  | Facility: GSU
100682 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 4119 | Unit:364762 1MAGNOL T2 18.0 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364762 1MAGNOL T2 18.0 Id:1 |  |  | Facility: GSU
100683 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 4119 | Unit:364762 1MAGNOL T2 18.0 Id:1 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364762 1MAGNOL T2 18.0 Id:1 |  |  | Facility: GSU
100684 | 18W | Approved | P1 | 7 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 4120 | Unit:364763 1MAGNOL T3 18.0 Id:1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364763 1MAGNOL T3 18.0 Id:1 |  |  | Facility: GSU
100685 | 18W | Approved | P1 | 7 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 4120 | Unit:364763 1MAGNOL T3 18.0 Id:1 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | Unit:364763 1MAGNOL T3 18.0 Id:1 |  |  | Facility: GSU
100686 | 18W | Approved | P0 | 8 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 331.9 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100687 | 18W | Approved | P0 | 8 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.1 | 35.1 | 39 | 90 |  |  |  |  | 0 | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
100688 | 18W | Approved | P0 | 8 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 44.7 | 44.7 | 38 | 117.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100688 | 18W | Approved | P0 | 8 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 44.7 | 44.7 | 38 | 117.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100689 | 18W | Approved | P0 | 8 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 85.4 | 85.4 | 93 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100690 | 18W | Approved | P0 | 8 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 19.9 | 19.9 | 20 | 99.4 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
100691 | 18W | Approved | P0 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 335.4 | 335.4 | 360 | 93.2 |  |  |  |  | 0 | ** Base Case ** | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100692 | 18W | Approved | P0 | 8 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100693 | 18W | Approved | P0 | 8 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | Facility: GSU
100694 | 18W | Approved | P0 | 8 | 500120 B.BRID 2 69.0 500620 NICKTAP2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500120 | 500620 | 1 |  | 69 | 69 | 502 | CLEC | 502 | CLEC | ** Base Case ** |  |  | No violation: below Rate A
100695 | 18W | Approved | P0 | 8 | 500620 NICKTAP2 69.0 502413 ELKS 2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500620 | 502413 | 1 |  | 69 | 69 | 502 | CLEC | 503 | LAFA | ** Base Case ** |  |  | No violation: below Rate A
100696 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.7 | 335.4 | 360 | 93.5 |  |  |  |  | 134 | G-338143-1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | G-338143-1 |  |  | Facility: GSU
100697 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 337.4 | 335.4 | 360 | 93.7 |  |  |  |  | 135 | G-338146-1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | G-338146-1 |  |  | Facility: GSU
100698 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333.7 | 335.4 | 360 | 92.7 |  |  |  |  | 136 | G-338388-1 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | G-338388-1 |  |  | Facility: GSU
100699 | 18W | Approved | P1 | 8 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.3 | 331.9 | 360 | 92.6 |  |  |  |  | 320 | P1_2-101 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-101_8COTNWOOD2!,8HARTBRG% |  |  | Facility: GSU
100700 | 18W | Approved | P1 | 8 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.6 | 331.9 | 360 | 92.7 |  |  |  |  | 322 | P1_2-103 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-103 |  |  | Facility: GSU
100701 | 18W | Approved | P1 | 8 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.3 | 133 | 206 | 91.4 |  |  |  |  | 378 | P1_2-159 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100702 | 18W | Approved | P1 | 8 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 119.4 | 59.9 | 120 | 99.5 |  |  |  |  | 456 | P1_2-237 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100703 | 18W | Approved | P1 | 8 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 126.9 | 67.2 | 127 | 99.9 |  |  |  |  | 456 | P1_2-237 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100704 | 18W | Approved | P1 | 8 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.4 |  |  |  |  | 466 | P1_2-247 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
100705 | 18W | Approved | P1 | 8 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.9 | 331.9 | 360 | 92.5 |  |  |  |  | 482 | P1_2-263 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-263 |  |  | Facility: GSU
100706 | 18W | Approved | P1 | 8 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 431.2 | 314.6 | 470 | 91.7 |  |  |  |  | 677 | P1_2-458 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% |  | Reduce PPG Plant | No violation: below Rate A
100707 | 18W | Approved | P1 | 8 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.8 |  |  |  |  | 719 | P1_2-500 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100708 | 18W | Approved | P1 | 8 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.1 | 171.5 | 225 | 90.7 |  |  |  |  | 764 | P1_2-545 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
100709 | 18W | Approved | P1 | 8 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211 | 171.5 | 225 | 93.8 |  |  |  |  | 767 | P1_2-548 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% |  |  | No violation: below Rate A
100710 | 18W | Approved | P1 | 8 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 202.8 | 163.5 | 225 | 90.1 |  |  |  |  | 767 | P1_2-548 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% |  |  | No violation: below Rate A
100711 | 18W | Approved | P1 | 8 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.3 | 113.5 | 191 | 97.5 |  |  |  |  | 784 | P1_2-565 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100712 | 18W | Approved | P1 | 8 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.3 | 113.5 | 191 | 97.5 |  |  |  |  | 785 | P1_2-566 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% |  | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100713 | 18W | Approved | P1 | 8 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 40.3 | 16.8 | 39 | 103.4 |  |  |  |  | 788 | P1_2-569 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100714 | 18W | Approved | P1 | 8 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 36.9 | 13.6 | 39 | 94.6 |  |  |  |  | 788 | P1_2-569 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed | No violation: below Rate A | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100715 | 18W | Approved | P1 | 8 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 92.5 | 44.6 | 100 | 92.5 |  |  |  |  | 980 | P1_2-761 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100716 | 18W | Approved | P1 | 8 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 91.3 | 44 | 100 | 91.3 |  |  |  |  | 980 | P1_2-761 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100719 | 18W | Approved | P1 | 8 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 179.8 | 128 | 199 | 90.3 |  |  |  |  | 1085 | P1_2-866 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-866_6ADMSCRK%,8FRANKLIN% |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100720 | 18W | Approved | P1 | 8 | 500510 MADISON6 230 500520 MANDEV 6 230 1 | LN | 415.6 | 249.6 | 449 | 92.6 |  |  |  |  | 1200 | P1_2-981 | 500510 | 500520 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-981_6MICHO%,FRONTST6! |  |  | No violation: below Rate A
100721 | 18W | Approved | P1 | 8 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 258.9 | 212.1 | 278 | 93.1 |  |  |  |  | 1354 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale | No violation: below Rate A
100722 | 18W | Approved | P1 | 8 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 302.2 | 212.1 | 278 | 108.7 |  |  |  |  | 1356 | P1_2-1137 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! |  | SPS: Clarksdale
100723 | 18W | Approved | P1 | 8 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.6 | 212.1 | 278 | 107.4 |  |  |  |  | 1357 | P1_2-1138 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! |  | SPS: Clarksdale
100724 | 18W | Approved | P1 | 8 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 303.9 | 92.8 | 278 | 109.3 |  |  |  |  | 1361 | P1_2-1142 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
100725 | 18W | Approved | P1 | 8 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 303.2 | 88.1 | 250 | 121.3 |  |  |  |  | 1361 | P1_2-1142 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
100726 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.7 | 335.4 | 360 | 93.5 |  |  |  |  | 1708 | P1_2-1492 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1492_5ISES-1!,5ISES-2! |  |  | Facility: GSU
100727 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 337.4 | 335.4 | 360 | 93.7 |  |  |  |  | 1710 | P1_2-1494 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1494_8ISES% |  |  | Facility: GSU
100728 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338 | 335.4 | 360 | 93.9 |  |  |  |  | 1738 | P1_2-1522 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | Facility: GSU
100729 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 1738 | P1_2-1522 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | Facility: GSU
100730 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 335.9 | 334.8 | 360 | 93.3 |  |  |  |  | 1738 | P1_2-1522 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | Facility: GSU
100731 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333.7 | 335.4 | 360 | 92.7 |  |  |  |  | 1739 | P1_2-1523 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1523 |  |  | Facility: GSU
100732 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.1 | 335.4 | 360 | 92.8 |  |  |  |  | 1740 | P1_2-1524 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1524 |  |  | Facility: GSU
100733 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.3 | 335.4 | 360 | 92.9 |  |  |  |  | 1776 | P1_2-1560 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% |  |  | Facility: GSU
100734 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338.6 | 335.4 | 360 | 94 |  |  |  |  | 1783 | P1_2-1567 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! |  |  | Facility: GSU
100735 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 1783 | P1_2-1567 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! |  |  | Facility: GSU
100736 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 1783 | P1_2-1567 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! |  |  | Facility: GSU
100737 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 333 | 335.4 | 360 | 92.5 |  |  |  |  | 1788 | P1_2-1572 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1572 |  |  | Facility: GSU
100738 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 333.2 | 334.8 | 360 | 92.6 |  |  |  |  | 1788 | P1_2-1572 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1572 |  |  | Facility: GSU
100739 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 333.2 | 334.8 | 360 | 92.6 |  |  |  |  | 1788 | P1_2-1572 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1572 |  |  | Facility: GSU
100740 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 338.4 | 335.4 | 360 | 94 |  |  |  |  | 1801 | P1_2-1585 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! |  |  | Facility: GSU
100741 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 1801 | P1_2-1585 | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! |  |  | Facility: GSU
100742 | 18W | Approved | P1 | 8 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 336.1 | 334.8 | 360 | 93.4 |  |  |  |  | 1801 | P1_2-1585 | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! |  |  | Facility: GSU
100743 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 1802 | P1_2-1586 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1586 |  |  | Facility: GSU
100744 | 18W | Approved | P1 | 8 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 336.5 | 335.4 | 360 | 93.5 |  |  |  |  | 1803 | P1_2-1587 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1587 |  |  | Facility: GSU
100745 | 18W | Approved | P1 | 8 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646 | 101.8 | 700 | 92.3 |  |  |  |  | 1880 | P1_2-1664 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
100746 | 18W | Approved | P1 | 8 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 236.3 | 90.1 | 204 | 115.9 |  |  |  |  | 1880 | P1_2-1664 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7
100747 | 18W | Approved | P1 | 8 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 213.3 | 66.9 | 233 | 91.6 |  |  |  |  | 1880 | P1_2-1664 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
100748 | 18W | Approved | P1 | 8 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.7 | 17 | 159 | 92.2 |  |  |  |  | 1951 | P1_2-1735 | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! |  |  | No violation: below Rate A
100749 | 18W | Approved | P1 | 8 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.6 | 21 | 157 | 95.9 |  |  |  |  | 1951 | P1_2-1735 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! |  |  | No violation: below Rate A
100750 | 23S | Approved | P0 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 332 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
100751 | 23S | Approved | P1 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 332 | 360 | 92.5 |  |  |  |  | 1338 | 334320 8CYPRESS% 500 334325 8HARTBRG% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 334320 8CYPRESS% 500 334325 8HARTBRG% 500 1 |  |  | Facility: GSU
100752 | 23S | Approved | P1 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.4 | 332 | 360 | 92.6 |  |  |  |  | 1342 | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 334325 8HARTBRG% 500 337368 8MT_OLIVE% 500 1 |  |  | Facility: GSU
100753 | 23S | Approved | P1 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.4 | 332 | 360 | 92.6 |  |  |  |  | 1689 | 335192 8NELSON% 500 335367 8RICHARD% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 335192 8NELSON% 500 335367 8RICHARD% 500 1 |  |  | Facility: GSU
100754 | 23S | Approved | P1 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.8 | 332 | 360 | 92.7 |  |  |  |  | 2368 | Unit:334440 1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | Unit:334440 1G4SABIN! 24.0 Id:1 |  |  | Facility: GSU
100755 | 23S | Approved | P1 | 9 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 332 | 360 | 92.5 |  |  |  |  | 2441 | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 303021 8COTNWOOD2! 500 334325 8HARTBRG% 500 1 |  |  | Facility: GSU
100756 | 23S | Approved | P0 | 9 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.6 | 18.6 | 19 | 98 |  |  |  |  | 0 | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
100757 | 23S | Approved | P1 | 9 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 221 | 115.9 | 241 | 91.7 |  |  |  |  | 1797 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  |  | No violation: below Rate A
100758 | 23S | Approved | P1 | 9 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 221 | 115.9 | 241 | 91.7 |  |  |  |  | 2512 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  |  | No violation: below Rate A
100759 | 23S | Approved | P1 | 9 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | LN | 220 | 127.1 | 241 | 91.3 |  |  |  |  | 1799 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 303150 | 335387 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  |  | No violation: below Rate A
100760 | 23S | Approved | P1 | 9 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 103.7 | 61.9 | 115 | 90.2 |  |  |  |  | 2296 | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 |  |  | No violation: below Rate A
100761 | 23S | Approved | P1 | 9 | 334054 4WALKER 138 334055 4RIVTRIN% 138 1 | LN | 109 | 47.9 | 121 | 90.1 |  |  |  |  | 1112 | 334020 4BRYAN! 138 334021 4COLSTTA! 138 1 | 334054 | 334055 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334020 4BRYAN! 138 334021 4COLSTTA! 138 1 |  |  | No violation: below Rate A
100762 | 23S | Approved | P1 | 9 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.1 | 128.4 | 206 | 91.3 |  |  |  |  | 1162 | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334072 4LEWIS% 138 334086 4CANEYCREEK! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
100763 | 23S | Approved | P1 | 9 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 221.9 | 182.7 | 243 | 91.3 |  |  |  |  | 1196 | 3Wnd: OPEN B$1607 PORTER 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 3Wnd: OPEN B$1607 PORTER 1 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
100764 | 23S | Approved | P1 | 9 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 222 | 182.7 | 243 | 91.3 |  |  |  |  | 1239 | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
100765 | 23S | Approved | P1 | 9 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 221.8 | 182.7 | 243 | 91.3 |  |  |  |  | 1240 | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
100766 | 23S | Approved | P1 | 9 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 221.8 | 182.7 | 243 | 91.3 |  |  |  |  | 1241 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
100767 | 23S | Approved | P1 | 9 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 222.4 | 84.7 | 243 | 91.5 |  |  |  |  | 1185 | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334093 4OAKRIDG! 138 334100 4PORTER% 138 1 |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
100768 | 23S | Approved | P1 | 9 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.7 | 92.6 | 206 | 97.5 |  |  |  |  | 1196 | 3Wnd: OPEN B$1607 PORTER 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 3Wnd: OPEN B$1607 PORTER 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100769 | 23S | Approved | P1 | 9 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.8 | 92.6 | 206 | 97.5 |  |  |  |  | 1239 | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334200 6PORTER% 230 334202 6CHPTSR2 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100770 | 23S | Approved | P1 | 9 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.7 | 92.6 | 206 | 97.4 |  |  |  |  | 1240 | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334202 6CHPTSR2 230 334203 6CHPTSR1 230 2 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100771 | 23S | Approved | P1 | 9 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.7 | 92.6 | 206 | 97.4 |  |  |  |  | 1241 | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334203 6CHPTSR1 230 334204 6CHINA% 230 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
100772 | 23S | Approved | P1 | 9 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | LN | 35.3 | 11.4 | 39 | 90.6 |  |  |  |  | 1274 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334265 | 334266 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  |  | No violation: below Rate A
100773 | 23S | Approved | P1 | 9 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 35.8 | 11.8 | 39 | 91.9 |  |  |  |  | 1274 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  |  | No violation: below Rate A
100774 | 23S | Approved | P1 | 9 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 36 | 11.9 | 39 | 92.3 |  |  |  |  | 1274 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  |  | No violation: below Rate A
100775 | 23S | Approved | P1 | 9 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 36.7 | 15.8 | 39 | 94.1 |  |  |  |  | 1269 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100776 | 23S | Approved | P1 | 9 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.1 | 15.8 | 39 | 95.1 |  |  |  |  | 1272 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100777 | 23S | Approved | P1 | 9 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 38 | 15.8 | 39 | 97.4 |  |  |  |  | 1273 | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100778 | 23S | Approved | P1 | 9 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 40 | 15.8 | 39 | 102.5 |  |  |  |  | 1274 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed |  | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
100779 | 23S | Approved | P1 | 9 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39.2 | 18.6 | 39 | 100.6 |  |  |  |  | 1269 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100780 | 23S | Approved | P1 | 9 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39.7 | 18.6 | 39 | 101.7 |  |  |  |  | 1272 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100781 | 23S | Approved | P1 | 9 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.6 | 18.6 | 39 | 104.1 |  |  |  |  | 1273 | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334226 4BYUFARM 138 334228 4MEMORIL! 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100782 | 23S | Approved | P1 | 9 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 42.7 | 18.6 | 39 | 109.4 |  |  |  |  | 1274 | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 334228 4MEMORIL! 138 334412 4MID CO% 138 1 |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
100783 | 23S | Approved | P1 | 9 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 110 | 52.6 | 120 | 91.6 |  |  |  |  | 1324 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
100784 | 23S | Approved | P1 | 9 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 109.2 | 49.6 | 120 | 91 |  |  |  |  | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100785 | 23S | Approved | P1 | 9 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 115.4 | 55.7 | 127 | 90.9 |  |  |  |  | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
100786 | 23S | Approved | P1 | 9 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | LN | 124.2 | 86.3 | 134 | 92.7 |  |  |  |  | 1350 | 334332 4HLYSPG# 138 334333 4NEWTONB! 138 1 | 334316 | 334317 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334332 4HLYSPG# 138 334333 4NEWTONB! 138 1 |  |  | No violation: below Rate A
100787 | 23S | Approved | P1 | 9 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 279.6 | 179.5 | 287 | 97.4 |  |  |  |  | 1409 | 334414 4LINDE 138 334430 4SABINE! 138 1 | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334414 4LINDE 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
100788 | 23S | Approved | P1 | 9 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 271.4 | 171.4 | 288 | 94.2 |  |  |  |  | 1405 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
100789 | 23S | Approved | P1 | 9 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 66.3 | 20 | 72 | 92.1 |  |  |  |  | 1614 | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335030 2LINE-285_TP69.0 335035 2LINE-238_TP69.0 1 |  |  | No violation: below Rate A
100790 | 23S | Approved | P1 | 9 | 335014 2LINE-15_TP 69.0 335022 2CATALYST! 69.0 1 | LN | 68.1 | 20 | 72 | 94.6 |  |  |  |  | 1619 | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 | 335014 | 335022 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335035 2LINE-238_TP69.0 335045 2CARLYSS! 69.0 1 |  |  | No violation: below Rate A
100791 | 23S | Approved | P0 | 9 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 40 | 40 | 38 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
100791 | 23S | Approved | P0 | 9 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 40 | 40 | 38 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
100792 | 23S | Approved | P1 | 9 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 38.3 | 40 | 38 | 100.9 |  |  |  |  | 1670 | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335101 2DIXIE_SULFR69.0 335102 2CANAL_LA 69.0 1 |  |  | Delta: No worse than P0
100793 | 23S | Approved | P1 | 9 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 226.1 | 120.7 | 200 | 113 |  |  |  |  | 1686 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
100794 | 23S | Approved | P1 | 9 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 226.1 | 120.7 | 200 | 113 |  |  |  |  | 1685 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
100795 | 23S | Approved | P0 | 9 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30.8 | 30.8 | 33 | 93.3 |  |  |  |  | 0 | ** Base Case ** | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
100796 | 23S | Approved | P0 | 9 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 52.8 | 52.8 | 56 | 94.3 |  |  |  |  | 0 | ** Base Case ** | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
100797 | 23S | Approved | P1 | 9 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211.1 | 176.8 | 225 | 93.8 |  |  |  |  | 1789 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100798 | 23S | Approved | P1 | 9 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 209.5 | 176.8 | 225 | 93.1 |  |  |  |  | 2447 | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303130 4N_CROWLEY 138 335366 4RICHARD% 138 1 |  |  | No violation: below Rate A
100799 | 23S | Approved | P1 | 9 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.8 | 176.8 | 225 | 91 |  |  |  |  | 2448 | 303130 4N_CROWLEY 138 335379 4SCOTT_1! 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303130 4N_CROWLEY 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100800 | 23S | Approved | P1 | 9 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.3 | 176.8 | 225 | 91.2 |  |  |  |  | 2655 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 500230 COUGH 4 138 500720 PLAISAN4 138 1 |  |  | No violation: below Rate A
100801 | 23S | Approved | P1 | 9 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 202.5 | 168.2 | 225 | 90 |  |  |  |  | 1789 | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335366 4RICHARD% 138 335379 4SCOTT_1! 138 1 |  |  | No violation: below Rate A
100802 | 23S | Approved | P1 | 9 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 255.7 | 107.8 | 233 | 109.8 |  |  |  |  | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
100802 | 23S | Approved | P1 | 9 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 255.7 | 107.8 | 233 | 109.8 |  |  |  |  | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-015-HZ | 2022-06-01 | Meaux to Abbeville - Reconductor Line
100803 | 23S | Approved | P1 | 9 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 233.1 | 107.8 | 233 | 100.1 |  |  |  |  | 2456 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 |  | Project Horizon |  | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
100803 | 23S | Approved | P1 | 9 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 233.1 | 107.8 | 233 | 100.1 |  |  |  |  | 2456 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 |  | Project Horizon |  | 14-EGL-015-HZ | 2022-06-01 | Meaux to Abbeville - Reconductor Line
100804 | 23S | Approved | P1 | 9 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 227 | 144.3 | 191 | 118.8 |  |  |  |  | 1797 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100805 | 23S | Approved | P1 | 9 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 238 | 144.3 | 191 | 124.6 |  |  |  |  | 1799 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100806 | 23S | Approved | P1 | 9 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 207.9 | 144.3 | 191 | 108.9 |  |  |  |  | 2455 | 303150 4LEBLANC! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 303150 4LEBLANC! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100807 | 23S | Approved | P1 | 9 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 227 | 144.3 | 191 | 118.9 |  |  |  |  | 2512 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
100808 | 23S | Approved | P1 | 9 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 47 | 21 | 39 | 120.5 |  |  |  |  | 1803 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100809 | 23S | Approved | P1 | 9 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 47.8 | 21 | 39 | 122.6 |  |  |  |  | 1810 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100810 | 23S | Approved | P1 | 9 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 43.1 | 17.6 | 39 | 110.6 |  |  |  |  | 1803 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100811 | 23S | Approved | P1 | 9 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 43.9 | 17.6 | 39 | 112.6 |  |  |  |  | 1810 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
100812 | 23S | Approved | P1 | 9 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 42 | 17.7 | 39 | 107.7 |  |  |  |  | 1819 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100812 | 23S | Approved | P1 | 9 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | LN | 42 | 17.7 | 39 | 107.7 |  |  |  |  | 1819 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | 335408 | 335409 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100813 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 43.8 | 26.7 | 39 | 112.2 |  |  |  |  | 1803 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100814 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 41.6 | 26.7 | 39 | 106.7 |  |  |  |  | 1812 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100815 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 43.2 | 26.7 | 39 | 110.7 |  |  |  |  | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
100815 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 43.2 | 26.7 | 39 | 110.7 |  |  |  |  | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
100816 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.8 | 26.7 | 39 | 99.4 |  |  |  |  | 1825 | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100817 | 23S | Approved | P1 | 9 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 38.3 | 26.7 | 39 | 98.3 |  |  |  |  | 1826 | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 |  | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
100818 | 23S | Approved | P1 | 9 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | LN | 132.7 | 76.9 | 121 | 109.7 |  |  |  |  | 1983 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | 335699 | 335710 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100819 | 23S | Approved | P1 | 9 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 131.1 | 68.1 | 121 | 108.3 |  |  |  |  | 1987 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100820 | 23S | Approved | P1 | 9 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 129.4 | 68.1 | 121 | 106.9 |  |  |  |  | 1992 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100821 | 23S | Approved | P1 | 9 | 335711 2JONESCREEK!69.0 335712 2LOCKHART 69.0 1 | LN | 118.4 | 30.1 | 129 | 91.8 |  |  |  |  | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 | 335712 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100822 | 23S | Approved | P1 | 9 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | LN | 142.3 | 53.1 | 141 | 100.9 |  |  |  |  | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335712 | 335713 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
100823 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | LN | 131.3 | 63 | 141 | 93.1 |  |  |  |  | 1978 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | 335713 | 335718 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 |  |  | No violation: below Rate A
100824 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | TR | 186.6 | 134.2 | 200 | 93.3 |  |  |  |  | 1989 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | 335713 | 335771 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 2 |  |  | Model: does not represent split configuration
100825 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | TR | 193.7 | 134.2 | 200 | 96.9 |  |  |  |  | 1990 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | 335713 | 335771 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 3 |  |  | Model: does not represent split configuration
100826 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 181.8 | 128.2 | 200 | 90.9 |  |  |  |  | 1988 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 1 |  |  | Model: does not represent split configuration
100827 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 185.6 | 128.2 | 200 | 92.8 |  |  |  |  | 1990 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 3 |  |  | Model: does not represent split configuration
100828 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 199 | 140.7 | 200 | 99.5 |  |  |  |  | 1988 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 1 |  |  | Model: does not represent split configuration
100829 | 23S | Approved | P1 | 9 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 195.6 | 140.7 | 200 | 97.8 |  |  |  |  | 1989 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335771 6COLY% 230 2 |  |  | Model: does not represent split configuration
100830 | 23S | Approved | P1 | 9 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | LN | 129.6 | 61.3 | 136 | 95.3 |  |  |  |  | 1978 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | 335718 | 335719 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 |  |  | No violation: below Rate A
100831 | 23S | Approved | P0 | 9 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 109.4 | 109.4 | 93 | 117.6 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
100832 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.1 | 48.5 | 100 | 101.1 |  |  |  |  | 2037 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100833 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.4 | 167.4 | 200 | 90.2 |  |  |  |  | 2008 | 335742 2JAGUAR_T2! 69.0 335770 6JAGUAR% 230 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335742 2JAGUAR_T2! 69.0 335770 6JAGUAR% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100834 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 184.1 | 167.4 | 200 | 92 |  |  |  |  | 2025 | 335770 6JAGUAR% 230 335772 6ENJAY! 230 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335770 6JAGUAR% 230 335772 6ENJAY! 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100835 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 187.6 | 167.4 | 200 | 93.8 |  |  |  |  | 2029 | 335772 6ENJAY! 230 335825 6FANCY_PT% 230 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335772 6ENJAY! 230 335825 6FANCY_PT% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100836 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 189.7 | 167.4 | 200 | 94.8 |  |  |  |  | 2036 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100837 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 189.3 | 167.4 | 200 | 94.7 |  |  |  |  | 2051 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100838 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190.4 | 167.4 | 200 | 95.2 |  |  |  |  | 2053 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100839 | 23S | Approved | P1 | 9 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190 | 167.4 | 200 | 95 |  |  |  |  | 2054 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100840 | 23S | Approved | P0 | 9 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 20.3 | 20.3 | 20 | 101.5 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
100841 | 23S | Approved | P1 | 9 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 18.3 | 20.3 | 20 | 91.6 |  |  |  |  | 2044 | 335788 2BRADY_HGHTS69.0 335789 2CLINTON 69.0 1 | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335788 2BRADY_HGHTS69.0 335789 2CLINTON 69.0 1 |  |  | Delta: No worse than P0
100842 | 23S | Approved | P1 | 9 | 335792 2MARYDALE 69.0 335793 2FRANCIS! 69.0 1 | LN | 65.7 | 17.2 | 70 | 93.9 |  |  |  |  | 2034 | 335782 2PORT_HUD_A!69.0 335783 2SANDY_CREEK69.0 1 | 335792 | 335793 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335783 2SANDY_CREEK69.0 1 |  |  | No violation: below Rate A
100843 | 23S | Approved | P1 | 9 | 335792 2MARYDALE 69.0 335793 2FRANCIS! 69.0 1 | LN | 64.8 | 17.2 | 70 | 92.5 |  |  |  |  | 2038 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335792 | 335793 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | No violation: below Rate A
100844 | 23S | Approved | P1 | 9 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.8 | 47.9 | 100 | 99.8 |  |  |  |  | 2037 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100845 | 23S | Approved | P1 | 9 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 303.6 | 177.5 | 300 | 101.2 |  |  |  |  | 2054 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100846 | 23S | Approved | P1 | 9 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 302.7 | 175.7 | 300 | 100.9 |  |  |  |  | 2053 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
100847 | 23S | Approved | P1 | 9 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 590.5 | 346 | 593 | 99.6 |  |  |  |  | 2060 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100848 | 23S | Approved | P1 | 9 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | LN | 587 | 338.9 | 593 | 99 |  |  |  |  | 2059 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | 335815 | 335825 | 2 |  | 230 | 230 | 351 | EES | 351 | EES | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
100849 | 23S | Approved | P1 | 9 | 336007 6VACHRE! 230 336154 6WATFRD% 230 1 | LN | 420.8 | 310.1 | 459 | 91.7 |  |  |  |  | 2099 | 336042 6RACLND! 230 336154 6WATFRD% 230 1 | 336007 | 336154 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 336042 6RACLND! 230 336154 6WATFRD% 230 1 |  |  | No violation: below Rate A
100850 | 23S | Approved | P1 | 9 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 129.1 | 76.4 | 115 | 112.2 |  |  |  |  | 2125 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100851 | 23S | Approved | P1 | 9 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 76.4 | 115 | 91.7 |  |  |  |  | 2128 | 336084 3BARATA! 115 336280 39MILE% 115 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336084 3BARATA! 115 336280 39MILE% 115 1 |  | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
100852 | 23S | Approved | P1 | 9 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | LN | 104.3 | 56.4 | 115 | 90.7 |  |  |  |  | 2125 | 336081 3GMEADW! 115 336084 3BARATA! 115 1 | 336080 | 336081 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336081 3GMEADW! 115 336084 3BARATA! 115 1 |  |  | No violation: below Rate A
100853 | 23S | Approved | P1 | 9 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 231 | 165.5 | 229 | 100.9 |  |  |  |  | 2220 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  | Project Horizon |  | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100854 | 23S | Approved | P1 | 9 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 209 | 165.5 | 229 | 91.2 |  |  |  |  | 2223 | 336286 3HARVEY2 115 336287 3GRETNA! 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336286 3HARVEY2 115 336287 3GRETNA! 115 1 |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
100855 | 23S | Approved | P1 | 9 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 222.4 | 139.9 | 229 | 97.1 |  |  |  |  | 2219 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336284 3WSTWGO! 115 1 |  |  | No violation: below Rate A
100856 | 23S | Approved | P1 | 9 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 183.5 | 133.6 | 199 | 92.2 |  |  |  |  | 394 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100857 | 23S | Approved | P1 | 9 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 183.6 | 133.6 | 199 | 92.3 |  |  |  |  | 2144 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100858 | 23S | Approved | P1 | 9 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 184 | 111.8 | 199 | 92.5 |  |  |  |  | 52 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100859 | 23S | Approved | P1 | 9 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 190.4 | 111.8 | 199 | 95.7 |  |  |  |  | 53 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100860 | 23S | Approved | P1 | 9 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 210.2 | 137.3 | 231 | 91 |  |  |  |  | 52 | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336557 3CALIFORNIA 115 336558 3VAUGHN+ 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100861 | 23S | Approved | P1 | 9 | 336555 3S.BROOKHAVN 115 336559 3FRANKLIN! 115 1 | LN | 216.8 | 137.3 | 231 | 93.9 |  |  |  |  | 53 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336555 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
100862 | 23S | Approved | P1 | 9 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 215.7 | 124.4 | 239 | 90.2 |  |  |  |  | 92 | 336800 3BXTRWILSON% 115 336802 3SPEN.POTASH 115 1 | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336800 3BXTRWILSON% 115 336802 3SPEN.POTASH 115 1 |  | Project Proposed | No violation: below Rate A | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
100863 | 23S | Approved | P2 | 9 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 164.2 | 85.5 | 161 | 102 |  |  |  |  | 100 | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336804 3VICKSBURG! 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100864 | 23S | Approved | P1 | 9 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 151.9 | 85.5 | 161 | 94.4 |  |  |  |  | 201 | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336959 3HAINING RD 115 336962 3W.VICKSBURG 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
100865 | 23S | Approved | P0 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179 | 179 | 193 | 92.7 |  |  |  |  | 0 | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | Facility: Radial
100866 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.1 | 179 | 193 | 93.3 |  |  |  |  | 57 | 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 |  |  | Facility: Radial
100867 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.9 | 179 | 193 | 93.8 |  |  |  |  | 112 | 336830 8BXTRWILSON% 500 336839 8R.BRASWELL% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336830 8BXTRWILSON% 500 336839 8R.BRASWELL% 500 1 |  |  | Facility: Radial
100868 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 179 | 193 | 93.4 |  |  |  |  | 113 | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 1 |  |  | Facility: Radial
100869 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 179 | 193 | 93.4 |  |  |  |  | 114 | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 2 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336840 6R.BRASWELL% 230 2 |  |  | Facility: Radial
100870 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 179 | 193 | 93.4 |  |  |  |  | 115 | 336839 8R.BRASWELL% 500 336880 3R.BRASWELL% 115 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336839 8R.BRASWELL% 500 336880 3R.BRASWELL% 115 1 |  |  | Facility: Radial
100871 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.6 | 179 | 193 | 93.6 |  |  |  |  | 120 | 336840 6R.BRASWELL% 230 336856 6NORTHSIDE 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336840 6R.BRASWELL% 230 336856 6NORTHSIDE 230 1 |  |  | Facility: Radial
100872 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181 | 179 | 193 | 93.8 |  |  |  |  | 132 | 336848 6LAKEOVER% 230 336852 6HINDS-1 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336848 6LAKEOVER% 230 336852 6HINDS-1 230 1 |  |  | Facility: Radial
100873 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 175.9 | 179 | 193 | 91.1 |  |  |  |  | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  |  | Facility: Radial
100874 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.4 | 179 | 193 | 93.5 |  |  |  |  | 137 | 336855 6REX BROWN! 230 336856 6NORTHSIDE 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336855 6REX BROWN! 230 336856 6NORTHSIDE 230 1 |  |  | Facility: Radial
100875 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.3 | 179 | 193 | 91.4 |  |  |  |  | 140 | 336860 6CHARITY CH 230 336861 6HOY RD 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336860 6CHARITY CH 230 336861 6HOY RD 230 1 |  |  | Facility: Radial
100876 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.4 | 179 | 193 | 91.4 |  |  |  |  | 141 | 336861 6HOY RD 230 336862 6YANDELL RD! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336861 6HOY RD 230 336862 6YANDELL RD! 230 1 |  |  | Facility: Radial
100877 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.6 | 179 | 193 | 93.6 |  |  |  |  | 146 | 336864 6S.CANTON! 230 336866 6CANTON 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336864 6S.CANTON! 230 336866 6CANTON 230 1 |  |  | Facility: Radial
100878 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181.7 | 179 | 193 | 94.2 |  |  |  |  | 147 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336866 6CANTON 230 337015 6PICKENS! 230 1 |  |  | Facility: Radial
100879 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 179 | 193 | 93.4 |  |  |  |  | 192 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 |  |  | Facility: Radial
100880 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 179 | 193 | 93.7 |  |  |  |  | 200 | 336945 8LAKEOVER% 500 337009 8MCADAMS% 500 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 336945 8LAKEOVER% 500 337009 8MCADAMS% 500 1 |  |  | Facility: Radial
100881 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181.2 | 179 | 193 | 93.9 |  |  |  |  | 235 | 337000 6MCADAMS% 230 337015 6PICKENS! 230 1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337000 6MCADAMS% 230 337015 6PICKENS! 230 1 |  |  | Facility: Radial
100882 | 23S | Approved | P1 | 9 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.4 | 179 | 193 | 93.5 |  |  |  |  | 370 | Unit:336853 1HINDS G1 18.0 Id:1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | Unit:336853 1HINDS G1 18.0 Id:1 |  |  | Facility: Radial
100883 | 23S | Approved | P1 | 9 | 336890 3S.JACKSON! 115 336911 3E.JACKSON! 115 1 | LN | 145.5 | 71.3 | 161 | 90.4 |  |  |  |  | 174 | 336906 3MONUMENT! 115 336908 3FONDREN 115 1 | 336890 | 336911 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336906 3MONUMENT! 115 336908 3FONDREN 115 1 |  | None | No violation: below Rate A
100884 | 23S | Approved | P1 | 9 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 557.6 | 331.2 | 561 | 99.4 |  |  |  |  | 232 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
100885 | 23S | Approved | P2 | 9 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 109.3 | 44.4 | 108 | 101.2 |  |  |  |  | 207 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
100886 | 23S | Approved | P1 | 9 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 100 | 44.4 | 108 | 92.6 |  |  |  |  | 208 | 336965 3S.REDWOOD+ 115 336966 3REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336965 3S.REDWOOD+ 115 336966 3REDWOOD+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
100887 | 23S | Approved | P1 | 9 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 292.3 | 81.3 | 278 | 105.2 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100888 | 23S | Approved | P1 | 9 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305 | 91.1 | 250 | 122 |  |  |  |  | 317 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
100889 | 23S | Approved | P1 | 9 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 287.2 | 208.6 | 278 | 103.3 |  |  |  |  | 314 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
100890 | 23S | Approved | P1 | 9 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 208.6 | 278 | 107 |  |  |  |  | 315 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
100891 | 23S | Approved | P2 | 9 | 337126 3BATESVILLE! 115 337135 3SARDIS 115 1 | LN | 129.4 | 36.7 | 136 | 95.1 |  |  |  |  | 339 | 337138 3HERNANDO 115 337139 3GETWELL! 115 1 | 337126 | 337135 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337138 3HERNANDO 115 337139 3GETWELL! 115 1 |  |  | No violation: below Rate A
100892 | 23S | Approved | P1 | 9 | 337162 6FREEPORT% 230 337163 6TWINKLTOWN! 230 1 | LN | 421.5 | 169.9 | 462 | 91.2 |  |  |  |  | 361 | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 | 337162 | 337163 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 |  | None | No violation: below Rate A
100893 | 23S | Approved | P1 | 9 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 227.6 | 100.4 | 226 | 100.7 |  |  |  |  | 3969 | 3Wnd: OPEN B$0054 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0054 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
100894 | 23S | Approved | P0 | 9 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.7 | 37.7 | 39 | 96.7 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
100895 | 23S | Approved | P1 | 9 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38.7 | 37.7 | 39 | 99.3 |  |  |  |  | 29 | 336529 3MEADVILLE 115 336559 3FRANKLIN! 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 336529 3MEADVILLE 115 336559 3FRANKLIN! 115 1 |  |  | Facility: Radial
100896 | 23S | Approved | P1 | 9 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38.8 | 37.7 | 39 | 99.5 |  |  |  |  | 90 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 |  |  | Facility: Radial
100897 | 23S | Approved | P1 | 9 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.6 | 37.7 | 39 | 94 |  |  |  |  | 2269 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
100898 | 23S | Approved | P1 | 9 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38.9 | 37.7 | 39 | 99.7 |  |  |  |  | 2276 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 |  |  | Facility: Radial
100899 | 23S | Approved | P1 | 9 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 103.6 | 88.8 | 115 | 90.1 |  |  |  |  | 88 | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100900 | 23S | Approved | P1 | 9 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 109.4 | 88.8 | 115 | 95.1 |  |  |  |  | 90 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100901 | 23S | Approved | P1 | 9 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 113.2 | 88.8 | 115 | 98.4 |  |  |  |  | 2272 | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337320 3PLANTATION! 115 337322 3MURRY_LA 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
100902 | 23S | Approved | P1 | 9 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 1 | LN | 83 | 19.3 | 80 | 103.8 |  |  |  |  | 2555 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 | 337371 | 337372 | 1 |  | 115 | 115 | 351 | EES | 338 | DERS | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 |  | Project Horizon |  | 13-ELL-005-HZ | 2020-06-01 | Vienna to Ruston Frazier Road 115 kV Line 173: Upgrade metering CTs at Ruston
100903 | 23S | Approved | P1 | 9 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 239.5 | 200.1 | 262 | 91.4 |  |  |  |  | 2308 | 337382 3DREW_LA 115 337383 3CHENIERE 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337382 3DREW_LA 115 337383 3CHENIERE 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100904 | 23S | Approved | P1 | 9 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 250.2 | 200.1 | 262 | 95.5 |  |  |  |  | 2309 | 337382 3DREW_LA 115 337414 3STERL2% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337382 3DREW_LA 115 337414 3STERL2% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100905 | 23S | Approved | P1 | 9 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 258.3 | 200.1 | 262 | 98.6 |  |  |  |  | 2317 | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337387 3SELMAN_FLD! 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100906 | 23S | Approved | P1 | 9 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 252 | 200.1 | 262 | 96.2 |  |  |  |  | 2320 | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100907 | 23S | Approved | P1 | 9 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 254.5 | 200.1 | 262 | 97.1 |  |  |  |  | 2323 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
100908 | 23S | Approved | P1 | 9 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.5 | 36 | 80 | 101.8 |  |  |  |  | 2320 | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337390 3SWARTZ! 115 337391 3WALNUT_GR_2 115 1 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100909 | 23S | Approved | P1 | 9 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83.6 | 36 | 80 | 104.6 |  |  |  |  | 2323 | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 337391 3WALNUT_GR_2 115 337415 3STERLING% 115 1 |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
100910 | 23S | Approved | P0 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 109.8 | 109.8 | 112 | 98 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100911 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.8 | 112 | 99.2 |  |  |  |  | 377 | Unit:337041 1ANDRUS U1 24.0 Id:1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | Unit:337041 1ANDRUS U1 24.0 Id:1 |  |  | Facility: Radial
100912 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.8 | 112 | 99.7 |  |  |  |  | 403 | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 |  |  | Facility: Radial
100913 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111 | 109.8 | 112 | 99.1 |  |  |  |  | 449 | 337539 3EL DORADO! 115 337560 3ELD QUINN 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337539 3EL DORADO! 115 337560 3ELD QUINN 115 1 |  |  | Facility: Radial
100914 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.8 | 109.8 | 112 | 98.9 |  |  |  |  | 450 | 337539 3EL DORADO! 115 337561 8EL DORADO% 500 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337539 3EL DORADO! 115 337561 8EL DORADO% 500 1 |  |  | Facility: Radial
100915 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.9 | 109.8 | 112 | 99 |  |  |  |  | 471 | 337560 3ELD QUINN 115 337572 3HILO 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337560 3ELD QUINN 115 337572 3HILO 115 1 |  |  | Facility: Radial
100916 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.9 | 109.8 | 112 | 99 |  |  |  |  | 474 | 337572 3HILO 115 337573 3HERMITAGE 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337572 3HILO 115 337573 3HERMITAGE 115 1 |  |  | Facility: Radial
100917 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.9 | 109.8 | 112 | 99 |  |  |  |  | 479 | 337577 3WILMAR 115 337578 3MONTCELO.S 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337577 3WILMAR 115 337578 3MONTCELO.S 115 1 |  |  | Facility: Radial
100918 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.8 | 109.8 | 112 | 98.9 |  |  |  |  | 484 | 337581 3CROSSETT.N! 115 337583 3CROSSETT.S 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337583 3CROSSETT.S 115 1 |  |  | Facility: Radial
100919 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.8 | 112 | 99.2 |  |  |  |  | 485 | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 |  |  | Facility: Radial
100920 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.8 | 109.8 | 112 | 99.8 |  |  |  |  | 488 | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100921 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.4 | 109.8 | 112 | 99.5 |  |  |  |  | 489 | 337590 3HAMBURG 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337590 3HAMBURG 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100922 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 112.7 | 109.8 | 112 | 100.7 |  |  |  |  | 490 | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100923 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.5 | 109.8 | 112 | 99.5 |  |  |  |  | 491 | 337591 3MONTROSE 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338644 3MIST# 115 1 |  |  | Facility: Radial
100924 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.8 | 112 | 99.7 |  |  |  |  | 492 | 337592 3BAGBY! 115 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 337594 6BAGBY 230 1 |  |  | Facility: Radial
100925 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 112.9 | 109.8 | 112 | 100.8 |  |  |  |  | 495 | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
100926 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.8 | 109.8 | 112 | 99.8 |  |  |  |  | 520 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  |  | Facility: Radial
100927 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.9 | 109.8 | 112 | 99 |  |  |  |  | 958 | 338657 3GLENDALE# 115 338660 3PINEBERGEN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338657 3GLENDALE# 115 338660 3PINEBERGEN# 115 1 |  |  | Facility: Radial
100928 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.9 | 109.8 | 112 | 99.9 |  |  |  |  | 1033 | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
100929 | 23S | Approved | P1 | 9 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.4 | 109.8 | 112 | 99.5 |  |  |  |  | 1036 | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 |  |  | Facility: Radial
100930 | 23S | Approved | P1 | 9 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 219.3 | 159.1 | 239 | 91.8 |  |  |  |  | 546 | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100931 | 23S | Approved | P1 | 9 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 227.3 | 159.1 | 239 | 95.1 |  |  |  |  | 547 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100932 | 23S | Approved | P1 | 9 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 231.3 | 159.1 | 239 | 96.8 |  |  |  |  | 548 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100933 | 23S | Approved | P1 | 9 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 112.2 | 50.5 | 106 | 105.8 |  |  |  |  | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100934 | 23S | Approved | P1 | 9 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 243.2 | 179.1 | 266 | 91.4 |  |  |  |  | 518 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 |  |  | No violation: below Rate A
100935 | 23S | Approved | P1 | 9 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 245.9 | 179.1 | 266 | 92.4 |  |  |  |  | 549 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 |  |  | No violation: below Rate A
100936 | 23S | Approved | P1 | 9 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 234.1 | 165.8 | 253 | 92.5 |  |  |  |  | 547 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100937 | 23S | Approved | P1 | 9 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 238.1 | 165.8 | 253 | 94.1 |  |  |  |  | 548 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
100938 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 220.7 | 194.1 | 239 | 92.3 |  |  |  |  | 542 | 337642 3SHERIDAN 115 337745 3POYEN 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337642 3SHERIDAN 115 337745 3POYEN 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100939 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 215.3 | 194.1 | 239 | 90.1 |  |  |  |  | 579 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100940 | 23S | Approved | P2 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242.4 | 194.1 | 239 | 101.4 |  |  |  |  | 583 | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100941 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 273.2 | 194.1 | 239 | 114.3 |  |  |  |  | 584 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100942 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242 | 194.1 | 239 | 101.3 |  |  |  |  | 588 | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 |  | Project Approved | Contingency: invalid, no breakers | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100943 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242 | 194.1 | 239 | 101.3 |  |  |  |  | 589 | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | Contingency: invalid, no breakers | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100944 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 236.6 | 194.1 | 239 | 99 |  |  |  |  | 591 | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100945 | 23S | Approved | P2 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 239 | 194.1 | 239 | 100 |  |  |  |  | 610 | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100946 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 235.9 | 194.1 | 239 | 98.7 |  |  |  |  | 611 | 337740 3HS EHV-E! 115 337742 3MALVERN.N+ 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337742 3MALVERN.N+ 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100947 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 237.3 | 194.1 | 239 | 99.3 |  |  |  |  | 613 | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 |  | Project Approved | Contingency: invalid, no breakers | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100948 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 229.4 | 194.1 | 239 | 96 |  |  |  |  | 615 | 337742 3MALVERN.N+ 115 337744 3GIFFORD 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337742 3MALVERN.N+ 115 337744 3GIFFORD 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100949 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 223.7 | 194.1 | 239 | 93.6 |  |  |  |  | 616 | 337744 3GIFFORD 115 337745 3POYEN 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337744 3GIFFORD 115 337745 3POYEN 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100950 | 23S | Approved | P2 | 9 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 231.1 | 194.1 | 239 | 96.7 |  |  |  |  | 629 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100951 | 23S | Approved | P1 | 9 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 187.2 | 99 | 176 | 106.3 |  |  |  |  | 584 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
100952 | 23S | Approved | P0 | 9 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 547.4 | 547.4 | 598 | 91.5 |  |  |  |  | 0 | ** Base Case ** | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
100953 | 23S | Approved | P1 | 9 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.4 | 547.4 | 598 | 91.4 |  |  |  |  | 579 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 |  |  | Facility: Radial
100954 | 23S | Approved | P1 | 9 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.3 | 547.4 | 598 | 91.4 |  |  |  |  | 612 | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337753 8HS EHV% 500 1 |  |  | Facility: Radial
100955 | 23S | Approved | P2 | 9 | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | LN | 204.8 | 139.2 | 201 | 101.9 |  |  |  |  | 603 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337686 | 337695 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100956 | 23S | Approved | P1 | 9 | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 2 | LN | 240.5 | 132.9 | 266 | 90.4 |  |  |  |  | 585 | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 1 | 337686 | 337740 | 2 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
100957 | 23S | Approved | P2 | 9 | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | LN | 203.6 | 138 | 201 | 101.3 |  |  |  |  | 603 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337695 | 337697 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100958 | 23S | Approved | P2 | 9 | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | LN | 203.6 | 138 | 201 | 101.3 |  |  |  |  | 603 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337697 | 337706 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100959 | 23S | Approved | P2 | 9 | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | LN | 187.4 | 122.2 | 201 | 93.2 |  |  |  |  | 603 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337705 | 337706 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | No violation: below Rate A | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100960 | 23S | Approved | P2 | 9 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | LN | 165.1 | 64.5 | 159 | 103.8 |  |  |  |  | 603 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | 337710 | 337713 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337717 3HS.S 115 337718 3CARPENTER! 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100961 | 23S | Approved | P2 | 9 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 162.9 | 100.7 | 159 | 102.5 |  |  |  |  | 583 | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100962 | 23S | Approved | P1 | 9 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 162.4 | 100.7 | 159 | 102.1 |  |  |  |  | 588 | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 |  | Project Approved | Contingency: invalid, no breakers | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100963 | 23S | Approved | P1 | 9 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 162.4 | 100.7 | 159 | 102.1 |  |  |  |  | 589 | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | Contingency: invalid, no breakers | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100964 | 23S | Approved | P2 | 9 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 155.1 | 100.7 | 159 | 97.6 |  |  |  |  | 591 | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100965 | 23S | Approved | P2 | 9 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 163.5 | 100.7 | 159 | 102.8 |  |  |  |  | 598 | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337710 3BLAKELY! 115 337713 3MT PINE.S 115 1 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
100966 | 23S | Approved | P1 | 9 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 175.2 | 87.1 | 176 | 99.6 |  |  |  |  | 584 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
100967 | 23S | Approved | P1 | 9 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 186.2 | 98.1 | 176 | 105.8 |  |  |  |  | 584 | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337718 3CARPENTER! 115 1 |  | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
100968 | 23S | Approved | P2 | 9 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 181.7 | 93.2 | 159 | 114.3 |  |  |  |  | 610 | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337740 3HS EHV-E! 115 337741 3BUTTERFIELD 115 1 |  | Project Horizon |  | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100969 | 23S | Approved | P1 | 9 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 177.7 | 93.2 | 159 | 111.7 |  |  |  |  | 613 | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337741 3BUTTERFIELD 115 337800 3HASKELL 115 1 |  | Project Horizon | Contingency: invalid, no breakers | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100970 | 23S | Approved | P2 | 9 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 163.6 | 93.2 | 159 | 102.9 |  |  |  |  | 629 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 |  | Project Horizon |  | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100971 | 23S | Approved | P1 | 9 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 158.4 | 93.2 | 159 | 99.6 |  |  |  |  | 630 | 337801 3WOODLAWN% 115 337802 3BAUXITE 115 1 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337801 3WOODLAWN% 115 337802 3BAUXITE 115 1 |  | Project Horizon | No violation: below Rate A | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
100972 | 23S | Approved | P1 | 9 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | TR | 422.9 | 297.1 | 448 | 94.4 |  |  |  |  | 633 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | 337799 | 337808 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100973 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 163.4 | 127.4 | 159 | 102.8 |  |  |  |  | 544 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100974 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 146.4 | 127.4 | 159 | 92.1 |  |  |  |  | 545 | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337643 8SHERIDAN% 500 337808 8MABELVALE% 500 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100975 | 23S | Approved | P2 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 145.6 | 127.4 | 159 | 91.6 |  |  |  |  | 583 | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337695 3TIGRE BAY 115 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100976 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 145.5 | 127.4 | 159 | 91.5 |  |  |  |  | 588 | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337695 3TIGRE BAY 115 337697 3PANTHER 115 1 |  | Project Approved | Contingency: invalid, no breakers | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100977 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 145.5 | 127.4 | 159 | 91.5 |  |  |  |  | 589 | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337697 3PANTHER 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | Contingency: invalid, no breakers | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100978 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 143.3 | 127.4 | 159 | 90.2 |  |  |  |  | 591 | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337705 3CHEETAH% 115 337706 3FOUNTAIN LK 115 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100979 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 150.6 | 127.4 | 159 | 94.7 |  |  |  |  | 594 | 337705 3CHEETAH% 115 338739 3ALENTEJO# 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337705 3CHEETAH% 115 338739 3ALENTEJO# 115 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100980 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 163.4 | 127.4 | 159 | 102.8 |  |  |  |  | 621 | 337753 8HS EHV% 500 337763 8MAGNETCOVE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337753 8HS EHV% 500 337763 8MAGNETCOVE% 500 1 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100981 | 23S | Approved | P2 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 174.8 | 127.4 | 159 | 109.9 |  |  |  |  | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100982 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 150.5 | 127.4 | 159 | 94.6 |  |  |  |  | 626 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100983 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 147.8 | 127.4 | 159 | 93 |  |  |  |  | 632 | 337803 3BRYANT 115 338757 3BRYANT.S# 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337803 3BRYANT 115 338757 3BRYANT.S# 115 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100984 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 150.2 | 127.4 | 159 | 94.5 |  |  |  |  | 633 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100985 | 23S | Approved | P1 | 9 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 146.8 | 127.4 | 159 | 92.3 |  |  |  |  | 965 | 338739 3ALENTEJO# 115 338740 3HS VILGE.E# 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338739 3ALENTEJO# 115 338740 3HS VILGE.E# 115 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
100986 | 23S | Approved | P2 | 9 | 337801 3WOODLAWN% 115 337802 3BAUXITE 115 1 | LN | 169.3 | 66.3 | 159 | 106.5 |  |  |  |  | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337801 | 337802 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 14-EAI-016-HZ | 2022-06-01 | Woodlawn to Bauxite 115 kV line - Upgrade line
100987 | 23S | Approved | P1 | 9 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 422.1 | 296.1 | 448 | 94.2 |  |  |  |  | 626 | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337808 8MABELVALE% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
100988 | 23S | Approved | P1 | 9 | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 | LN | 270.7 | 196.9 | 298 | 90.8 |  |  |  |  | 627 | 337799 3MABLVALE-W! 115 337831 3LAWSON RD 115 1 | 337818 | 337821 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337831 3LAWSON RD 115 1 |  |  | No violation: below Rate A
100989 | 23S | Approved | P1 | 9 | 337842 3GAINES% 115 338485 3NLR W.GATE 115 1 | LN | 149 | 74 | 159 | 93.7 |  |  |  |  | 647 | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 | 337842 | 338485 | 1 |  | 115 | 115 | 327 | EES-EAI | 339 | NLR | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 |  |  | No violation: below Rate A
100990 | 23S | Approved | P1 | 9 | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | TR | 585.3 | 413.4 | 600 | 97.5 |  |  |  |  | 694 | 3Wnd: OPEN B$0459 ANO 1 | 337922 | 337923 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | 3Wnd: OPEN B$0459 ANO 1 |  |  | No violation: below Rate A
100991 | 23S | Approved | P1 | 9 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 108.3 | 47.4 | 106 | 102.1 |  |  |  |  | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100992 | 23S | Approved | P1 | 9 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 102.4 | 43.6 | 106 | 96.6 |  |  |  |  | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100993 | 23S | Approved | P1 | 9 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 99.8 | 42.6 | 106 | 94.1 |  |  |  |  | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100994 | 23S | Approved | P1 | 9 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 99.4 | 61.6 | 106 | 93.8 |  |  |  |  | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100995 | 23S | Approved | P1 | 9 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 107.2 | 61.6 | 106 | 101.2 |  |  |  |  | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100996 | 23S | Approved | P1 | 9 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | LN | 97.2 | 51.8 | 106 | 91.7 |  |  |  |  | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337972 | 337973 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100997 | 23S | Approved | P1 | 9 | 337980 3ELAINE 115 337981 3MARVELL 115 1 | LN | 109.3 | 8.5 | 120 | 91.1 |  |  |  |  | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337980 | 337981 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100998 | 23S | Approved | P1 | 9 | 337981 3MARVELL 115 337982 3BARTON 115 1 | LN | 116.4 | 15.2 | 120 | 97 |  |  |  |  | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337981 | 337982 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
100999 | 23S | Approved | P1 | 9 | 337986 3RITCHIE! 115 337998 6RITCHIE-1! 230 1 | TR | 107.2 | 51.8 | 112 | 95.7 |  |  |  |  | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337986 | 337998 | 1 |  | 230 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101000 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 250.1 | 206.2 | 266 | 94 |  |  |  |  | 784 | 338010 3SRCY PRICE! 115 338045 5SRCY PRICE! 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338010 3SRCY PRICE! 115 338045 5SRCY PRICE! 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101001 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 240.3 | 206.2 | 266 | 90.3 |  |  |  |  | 811 | 338045 5SRCY PRICE! 161 338048 5BALD KNOB 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338045 5SRCY PRICE! 161 338048 5BALD KNOB 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101002 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 251.6 | 206.2 | 266 | 94.6 |  |  |  |  | 815 | 338048 5BALD KNOB 161 338049 5T.E.P/S-6 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338048 5BALD KNOB 161 338049 5T.E.P/S-6 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101003 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 253.6 | 206.2 | 266 | 95.3 |  |  |  |  | 817 | 338049 5T.E.P/S-6 161 338759 5COFFEEVLE# 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338049 5T.E.P/S-6 161 338759 5COFFEEVLE# 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101004 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 241.7 | 206.2 | 266 | 90.9 |  |  |  |  | 853 | 338142 5ISES-1! 161 338147 5NEWARK AR 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338142 5ISES-1! 161 338147 5NEWARK AR 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101005 | 23S | Approved | P1 | 9 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 254.8 | 206.2 | 266 | 95.8 |  |  |  |  | 856 | 338142 5ISES-1! 161 338759 5COFFEEVLE# 161 1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338142 5ISES-1! 161 338759 5COFFEEVLE# 161 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101006 | 23S | Approved | P2 | 9 | 338007 3BEEBE 115 338008 3GARNER+ 115 1 | LN | 254.2 | 23.5 | 266 | 95.6 |  |  |  |  | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338007 | 338008 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101007 | 23S | Approved | P2 | 9 | 338008 3GARNER+ 115 338010 3SRCY PRICE! 115 1 | LN | 255.1 | 22.7 | 239 | 106.7 |  |  |  |  | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338008 | 338010 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101008 | 23S | Approved | P2 | 9 | 338010 3SRCY PRICE! 115 338045 5SRCY PRICE! 161 1 | TR | 231.2 | 77.5 | 225 | 102.8 |  |  |  |  | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338010 | 338045 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101009 | 23S | Approved | P1 | 9 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 138.4 | 109.3 | 148 | 93.5 |  |  |  |  | 872 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 |  |  | No violation: below Rate A
101010 | 23S | Approved | P1 | 9 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 133.9 | 109.3 | 148 | 90.5 |  |  |  |  | 1084 | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338188 8SANS SOUCI% 500 360021 8SHELBY TN 500 1 |  |  | No violation: below Rate A
101011 | 23S | Approved | P1 | 9 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 144.9 | 115.5 | 160 | 90.5 |  |  |  |  | 872 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 |  | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
101012 | 23S | Approved | P1 | 9 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 153.4 | 81.2 | 148 | 103.6 |  |  |  |  | 850 | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 |  | Project Proposed |  | 11-EAI-025-CP | 2016-06-01 | Upgrade Norfork-Calico Rock 161 kV
101013 | 23S | Approved | P1 | 9 | 338160 5EBONY% 161 338412 5WM LEHI-W 161 1 | LN | 203.9 | 103.9 | 223 | 91.4 |  |  |  |  | 1078 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | 338160 | 338412 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 |  |  | No violation: below Rate A
101014 | 23S | Approved | P1 | 9 | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 | LN | 216.9 | 116.7 | 223 | 97.3 |  |  |  |  | 1078 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | 338161 | 338412 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 |  |  | No violation: below Rate A
101015 | 23S | Approved | P1 | 9 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 201.4 | 117.9 | 223 | 90.3 |  |  |  |  | 1075 | 338160 5EBONY% 161 338412 5WM LEHI-W 161 1 | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338160 5EBONY% 161 338412 5WM LEHI-W 161 1 |  |  | No violation: below Rate A
101016 | 23S | Approved | P1 | 9 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 212 | 117.9 | 223 | 95.1 |  |  |  |  | 1077 | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 |  |  | No violation: below Rate A
101017 | 23S | Approved | P2 | 9 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 155 | 86 | 148 | 104.7 |  |  |  |  | 867 | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 |  | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101018 | 23S | Approved | P2 | 9 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 138.8 | 86 | 148 | 93.8 |  |  |  |  | 879 | 338170 5JONESBORO! 161 338171 5CASH 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338170 5JONESBORO! 161 338171 5CASH 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101019 | 23S | Approved | P1 | 9 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 145.9 | 86 | 148 | 98.6 |  |  |  |  | 882 | 338171 5CASH 161 338172 5NEWPORT AB 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338171 5CASH 161 338172 5NEWPORT AB 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101020 | 23S | Approved | P1 | 9 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 153.3 | 86 | 148 | 103.6 |  |  |  |  | 883 | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101021 | 23S | Approved | P1 | 9 | 338202 5JIM HILL% 161 338230 3JIM HILL! 115 1 | TR | 108.3 | 54.8 | 112 | 96.7 |  |  |  |  | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338202 | 338230 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101022 | 23S | Approved | P1 | 9 | 338202 5JIM HILL% 161 338230 3JIM HILL! 115 1 | TR | 108.1 | 54.8 | 112 | 96.5 |  |  |  |  | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338202 | 338230 | 1 |  | 161 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101023 | 23S | Approved | P1 | 9 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 92.1 | 40.7 | 70 | 131.6 |  |  |  |  | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101024 | 23S | Approved | P1 | 9 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 70 | 40.7 | 70 | 99.9 |  |  |  |  | 928 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101025 | 23S | Approved | P1 | 9 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 91.9 | 40.7 | 70 | 131.4 |  |  |  |  | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101026 | 23S | Approved | P1 | 9 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 100 | 46.9 | 70 | 142.8 |  |  |  |  | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101027 | 23S | Approved | P1 | 9 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 77 | 46.9 | 70 | 110 |  |  |  |  | 928 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101028 | 23S | Approved | P1 | 9 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 99.8 | 46.9 | 70 | 142.5 |  |  |  |  | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101029 | 23S | Approved | P1 | 9 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | LN | 1723.4 | 1333.7 | 1732.1 | 99.5 |  |  |  |  | 3996 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 360065 | 360081 | 1 |  | 500 | 500 | 347 | TVA | 347 | TVA | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 |  |  | No violation: below Rate A
101030 | 23S | Approved | P1 | 9 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | LN | 1840 | 1333.7 | 1732.1 | 106.2 |  |  |  |  | 4003 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | 360065 | 360081 | 1 |  | 500 | 500 | 347 | TVA | 347 | TVA | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1
101031 | 23S | Approved | P1 | 9 | 360071 8WILSON TN 500 990066 1.00 1 | TR | 1152.2 | 804.1 | 1247 | 92.4 |  |  |  |  | 4047 | 3Wnd: OPEN B$0204 1 | 360071 | 990066 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0204 1 |  |  | No violation: below Rate A
101032 | 23S | Approved | P1 | 9 | 360581 8PIN HOOK TN 500 990204 1.00 1 | TR | 1203.3 | 1013 | 1253.7 | 96 |  |  |  |  | 3948 | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1 | 360581 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1 |  |  | No violation: below Rate A
101033 | 23S | Approved | P1 | 9 | 360581 8PIN HOOK TN 500 990204 1.00 1 | TR | 1321.4 | 1013 | 1253.7 | 105.4 |  |  |  |  | 4016 | 3Wnd: OPEN B$0066 1 | 360581 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0066 1
101034 | 23S | Approved | P1 | 9 | 360613 8MAGNOL CC1 500 990174 1.00 1 | TR | 324.2 | 314.2 | 360 | 90.1 |  |  |  |  | 3996 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 360613 | 990174 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 |  |  | No violation: below Rate A
101035 | 23S | Approved | P1 | 9 | 360613 8MAGNOL CC1 500 990174 1.00 1 | TR | 330.3 | 314.2 | 360 | 91.8 |  |  |  |  | 4055 | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 | 360613 | 990174 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 |  |  | No violation: below Rate A
101036 | 23S | Approved | P1 | 9 | 380008 8VOGTLE 500 380009 8W MCINTOSH 500 1 | LN | 2461.9 | 1828.9 | 2439 | 100.9 |  |  |  |  | 2885 | 380018 8SCHERER + 500 383008 8HANCOCK CO 500 1 | 380008 | 380009 | 1 |  | 500 | 500 | 346 | SOCO | 346 | SOCO | 380018 8SCHERER + 500 383008 8HANCOCK CO 500 1
101037 | 23S | Approved | P1 | 9 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648 | 207.1 | 700 | 92.6 |  |  |  |  | 2738 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101038 | 23S | Approved | P1 | 9 | 500265 DTOWN 138 500420 HUNTER4 138 1 | LN | 136.3 | 67.2 | 148 | 92.1 |  |  |  |  | 2703 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | 500265 | 500420 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 |  |  | No violation: below Rate A
101039 | 23S | Approved | P1 | 9 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | LN | 136.4 | 67.7 | 148 | 92.1 |  |  |  |  | 2659 | 500265 DTOWN 138 500420 HUNTER4 138 1 | 500735 | 500816 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500265 DTOWN 138 500420 HUNTER4 138 1 |  |  | No violation: below Rate A
101040 | 23S | Approved | P1 | 9 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.4 | 65.1 | 115 | 97.8 |  |  |  |  | 2747 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  |  | No violation: below Rate A
101041 | 23S | Approved | P1 | 9 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 128.4 | 65.1 | 115 | 111.7 |  |  |  |  | 2762 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1
101042 | 23S | Approved | P1 | 9 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 94.3 | 56.8 | 95 | 99.2 |  |  |  |  | 2756 | 502405 BONIN 2 69.0 502408 STGEORG2 69.0 1 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502408 STGEORG2 69.0 1 |  |  | No violation: below Rate A
101043 | 23S | Approved | P1 | 9 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 98.1 | 56.8 | 95 | 103.2 |  |  |  |  | 2773 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1
101044 | 23S | Approved | P1 | 9 | 502407 PINHOOK2 69.0 502413 ELKS 2 69.0 1 | LN | 127.7 | 61.3 | 115 | 111.1 |  |  |  |  | 2757 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | 502407 | 502413 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1
101045 | 23S | Approved | P0 | 9 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100 | 100 | 95 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101046 | 23S | Approved | P1 | 9 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.6 | 100 | 95 | 108 |  |  |  |  | 2730 | Unit:501823 G3TECHE 24.0 Id:1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | Unit:501823 G3TECHE 24.0 Id:1 |  |  | Facility: Radial
101047 | 23S | Approved | P1 | 9 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.4 | 100 | 95 | 107.8 |  |  |  |  | 2769 | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502413 ELKS 2 69.0 502417 ELKS 6 230 1 |  |  | Facility: Radial
101048 | 23S | Approved | P1 | 9 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.4 | 100 | 95 | 107.8 |  |  |  |  | 2772 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
101049 | 23S | Approved | P1 | 9 | 502426 PERARD 2 69.0 502442 SW 1482 69.0 1 | LN | 97.8 | 40.6 | 95 | 102.9 |  |  |  |  | 2758 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | 502426 | 502442 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1
101050 | 23S | Approved | P1 | 9 | 508832 DIANA 7 345 990778 DIANA 2 1.00 2 | TR | 293.1 | 186.4 | 314 | 93.3 |  |  |  |  | 4663 | 3Wnd: OPEN B$0779 DIANA 3 3 | 508832 | 990778 | 2 |  | 345 | 1 | 520 | AEPW | 520 | AEPW | 3Wnd: OPEN B$0779 DIANA 3 3 |  |  | No violation: below Rate A
101051 | 23S | Approved | P1 | 9 | 514880 NORTWST7 345 991461 NORTWST2 1.00 1 | TR | 484.9 | 345.5 | 493 | 98.4 |  |  |  |  | 4798 | 3Wnd: OPEN B$1462 NORTWST3 1 | 514880 | 991461 | 1 |  | 345 | 1 | 524 | OKGE | 524 | OKGE | 3Wnd: OPEN B$1462 NORTWST3 1 |  |  | No violation: below Rate A
101052 | 23S | Approved | P0 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 332 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
101053 | 23S | Approved | P0 | 10 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.6 | 18.6 | 19 | 98 |  |  |  |  | 0 | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101054 | 23S | Approved | P0 | 10 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 40 | 40 | 38 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
101054 | 23S | Approved | P0 | 10 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 40 | 40 | 38 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-02-CP | 2014-12-01 | Upgrade Mossville-Canal 69 kV Phase 2
101055 | 23S | Approved | P0 | 10 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 30.8 | 30.8 | 33 | 93.3 |  |  |  |  | 0 | ** Base Case ** | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101056 | 23S | Approved | P0 | 10 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 52.8 | 52.8 | 56 | 94.3 |  |  |  |  | 0 | ** Base Case ** | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101057 | 23S | Approved | P0 | 10 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 109.4 | 109.4 | 93 | 117.6 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
101058 | 23S | Approved | P0 | 10 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 20.3 | 20.3 | 20 | 101.5 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
101059 | 23S | Approved | P0 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179 | 179 | 193 | 92.7 |  |  |  |  | 0 | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | Facility: Radial
101060 | 23S | Approved | P0 | 10 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.7 | 37.7 | 39 | 96.7 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
101061 | 23S | Approved | P0 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 109.8 | 109.8 | 112 | 98 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101062 | 23S | Approved | P0 | 10 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 547.4 | 547.4 | 598 | 91.5 |  |  |  |  | 0 | ** Base Case ** | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101063 | 23S | Approved | P0 | 10 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100 | 100 | 95 | 105.3 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101064 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.8 | 332 | 360 | 92.7 |  |  |  |  | 38 | G-334440-1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | G-334440-1 |  |  | Facility: GSU
101065 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.4 | 179 | 193 | 93.5 |  |  |  |  | 105 | G-336853-1 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | G-336853-1 |  |  | Facility: Radial
101066 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.8 | 112 | 99.2 |  |  |  |  | 112 | G-337041-1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | G-337041-1 |  |  | Facility: Radial
101067 | 23S | Approved | P1 | 10 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.6 | 100 | 95 | 108 |  |  |  |  | 195 | G-501823-1 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | G-501823-1 |  |  | Facility: Radial
101068 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 332 | 360 | 92.5 |  |  |  |  | 353 | P1_2-101 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-101_8COTNWOOD2!,8HARTBRG% |  |  | Facility: GSU
101069 | 23S | Approved | P1 | 10 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 207.6 | 144.3 | 191 | 108.7 |  |  |  |  | 364 | P1_2-112 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-112 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101070 | 23S | Approved | P1 | 10 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 233 | 107.8 | 233 | 100 |  |  |  |  | 365 | P1_2-113 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-113_4LEBLANC!,4MORIL! |  | Project Horizon |  | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
101070 | 23S | Approved | P1 | 10 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 233 | 107.8 | 233 | 100 |  |  |  |  | 365 | P1_2-113 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-113_4LEBLANC!,4MORIL! |  | Project Horizon |  | 14-EGL-015-HZ | 2022-06-01 | Meaux to Abbeville - Reconductor Line
101071 | 23S | Approved | P1 | 10 | 334054 4WALKER 138 334055 4RIVTRIN% 138 1 | LN | 109 | 47.9 | 121 | 90.1 |  |  |  |  | 383 | P1_2-131 | 334054 | 334055 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-131 |  |  | No violation: below Rate A
101072 | 23S | Approved | P1 | 10 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.1 | 128.4 | 206 | 91.3 |  |  |  |  | 411 | P1_2-159 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! |  | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101073 | 23S | Approved | P1 | 10 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 222.4 | 84.7 | 243 | 91.5 |  |  |  |  | 427 | P1_2-175 | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% |  | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101074 | 23S | Approved | P1 | 10 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 221.9 | 182.7 | 243 | 91.3 |  |  |  |  | 436 | P1_2-184 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
101075 | 23S | Approved | P1 | 10 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.7 | 92.6 | 206 | 97.5 |  |  |  |  | 436 | P1_2-184 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
101076 | 23S | Approved | P1 | 10 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 222 | 182.7 | 243 | 91.4 |  |  |  |  | 455 | P1_2-203 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203 |  | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
101077 | 23S | Approved | P1 | 10 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 200.8 | 92.6 | 206 | 97.5 |  |  |  |  | 455 | P1_2-203 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203 |  | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
101078 | 23S | Approved | P1 | 10 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 36.7 | 15.8 | 39 | 94.1 |  |  |  |  | 472 | P1_2-220 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
101079 | 23S | Approved | P1 | 10 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39.2 | 18.6 | 39 | 100.6 |  |  |  |  | 472 | P1_2-220 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
101080 | 23S | Approved | P1 | 10 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.1 | 15.8 | 39 | 95.2 |  |  |  |  | 475 | P1_2-223 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! |  | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
101081 | 23S | Approved | P1 | 10 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 39.7 | 18.6 | 39 | 101.8 |  |  |  |  | 475 | P1_2-223 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
101082 | 23S | Approved | P1 | 10 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | LN | 35.3 | 11.4 | 39 | 90.6 |  |  |  |  | 476 | P1_2-224 | 334265 | 334266 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  |  | No violation: below Rate A
101083 | 23S | Approved | P1 | 10 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 35.8 | 11.8 | 39 | 91.9 |  |  |  |  | 476 | P1_2-224 | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  |  | No violation: below Rate A
101084 | 23S | Approved | P1 | 10 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 36 | 11.9 | 39 | 92.3 |  |  |  |  | 476 | P1_2-224 | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  |  | No violation: below Rate A
101086 | 23S | Approved | P1 | 10 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 42.7 | 18.6 | 39 | 109.4 |  |  |  |  | 476 | P1_2-224 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% |  | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
101087 | 23S | Approved | P1 | 10 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 109.2 | 49.6 | 120 | 91 |  |  |  |  | 489 | P1_2-237 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
101088 | 23S | Approved | P1 | 10 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 115.4 | 55.7 | 127 | 90.9 |  |  |  |  | 489 | P1_2-237 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
101089 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 332 | 360 | 92.5 |  |  |  |  | 511 | P1_2-259 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-259_8CYPRESS%,8HARTBRG% |  |  | Facility: GSU
101090 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.4 | 332 | 360 | 92.6 |  |  |  |  | 515 | P1_2-263 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-263 |  |  | Facility: GSU
101091 | 23S | Approved | P1 | 10 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 265.2 | 179.5 | 287 | 92.4 |  |  |  |  | 555 | P1_2-303 | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-303_4PNEC BK!,4SABINE! |  | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
101092 | 23S | Approved | P1 | 10 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 271.4 | 171.4 | 288 | 94.2 |  |  |  |  | 556 | P1_2-304 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-304_4PNEC BK!,4SABINE! |  | Project Proposed | No violation: below Rate A | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
101093 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.8 | 332 | 360 | 92.7 |  |  |  |  | 569 | P1_2-317 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-317_6SABINE%,1G4SABIN! |  |  | Facility: GSU
101094 | 23S | Approved | P1 | 10 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.4 | 332 | 360 | 92.6 |  |  |  |  | 740 | P1_2-488 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-488 |  |  | Facility: GSU
101095 | 23S | Approved | P1 | 10 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.8 | 176.8 | 225 | 91.9 |  |  |  |  | 796 | P1_2-544 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-544_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
101096 | 23S | Approved | P1 | 10 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211.1 | 176.8 | 225 | 93.8 |  |  |  |  | 797 | P1_2-545 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
101097 | 23S | Approved | P1 | 10 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 202.5 | 168.2 | 225 | 90 |  |  |  |  | 797 | P1_2-545 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! |  |  | No violation: below Rate A
101098 | 23S | Approved | P1 | 10 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 221 | 115.9 | 241 | 91.7 |  |  |  |  | 817 | P1_2-565 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! |  |  | No violation: below Rate A
101099 | 23S | Approved | P1 | 10 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 227 | 144.3 | 191 | 118.8 |  |  |  |  | 817 | P1_2-565 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101100 | 23S | Approved | P1 | 10 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 221 | 115.9 | 241 | 91.7 |  |  |  |  | 818 | P1_2-566 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% |  |  | No violation: below Rate A
101101 | 23S | Approved | P1 | 10 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 227 | 144.3 | 191 | 118.9 |  |  |  |  | 818 | P1_2-566 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101102 | 23S | Approved | P1 | 10 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 47 | 21 | 39 | 120.5 |  |  |  |  | 821 | P1_2-569 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
101103 | 23S | Approved | P1 | 10 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 43.1 | 17.6 | 39 | 110.6 |  |  |  |  | 821 | P1_2-569 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
101104 | 23S | Approved | P1 | 10 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 43.8 | 26.7 | 39 | 112.2 |  |  |  |  | 821 | P1_2-569 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
101105 | 23S | Approved | P1 | 10 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 41.6 | 26.7 | 39 | 106.7 |  |  |  |  | 831 | P1_2-579 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
101106 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | LN | 131.3 | 63 | 141 | 93.1 |  |  |  |  | 971 | P1_2-719 | 335713 | 335718 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-719 |  |  | No violation: below Rate A
101107 | 23S | Approved | P1 | 10 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | LN | 129.6 | 61.3 | 136 | 95.3 |  |  |  |  | 971 | P1_2-719 | 335718 | 335719 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-719 |  |  | No violation: below Rate A
101108 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 181.8 | 128.2 | 200 | 90.9 |  |  |  |  | 979 | P1_2-727 | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727 |  |  | Model: does not represent split configuration
101109 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 199 | 140.7 | 200 | 99.5 |  |  |  |  | 979 | P1_2-727 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727 |  |  | Model: does not represent split configuration
101110 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | TR | 186.6 | 134.2 | 200 | 93.3 |  |  |  |  | 980 | P1_2-728 | 335713 | 335771 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-728 |  |  | Model: does not represent split configuration
101111 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 195.6 | 140.7 | 200 | 97.8 |  |  |  |  | 980 | P1_2-728 | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-728 |  |  | Model: does not represent split configuration
101112 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 1 | TR | 193.7 | 134.2 | 200 | 96.9 |  |  |  |  | 981 | P1_2-729 | 335713 | 335771 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-729 |  |  | Model: does not represent split configuration
101113 | 23S | Approved | P1 | 10 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 185.6 | 128.2 | 200 | 92.8 |  |  |  |  | 981 | P1_2-729 | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-729 |  |  | Model: does not represent split configuration
101114 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 180.4 | 167.4 | 200 | 90.2 |  |  |  |  | 991 | P1_2-739 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-739 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101115 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 184.1 | 167.4 | 200 | 92 |  |  |  |  | 1001 | P1_2-749 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-749 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101116 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 187.6 | 167.4 | 200 | 93.8 |  |  |  |  | 1006 | P1_2-754 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-754 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101117 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 189.7 | 167.4 | 200 | 94.8 |  |  |  |  | 1011 | P1_2-759 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-759 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101118 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.1 | 48.5 | 100 | 101.1 |  |  |  |  | 1012 | P1_2-760 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101119 | 23S | Approved | P1 | 10 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.8 | 47.9 | 100 | 99.8 |  |  |  |  | 1012 | P1_2-760 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101120 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 189.3 | 167.4 | 200 | 94.7 |  |  |  |  | 1017 | P1_2-765 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101121 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190.4 | 167.4 | 200 | 95.2 |  |  |  |  | 1020 | P1_2-768 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-768 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101122 | 23S | Approved | P1 | 10 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 302.7 | 175.7 | 300 | 100.9 |  |  |  |  | 1020 | P1_2-768 | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-768 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101123 | 23S | Approved | P1 | 10 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190 | 167.4 | 200 | 95 |  |  |  |  | 1021 | P1_2-769 | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101124 | 23S | Approved | P1 | 10 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 303.6 | 177.5 | 300 | 101.2 |  |  |  |  | 1021 | P1_2-769 | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101127 | 23S | Approved | P1 | 10 | 336007 6VACHRE! 230 336154 6WATFRD% 230 1 | LN | 420.8 | 310.1 | 459 | 91.7 |  |  |  |  | 1062 | P1_2-810 | 336007 | 336154 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-810 |  |  | No violation: below Rate A
101129 | 23S | Approved | P1 | 10 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | LN | 104.3 | 56.4 | 115 | 90.7 |  |  |  |  | 1086 | P1_2-834 | 336080 | 336081 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-834_3GMEADW!,3BARATA! |  |  | No violation: below Rate A
101130 | 23S | Approved | P1 | 10 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 76.4 | 115 | 91.7 |  |  |  |  | 1088 | P1_2-836 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-836 |  | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
101131 | 23S | Approved | P1 | 10 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 183.5 | 133.6 | 199 | 92.2 |  |  |  |  | 1117 | P1_2-865 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101132 | 23S | Approved | P1 | 10 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 222.4 | 139.9 | 229 | 97.1 |  |  |  |  | 1203 | P1_2-951 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! |  |  | No violation: below Rate A
101133 | 23S | Approved | P1 | 10 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 217.3 | 165.5 | 229 | 94.9 |  |  |  |  | 1204 | P1_2-952 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-952_39MILE%,3GRETNA! |  | Project Horizon | No violation: below Rate A | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
101134 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.1 | 179 | 193 | 93.3 |  |  |  |  | 1256 | P1_2-1004 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1004 |  |  | Facility: Radial
101135 | 23S | Approved | P1 | 10 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38.8 | 37.7 | 39 | 99.5 |  |  |  |  | 1274 | P1_2-1022 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1022 |  |  | Facility: Radial
101136 | 23S | Approved | P1 | 10 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 109.4 | 88.8 | 115 | 95.1 |  |  |  |  | 1274 | P1_2-1022 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1022 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
101137 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.9 | 179 | 193 | 93.8 |  |  |  |  | 1288 | P1_2-1036 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1036 |  |  | Facility: Radial
101138 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 179 | 193 | 93.4 |  |  |  |  | 1290 | P1_2-1038 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1038 |  |  | Facility: Radial
101139 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 179 | 193 | 93.4 |  |  |  |  | 1291 | P1_2-1039 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1039 |  |  | Facility: Radial
101140 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.3 | 179 | 193 | 93.4 |  |  |  |  | 1292 | P1_2-1040 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1040 |  |  | Facility: Radial
101141 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 179 | 193 | 93.4 |  |  |  |  | 1296 | P1_2-1044 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1044 |  |  | Facility: Radial
101142 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 176.1 | 179 | 193 | 91.3 |  |  |  |  | 1301 | P1_2-1049 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1049 |  |  | Facility: Radial
101143 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181 | 179 | 193 | 93.8 |  |  |  |  | 1304 | P1_2-1052 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1052 |  |  | Facility: Radial
101144 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 175.8 | 179 | 193 | 91.1 |  |  |  |  | 1307 | P1_2-1055 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1055 |  |  | Facility: Radial
101145 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.6 | 179 | 193 | 93.6 |  |  |  |  | 1312 | P1_2-1060 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1060_6S.CANTON!,6PICKENS! |  |  | Facility: Radial
101146 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 177 | 179 | 193 | 91.7 |  |  |  |  | 1318 | P1_2-1066 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1066 |  |  | Facility: Radial
101147 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.2 | 179 | 193 | 93.4 |  |  |  |  | 1333 | P1_2-1081 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1081 |  |  | Facility: Radial
101148 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180.8 | 179 | 193 | 93.7 |  |  |  |  | 1340 | P1_2-1088 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% |  |  | Facility: Radial
101149 | 23S | Approved | P1 | 10 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 557.6 | 331.2 | 561 | 99.4 |  |  |  |  | 1349 | P1_2-1097 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101150 | 23S | Approved | P1 | 10 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181.2 | 179 | 193 | 93.9 |  |  |  |  | 1351 | P1_2-1099 | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1099 |  |  | Facility: Radial
101151 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.8 | 112 | 99.2 |  |  |  |  | 1364 | P1_2-1112 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1112 |  |  | Facility: Radial
101152 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.8 | 112 | 99.7 |  |  |  |  | 1367 | P1_2-1115 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1115_6ANDRUS%,3BAGBY! |  |  | Facility: Radial
101153 | 23S | Approved | P1 | 10 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 287.2 | 208.6 | 278 | 103.3 |  |  |  |  | 1386 | P1_2-1134 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
101154 | 23S | Approved | P1 | 10 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 297.5 | 208.6 | 278 | 107 |  |  |  |  | 1387 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale
101155 | 23S | Approved | P1 | 10 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 292.3 | 81.3 | 278 | 105.2 |  |  |  |  | 1391 | P1_2-1139 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101156 | 23S | Approved | P1 | 10 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305 | 91.1 | 250 | 122 |  |  |  |  | 1391 | P1_2-1139 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101158 | 23S | Approved | P1 | 10 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 113.2 | 88.8 | 115 | 98.4 |  |  |  |  | 1427 | P1_2-1175 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175 |  | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
101159 | 23S | Approved | P1 | 10 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 103.7 | 61.9 | 115 | 90.2 |  |  |  |  | 1444 | P1_2-1192 | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1192_3MINDEN_LA!,3SAREPTA! |  |  | No violation: below Rate A
101160 | 23S | Approved | P1 | 10 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 258.3 | 200.1 | 262 | 98.6 |  |  |  |  | 1465 | P1_2-1213 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1213 |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
101161 | 23S | Approved | P1 | 10 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 252.4 | 200.1 | 262 | 96.3 |  |  |  |  | 1466 | P1_2-1214 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% |  | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
101162 | 23S | Approved | P1 | 10 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.3 | 36 | 80 | 101.6 |  |  |  |  | 1466 | P1_2-1214 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% |  | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101163 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.8 | 109.8 | 112 | 98.9 |  |  |  |  | 1482 | P1_2-1230 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1230 |  |  | Facility: Radial
101164 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.4 | 109.8 | 112 | 99.5 |  |  |  |  | 1502 | P1_2-1250 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1250 |  |  | Facility: Radial
101165 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.8 | 109.8 | 112 | 98.9 |  |  |  |  | 1527 | P1_2-1275 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1275 |  |  | Facility: Radial
101166 | 23S | Approved | P1 | 10 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.8 | 112 | 99.2 |  |  |  |  | 1536 | P1_2-1284 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1284 |  |  | Facility: Radial
101167 | 23S | Approved | P1 | 10 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 243.9 | 179.1 | 266 | 91.7 |  |  |  |  | 1543 | P1_2-1291 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1291_3FORDYCE!,3WOODWARD-S! |  |  | No violation: below Rate A
101168 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 235.4 | 194.1 | 239 | 98.5 |  |  |  |  | 1549 | P1_2-1297 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101169 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 163.4 | 127.4 | 159 | 102.8 |  |  |  |  | 1563 | P1_2-1311 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101170 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 146.4 | 127.4 | 159 | 92.1 |  |  |  |  | 1564 | P1_2-1312 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1312 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101171 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 215.3 | 194.1 | 239 | 90.1 |  |  |  |  | 1578 | P1_2-1326 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101172 | 23S | Approved | P1 | 10 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.4 | 547.4 | 598 | 91.4 |  |  |  |  | 1578 | P1_2-1326 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326 |  |  | Facility: Radial
101173 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.6 | 194.1 | 239 | 101.9 |  |  |  |  | 1584 | P1_2-1332 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101174 | 23S | Approved | P1 | 10 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 155.7 | 100.7 | 159 | 97.9 |  |  |  |  | 1584 | P1_2-1332 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332 |  | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
101175 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 144.5 | 127.4 | 159 | 90.9 |  |  |  |  | 1584 | P1_2-1332 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101176 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 273.2 | 194.1 | 239 | 114.3 |  |  |  |  | 1585 | P1_2-1333 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101177 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 187.2 | 99 | 176 | 106.3 |  |  |  |  | 1585 | P1_2-1333 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
101178 | 23S | Approved | P1 | 10 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 175.2 | 87.1 | 176 | 99.6 |  |  |  |  | 1585 | P1_2-1333 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
101179 | 23S | Approved | P1 | 10 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 186.2 | 98.1 | 176 | 105.8 |  |  |  |  | 1585 | P1_2-1333 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! |  | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
101180 | 23S | Approved | P1 | 10 | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 2 | LN | 240.5 | 132.9 | 266 | 90.4 |  |  |  |  | 1586 | P1_2-1334 | 337686 | 337740 | 2 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1334 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101181 | 23S | Approved | P1 | 10 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.3 | 547.4 | 598 | 91.4 |  |  |  |  | 1597 | P1_2-1345 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1345_3HS EHV-E!,8HS EHV% |  |  | Facility: Radial
101182 | 23S | Approved | P1 | 10 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 240.3 | 194.1 | 239 | 100.5 |  |  |  |  | 1598 | P1_2-1346 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346 |  | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101183 | 23S | Approved | P1 | 10 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 163.3 | 93.2 | 159 | 102.7 |  |  |  |  | 1598 | P1_2-1346 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346 |  | Project Horizon |  | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
101184 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 163.4 | 127.4 | 159 | 102.8 |  |  |  |  | 1600 | P1_2-1348 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101185 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 150.5 | 127.4 | 159 | 94.6 |  |  |  |  | 1614 | P1_2-1362 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1362 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101188 | 23S | Approved | P1 | 10 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 150.2 | 127.4 | 159 | 94.5 |  |  |  |  | 1623 | P1_2-1371 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1371 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101189 | 23S | Approved | P1 | 10 | 337922 8P.HILL% 500 337923 5P.HILL% 161 1 | TR | 585.3 | 413.4 | 600 | 97.5 |  |  |  |  | 1656 | P1_2-1404 | 337922 | 337923 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1404 |  |  | No violation: below Rate A
101194 | 23S | Approved | P1 | 10 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 107.2 | 61.6 | 106 | 101.2 |  |  |  |  | 1700 | P1_2-1448 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101195 | 23S | Approved | P1 | 10 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | LN | 97.2 | 51.8 | 106 | 91.7 |  |  |  |  | 1700 | P1_2-1448 | 337972 | 337973 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101196 | 23S | Approved | P1 | 10 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 250.1 | 206.2 | 266 | 94 |  |  |  |  | 1709 | P1_2-1458 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1458_3BRINKLEY.E!,5MOSES% |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101197 | 23S | Approved | P1 | 10 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 239.5 | 206.2 | 266 | 90 |  |  |  |  | 1720 | P1_2-1471 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1471 |  | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101198 | 23S | Approved | P1 | 10 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 140 | 86 | 148 | 94.6 |  |  |  |  | 1745 | P1_2-1496 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101199 | 23S | Approved | P1 | 10 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 204 | 117.9 | 223 | 91.5 |  |  |  |  | 1749 | P1_2-1500 | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! |  |  | No violation: below Rate A
101200 | 23S | Approved | P1 | 10 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 138.4 | 109.3 | 148 | 93.5 |  |  |  |  | 1752 | P1_2-1503 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% |  |  | No violation: below Rate A
101202 | 23S | Approved | P1 | 10 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 133.9 | 109.3 | 148 | 90.5 |  |  |  |  | 1770 | P1_2-1521 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1521 |  |  | No violation: below Rate A
101203 | 23S | Approved | P1 | 10 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 227.6 | 100.4 | 226 | 100.7 |  |  |  |  | 1812 | P1_2-1563 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101204 | 23S | Approved | P1 | 10 | 500265 DTOWN 138 500420 HUNTER4 138 1 | LN | 137.5 | 67.2 | 148 | 92.9 |  |  |  |  | 1864 | P1_2-1615 | 500265 | 500420 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1615 |  |  | No violation: below Rate A
101205 | 23S | Approved | P1 | 10 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.3 | 176.8 | 225 | 91.2 |  |  |  |  | 1903 | P1_2-1654 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! |  |  | No violation: below Rate A
101206 | 23S | Approved | P1 | 10 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648 | 207.1 | 700 | 92.6 |  |  |  |  | 1910 | P1_2-1661 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
101207 | 23S | Approved | P1 | 10 | 500735 PSCOTT 138 500816 SW_BRAPI 138 1 | LN | 136.4 | 67.7 | 148 | 92.1 |  |  |  |  | 1912 | P1_2-1663 | 500735 | 500816 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1663 |  |  | No violation: below Rate A
101208 | 23S | Approved | P1 | 10 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 145.6 | 38.8 | 159 | 91.6 |  |  |  |  | 1981 | P1_2-1732 | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1732 |  |  | No violation: below Rate A
101209 | 23S | Approved | P1 | 10 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.9 | 44 | 157 | 96.1 |  |  |  |  | 1981 | P1_2-1732 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1732 |  |  | No violation: below Rate A
101210 | 15S | Proposed | P0 | 11 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105.1 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101211 | 15S | Proposed | P1 | 11 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 96 | 50 | 98 | 97.9 |  |  |  |  | 468 | P1_2-241 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101212 | 15S | Proposed | P1 | 11 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 452.9 | 324 | 470 | 96.4 |  |  |  |  | 679 | P1_2-452 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452 |  | Reduce PPG Plant | No violation: below Rate A
101213 | 15S | Proposed | P1 | 11 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 95.4 | 46.3 | 100 | 95.4 |  |  |  |  | 981 | P1_2-755 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-755 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101214 | 15S | Proposed | P1 | 11 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194.2 | 143 | 199 | 97.6 |  |  |  |  | 1086 | P1_2-860 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101216 | 15S | Proposed | P1 | 11 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 290.6 | 210.4 | 278 | 104.5 |  |  |  |  | 1355 | P1_2-1129 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1129 |  | SPS: Clarksdale
101217 | 15S | Proposed | P1 | 11 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.2 | 210.4 | 278 | 107.3 |  |  |  |  | 1356 | P1_2-1130 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1130 |  | SPS: Clarksdale
101218 | 15S | Proposed | P1 | 11 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 295.4 | 83.1 | 278 | 106.3 |  |  |  |  | 1360 | P1_2-1134 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
101219 | 15S | Proposed | P1 | 11 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.7 | 89.7 | 250 | 122.3 |  |  |  |  | 1360 | P1_2-1134 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
101220 | 15S | Proposed | P1 | 11 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 132.5 | 18.5 | 115 | 115.2 |  |  |  |  | 1561 | P1_2-1336 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1336 |  |  | Contingency: invalid after Albright
101221 | 15S | Proposed | P1 | 11 | 337715 3MILTON 115 337721 3ALBRIGHT 115 1 | LN | 167.7 | 14.4 | 176 | 95.3 |  |  |  |  | 1561 | P1_2-1336 | 337715 | 337721 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1336 |  |  | Contingency: invalid after Albright
101224 | 15S | Proposed | P1 | 11 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 237.9 | 118 | 226 | 105.2 |  |  |  |  | 1780 | P1_2-1558 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101225 | 15S | Proposed | P1 | 11 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 209.6 | 79.7 | 219 | 95.7 |  |  |  |  | 1878 | P1_2-1656 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_COUGH 4!,PNPRARIE 4% |  |  | No violation: below Rate A
101226 | 15S | Proposed | P1 | 11 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 186.7 | 56.5 | 188 | 99.3 |  |  |  |  | 1878 | P1_2-1656 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_COUGH 4!,PNPRARIE 4% |  |  | No violation: below Rate A
101227 | 15S | Proposed | P1 | 11 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 149.7 | 34.3 | 157 | 95.4 |  |  |  |  | 1949 | P1_2-1727 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1727 |  |  | No violation: below Rate A
101228 | 15S | Proposed | P0 | 12 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105.1 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101229 | 15S | Proposed | P1 | 12 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.9 | 33.3 | 106 | 102.8 |  |  |  |  | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101230 | 15S | Proposed | P1 | 12 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 105.3 | 30.7 | 106 | 99.3 |  |  |  |  | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101231 | 15S | Proposed | P1 | 12 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 149.3 | 71.2 | 148 | 100.9 |  |  |  |  | 446 | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | 338138 5MOOREFIELD 161 338142 5ISES-1! 161 1 |  | Project Proposed |  | 11-EAI-025-CP | 2016-06-01 | Upgrade Norfork-Calico Rock 161 kV
101232 | 15S | Proposed | P2 | 12 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 144 | 78.4 | 148 | 97.3 |  |  |  |  | 463 | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | No violation: below Rate A | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101233 | 15S | Proposed | P1 | 12 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 142.3 | 78.4 | 148 | 96.1 |  |  |  |  | 479 | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101234 | 15S | Proposed | P1 | 12 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 81.8 | 35.8 | 70 | 116.8 |  |  |  |  | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101235 | 15S | Proposed | P1 | 12 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 89.2 | 41.7 | 70 | 127.4 |  |  |  |  | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101236 | 15S | Proposed | P1 | 12 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 72.3 | 41.7 | 70 | 103.4 |  |  |  |  | 524 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101237 | 15S | Proposed | P1 | 12 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | LN | 81.7 | 35.8 | 70 | 116.7 |  |  |  |  | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 | 338229 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101238 | 15S | Proposed | P1 | 12 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 89.1 | 41.7 | 70 | 127.3 |  |  |  |  | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
101239 | 15S | Proposed | P1 | 12 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 95.8 | 50 | 98 | 97.8 |  |  |  |  | 914 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334307 4BUNA! 138 334308 4JNE EVA 138 1 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101240 | 15S | Proposed | P1 | 12 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 100.8 | 50 | 98 | 102.9 |  |  |  |  | 915 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101241 | 15S | Proposed | P1 | 12 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 452.9 | 324 | 470 | 96.4 |  |  |  |  | 1239 | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 335070 6CARLYSS% 230 335190 6NELSON% 230 1 |  | Reduce PPG Plant | No violation: below Rate A
101242 | 15S | Proposed | P1 | 12 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224.4 | 118.1 | 200 | 112.2 |  |  |  |  | 1276 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
101243 | 15S | Proposed | P1 | 12 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224.4 | 118.1 | 200 | 112.2 |  |  |  |  | 1277 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
101244 | 15S | Proposed | P1 | 12 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.2 | 112 | 191 | 103.2 |  |  |  |  | 1393 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 |  | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101245 | 15S | Proposed | P1 | 12 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 39.9 | 16 | 39 | 102.3 |  |  |  |  | 1406 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
101246 | 15S | Proposed | P1 | 12 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | LN | 116.4 | 61.6 | 121 | 96.2 |  |  |  |  | 1582 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | 335699 | 335710 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
101247 | 15S | Proposed | P1 | 12 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 116.4 | 51.9 | 121 | 96.2 |  |  |  |  | 1586 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
101248 | 15S | Proposed | P1 | 12 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 95.4 | 46.3 | 100 | 95.4 |  |  |  |  | 1636 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101249 | 15S | Proposed | P1 | 12 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194.3 | 143 | 199 | 97.6 |  |  |  |  | 1747 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101250 | 15S | Proposed | P1 | 12 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 194.2 | 143 | 199 | 97.6 |  |  |  |  | 1748 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101251 | 15S | Proposed | P1 | 12 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 223.2 | 160.2 | 229 | 97.5 |  |  |  |  | 1824 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  |  | No violation: below Rate A
101252 | 15S | Proposed | P1 | 12 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 194 | 114.9 | 199 | 97.5 |  |  |  |  | 1919 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101253 | 15S | Proposed | P1 | 12 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 109.7 | 84 | 115 | 95.4 |  |  |  |  | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | No violation: below Rate A
101254 | 15S | Proposed | P1 | 12 | 336907 3MIAMI ST 115 336938 3REX BRWN-W! 115 1 | LN | 312.1 | 237.4 | 320 | 97.5 |  |  |  |  | 1992 | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 | 336907 | 336938 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336842 6S.JACKSON! 230 336890 3S.JACKSON! 115 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101255 | 15S | Proposed | P2 | 12 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 103.5 | 55.4 | 108 | 95.8 |  |  |  |  | 2075 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
101256 | 15S | Proposed | P1 | 12 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 290.6 | 210.4 | 278 | 104.5 |  |  |  |  | 2182 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
101257 | 15S | Proposed | P1 | 12 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.2 | 210.4 | 278 | 107.3 |  |  |  |  | 2183 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
101258 | 15S | Proposed | P1 | 12 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 295.4 | 83.1 | 278 | 106.3 |  |  |  |  | 2185 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101259 | 15S | Proposed | P1 | 12 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.7 | 89.7 | 250 | 122.3 |  |  |  |  | 2185 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101260 | 15S | Proposed | P1 | 12 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 209.6 | 79.7 | 219 | 95.7 |  |  |  |  | 2738 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101261 | 15S | Proposed | P1 | 12 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 186.7 | 56.5 | 188 | 99.3 |  |  |  |  | 2738 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101262 | 15S | Proposed | P1 | 12 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 161.4 | 93.7 | 165 | 97.8 |  |  |  |  | 2753 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 |  |  | No violation: below Rate A
101263 | 15S | Proposed | P1 | 12 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 160.3 | 91.6 | 168 | 95.4 |  |  |  |  | 2754 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 |  |  | No violation: below Rate A
101264 | 15S | Proposed | P1 | 12 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 237.9 | 118 | 226 | 105.2 |  |  |  |  | 3899 | 3Wnd: OPEN B$0241 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0241 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101265 | 15S | Proposed | P1 | 12 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | LN | 1174.3 | 618 | 1195 | 98.3 |  |  |  |  | 4696 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | 514908 | 514909 | 2 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 |  |  | No violation: below Rate A
101266 | 15S | Proposed | P1 | 12 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | LN | 1171 | 579.2 | 1195 | 98 |  |  |  |  | 4697 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | 514908 | 514909 | 1 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 |  |  | No violation: below Rate A
101267 | 15S | Proposed | P0 | 13 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.8 | 99.8 | 95 | 105.1 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101268 | 18L | Proposed | P1 | 14 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 311 | 221.8 | 278 | 111.9 |  |  |  |  | 1292 | P1_2-1137 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! |  | SPS: Clarksdale
101269 | 18L | Proposed | P1 | 14 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 307.1 | 221.8 | 278 | 110.5 |  |  |  |  | 1293 | P1_2-1138 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! |  | SPS: Clarksdale
101270 | 18L | Proposed | P1 | 14 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 305.5 | 98.6 | 278 | 109.9 |  |  |  |  | 1297 | P1_2-1142 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
101271 | 18L | Proposed | P1 | 14 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 302.6 | 91.7 | 250 | 121.1 |  |  |  |  | 1297 | P1_2-1142 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
101272 | 18L | Proposed | P1 | 14 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 208.2 | 71.8 | 219 | 95.1 |  |  |  |  | 1814 | P1_2-1664 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 |  |  | No violation: below Rate A
101273 | 18L | Proposed | P1 | 15 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 311 | 221.8 | 278 | 111.9 |  |  |  |  | 316 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
101274 | 18L | Proposed | P1 | 15 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 307.1 | 221.8 | 278 | 110.5 |  |  |  |  | 317 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
101275 | 18L | Proposed | P1 | 15 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 305.5 | 98.6 | 278 | 109.9 |  |  |  |  | 319 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101276 | 18L | Proposed | P1 | 15 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 302.6 | 91.7 | 250 | 121.1 |  |  |  |  | 319 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101277 | 18L | Proposed | P1 | 15 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224.8 | 118.6 | 200 | 112.4 |  |  |  |  | 1671 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
101278 | 18L | Proposed | P1 | 15 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224.8 | 118.6 | 200 | 112.4 |  |  |  |  | 1672 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
101279 | 18L | Proposed | P1 | 15 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 41.2 | 35.2 | 39 | 105.7 |  |  |  |  | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Facility: Radial
101280 | 18L | Proposed | P1 | 15 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 208.2 | 71.8 | 219 | 95.1 |  |  |  |  | 2715 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101281 | 18S | Proposed | P0 | 17 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.6 | 99.6 | 95 | 104.9 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101282 | 18S | Proposed | P1 | 17 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 98.5 | 49.5 | 98 | 100.5 |  |  |  |  | 482 | P1_2-247 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101283 | 18S | Proposed | P1 | 17 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 103.4 | 54.5 | 100 | 103.4 |  |  |  |  | 993 | P1_2-760 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101284 | 18S | Proposed | P1 | 17 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 102 | 53.9 | 100 | 102 |  |  |  |  | 993 | P1_2-760 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101285 | 18S | Proposed | P1 | 17 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 191.4 | 141.9 | 199 | 96.2 |  |  |  |  | 1098 | P1_2-865 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101286 | 18S | Proposed | P1 | 17 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 217.6 | 136.7 | 229 | 95 |  |  |  |  | 1184 | P1_2-951 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! |  |  | No violation: below Rate A
101287 | 18S | Proposed | P1 | 17 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 534 | 318.2 | 561 | 95.2 |  |  |  |  | 1330 | P1_2-1097 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101288 | 18S | Proposed | P1 | 17 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 289.4 | 202.1 | 278 | 104.1 |  |  |  |  | 1367 | P1_2-1134 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
101289 | 18S | Proposed | P1 | 17 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.2 | 202.1 | 278 | 107.3 |  |  |  |  | 1368 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale
101290 | 18S | Proposed | P1 | 17 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 294.2 | 90.3 | 278 | 105.8 |  |  |  |  | 1372 | P1_2-1139 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101291 | 18S | Proposed | P1 | 17 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.7 | 98.2 | 250 | 122.3 |  |  |  |  | 1372 | P1_2-1139 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101292 | 18S | Proposed | P1 | 17 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 136.3 | 18.7 | 115 | 118.5 |  |  |  |  | 1572 | P1_2-1341 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341 |  |  | Contingency: invalid after Albright
101293 | 18S | Proposed | P1 | 17 | 337715 3MILTON 115 337721 3ALBRIGHT 115 1 | LN | 173.4 | 16.4 | 176 | 98.5 |  |  |  |  | 1572 | P1_2-1341 | 337715 | 337721 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341 |  |  | Contingency: invalid after Albright
101294 | 18S | Proposed | P1 | 17 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 234.6 | 114 | 226 | 103.8 |  |  |  |  | 1788 | P1_2-1563 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101295 | 18S | Proposed | P0 | 18 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.6 | 99.6 | 95 | 104.9 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101296 | 18S | Proposed | P1 | 18 | 336554 3BROOKHAVEN! 115 336555 3S.BROOKHAVN 115 1 | LN | 193.6 | 114.7 | 199 | 97.3 |  |  |  |  | 54 | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 | 336554 | 336555 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336558 3VAUGHN+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101297 | 18S | Proposed | P2 | 18 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | LN | 105.7 | 50 | 108 | 97.9 |  |  |  |  | 214 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 337044 | 337045 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | Project Proposed | No violation: below Rate A | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
101298 | 18S | Proposed | P1 | 18 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 534 | 318.2 | 561 | 95.2 |  |  |  |  | 239 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 |  | Project Proposed | No violation: below Rate A | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101299 | 18S | Proposed | P1 | 18 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 289.4 | 202.1 | 278 | 104.1 |  |  |  |  | 321 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
101300 | 18S | Proposed | P1 | 18 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.2 | 202.1 | 278 | 107.3 |  |  |  |  | 322 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
101301 | 18S | Proposed | P1 | 18 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 294.2 | 90.3 | 278 | 105.8 |  |  |  |  | 324 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101302 | 18S | Proposed | P1 | 18 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.7 | 98.2 | 250 | 122.3 |  |  |  |  | 324 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101303 | 18S | Proposed | P1 | 18 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 191.4 | 141.9 | 199 | 96.2 |  |  |  |  | 398 | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336562 8FRANKLIN% 500 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101304 | 18S | Proposed | P1 | 18 | 337804 3MABLVALE-E! 115 337815 3MANN RD 115 1 | LN | 314 | 213.5 | 319 | 98.4 |  |  |  |  | 646 | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 | 337804 | 337815 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 |  |  | No violation: below Rate A
101305 | 18S | Proposed | P2 | 18 | 337815 3MANN RD 115 337816 3LR CHICOT 115 1 | LN | 309.1 | 208.5 | 298 | 103.7 |  |  |  |  | 646 | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 | 337815 | 337816 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 |  | Generation redispatch: Turn on Lynch units
101306 | 18S | Proposed | P2 | 18 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 148.4 | 83.5 | 148 | 100.3 |  |  |  |  | 879 | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338151 5NEWPORT! 161 338173 5NEWPORT IND 161 1 |  | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101307 | 18S | Proposed | P1 | 18 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 141 | 83.5 | 148 | 95.3 |  |  |  |  | 894 | 338171 5CASH 161 338172 5NEWPORT AB 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338171 5CASH 161 338172 5NEWPORT AB 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101308 | 18S | Proposed | P1 | 18 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 146.8 | 83.5 | 148 | 99.2 |  |  |  |  | 895 | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | 338172 5NEWPORT AB 161 338173 5NEWPORT IND 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
101309 | 18S | Proposed | P1 | 18 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 98.4 | 49.5 | 98 | 100.4 |  |  |  |  | 1336 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334307 4BUNA! 138 334308 4JNE EVA 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101310 | 18S | Proposed | P1 | 18 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 103.9 | 49.5 | 98 | 106 |  |  |  |  | 1337 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101311 | 18S | Proposed | P1 | 18 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 226.4 | 121.2 | 200 | 113.2 |  |  |  |  | 1702 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
101312 | 18S | Proposed | P1 | 18 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 226.4 | 121.2 | 200 | 113.2 |  |  |  |  | 1703 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
101313 | 18S | Proposed | P1 | 18 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 42.7 | 17.3 | 39 | 109.5 |  |  |  |  | 1833 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
101314 | 18S | Proposed | P1 | 18 | 335401 2LINE-281_TP69.0 335403 2LINE-247_TP69.0 1 | LN | 38.8 | 13.9 | 39 | 99.6 |  |  |  |  | 1833 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335401 | 335403 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  |  | No violation: below Rate A
101315 | 18S | Proposed | P1 | 18 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | LN | 121.6 | 69.2 | 121 | 100.5 |  |  |  |  | 2008 | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 | 335699 | 335710 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335712 2LOCKHART 69.0 335713 2COLY! 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
101316 | 18S | Proposed | P1 | 18 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 121.7 | 60 | 121 | 100.5 |  |  |  |  | 2012 | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335713 2COLY! 69.0 335718 2POLYFORM 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
101317 | 18S | Proposed | P1 | 18 | 335699 2HARELSON! 69.0 335720 2GLORIA! 69.0 1 | LN | 120 | 60 | 121 | 99.2 |  |  |  |  | 2017 | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 | 335699 | 335720 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335718 2POLYFORM 69.0 335719 2DENHAM_SP 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
101318 | 18S | Proposed | P1 | 18 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 103.4 | 54.5 | 100 | 103.4 |  |  |  |  | 2062 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101319 | 18S | Proposed | P1 | 18 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 102 | 53.9 | 100 | 102 |  |  |  |  | 2062 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101320 | 18S | Proposed | P1 | 18 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 191.5 | 141.9 | 199 | 96.2 |  |  |  |  | 2172 | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 336130 8BOGALUS 500 336131 6ADMSCRK% 230 1 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101321 | 18S | Proposed | P1 | 18 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 217.6 | 136.7 | 229 | 95 |  |  |  |  | 2247 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336284 3WSTWGO! 115 1 |  |  | No violation: below Rate A
101322 | 18S | Proposed | P1 | 18 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 226.5 | 162.5 | 229 | 98.9 |  |  |  |  | 2248 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 336280 39MILE% 115 336286 3HARVEY2 115 1 |  |  | No violation: below Rate A
101323 | 18S | Proposed | P1 | 18 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.2 | 35.2 | 39 | 95.4 |  |  |  |  | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Facility: Radial
101324 | 18S | Proposed | P1 | 18 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 1 | LN | 78.2 | 18.1 | 80 | 97.7 |  |  |  |  | 2588 | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 | 337371 | 337372 | 1 |  | 115 | 115 | 351 | EES | 338 | DERS | 337371 3VIENNA_LA! 115 337372 3RUSTON 115 2 |  | Project Horizon | No violation: below Rate A | 13-ELL-005-HZ | 2020-06-01 | Vienna to Ruston Frazier Road 115 kV Line 173: Upgrade metering CTs at Ruston
101325 | 18S | Proposed | P1 | 18 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 234.6 | 114 | 226 | 103.8 |  |  |  |  | 3943 | 3Wnd: OPEN B$0231 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0231 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101326 | 18S | Proposed | P1 | 18 | 514880 NORTWST7 345 991455 NORTWST2 1.00 1 | TR | 483.9 | 341.3 | 493 | 98.1 |  |  |  |  | 4743 | 3Wnd: OPEN B$1456 NORTWST3 1 | 514880 | 991455 | 1 |  | 345 | 1 | 524 | OKGE | 524 | OKGE | 3Wnd: OPEN B$1456 NORTWST3 1 |  |  | No violation: below Rate A
101327 | 18S | Proposed | P1 | 18 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | LN | 1277.7 | 672.3 | 1195 | 106.9 |  |  |  |  | 4748 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | 514908 | 514909 | 2 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 1
101328 | 18S | Proposed | P1 | 18 | 514908 ARCADIA7 345 514909 REDBUD 7 345 1 | LN | 1274.3 | 630.1 | 1195 | 106.6 |  |  |  |  | 4749 | 514908 ARCADIA7 345 514909 REDBUD 7 345 2 | 514908 | 514909 | 1 |  | 345 | 345 | 524 | OKGE | 524 | OKGE | 514908 ARCADIA7 345 514909 REDBUD 7 345 2
101329 | 18S | Proposed | P0 | 19 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.6 | 99.6 | 95 | 104.9 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101330 | 18W | Proposed | P1 | 20 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 93.1 | 57.4 | 98 | 95 |  |  |  |  | 464 | P1_2-246 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-246 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101331 | 18W | Proposed | P1 | 20 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.3 | 57.4 | 98 | 116.6 |  |  |  |  | 465 | P1_2-247 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101332 | 18W | Proposed | P1 | 20 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.8 |  |  |  |  | 717 | P1_2-500 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101333 | 18W | Proposed | P1 | 20 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 98.5 | 52.5 | 100 | 98.5 |  |  |  |  | 977 | P1_2-761 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101334 | 18W | Proposed | P1 | 20 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 97.2 | 51.8 | 100 | 97.2 |  |  |  |  | 977 | P1_2-761 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101335 | 18W | Proposed | P1 | 20 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 303.1 | 205.6 | 278 | 109 |  |  |  |  | 1353 | P1_2-1137 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! |  | SPS: Clarksdale
101336 | 18W | Proposed | P1 | 20 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 299.6 | 205.6 | 278 | 107.8 |  |  |  |  | 1354 | P1_2-1138 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! |  | SPS: Clarksdale
101337 | 18W | Proposed | P1 | 20 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 303.8 | 100.5 | 278 | 109.3 |  |  |  |  | 1358 | P1_2-1142 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
101338 | 18W | Proposed | P1 | 20 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 303.1 | 96 | 250 | 121.2 |  |  |  |  | 1358 | P1_2-1142 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1142_6CROSSROADS!,6MOONLAKE% |  | SPS: Clarksdale
101339 | 18W | Proposed | P1 | 20 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.6 | 23.8 | 157 | 95.9 |  |  |  |  | 1943 | P1_2-1735 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! |  |  | No violation: below Rate A
101340 | 18W | Proposed | P1 | 21 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 303.1 | 205.6 | 278 | 109 |  |  |  |  | 321 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
101341 | 18W | Proposed | P1 | 21 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 299.6 | 205.6 | 278 | 107.8 |  |  |  |  | 322 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
101342 | 18W | Proposed | P1 | 21 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 303.8 | 100.5 | 278 | 109.3 |  |  |  |  | 324 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101343 | 18W | Proposed | P1 | 21 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 303.1 | 96 | 250 | 121.2 |  |  |  |  | 324 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101344 | 18W | Proposed | P1 | 21 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 103.8 | 57.4 | 98 | 105.9 |  |  |  |  | 1333 | 334305 4BUNASW 138 334307 4BUNA! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334305 4BUNASW 138 334307 4BUNA! 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101345 | 18W | Proposed | P1 | 21 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.1 | 57.4 | 98 | 116.5 |  |  |  |  | 1334 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334307 4BUNA! 138 334308 4JNE EVA 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101346 | 18W | Proposed | P1 | 21 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 120.6 | 57.4 | 98 | 123.1 |  |  |  |  | 1335 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area |  | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101347 | 18W | Proposed | P1 | 21 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 224.6 | 118.3 | 200 | 112.3 |  |  |  |  | 1700 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
101348 | 18W | Proposed | P1 | 21 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 224.6 | 118.3 | 200 | 112.3 |  |  |  |  | 1701 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
101349 | 18W | Proposed | P1 | 21 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.8 |  |  |  |  | 1714 | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335211 2LK_CH_BULK!69.0 335217 2CHLOMAL! 69.0 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101350 | 18W | Proposed | P1 | 21 | 335400 2FIVE_PTS! 69.0 335401 2LINE-281_TP69.0 1 | LN | 39.1 | 13.4 | 39 | 100.2 |  |  |  |  | 1831 | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 | 335400 | 335401 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335404 2LEBLANC 69.0 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 11-EGL-017-CP | 2019-06-01 | Upgrade Five Points-Line 281 Tap-Line 247 Tap 69 kV
101351 | 18W | Proposed | P1 | 21 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 98.5 | 52.5 | 100 | 98.5 |  |  |  |  | 2061 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101352 | 18W | Proposed | P1 | 21 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 97.2 | 51.8 | 100 | 97.2 |  |  |  |  | 2061 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 |  | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
101353 | 18W | Proposed | P1 | 21 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 346.6 | 335.7 | 360 | 96.3 |  |  |  |  | 3963 | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 360612 8BENTON MS 500 360614 8MAGNOL CC2 500 2 |  |  | Facility: GSU
101354 | 23S | Proposed | P0 | 23 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.5 | 18.5 | 19 | 97.6 |  |  |  |  | 0 | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101355 | 23S | Proposed | P0 | 23 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.2 | 37.2 | 39 | 95.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
101356 | 23S | Proposed | P0 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 109.1 | 109.1 | 112 | 97.4 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101357 | 23S | Proposed | P0 | 23 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.5 | 99.5 | 95 | 104.8 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101358 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.7 |  |  |  |  | 112 | G-337041-1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | G-337041-1 |  |  | Facility: Radial
101359 | 23S | Proposed | P1 | 23 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.6 | 52.6 | 56 | 95.8 |  |  |  |  | 814 | P1_2-565 | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! |  |  | No violation: below Rate A
101360 | 23S | Proposed | P1 | 23 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.7 | 52.6 | 56 | 95.8 |  |  |  |  | 815 | P1_2-566 | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% |  |  | No violation: below Rate A
101361 | 23S | Proposed | P1 | 23 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 2 | LN | 74.9 | 20.8 | 72 | 104 |  |  |  |  | 829 | P1_2-581 | 335408 | 335427 | 2 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-581
101362 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.7 |  |  |  |  | 1357 | P1_2-1112 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1112 |  |  | Facility: Radial
101363 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.1 | 112 | 99.7 |  |  |  |  | 1360 | P1_2-1115 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1115_6ANDRUS%,3BAGBY! |  |  | Facility: Radial
101364 | 23S | Proposed | P1 | 23 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 288.2 | 200.1 | 278 | 103.7 |  |  |  |  | 1379 | P1_2-1134 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1134 |  | SPS: Clarksdale
101365 | 23S | Proposed | P1 | 23 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.4 | 200.1 | 278 | 107.4 |  |  |  |  | 1380 | P1_2-1135 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! |  | SPS: Clarksdale
101366 | 23S | Proposed | P1 | 23 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 292.8 | 91.3 | 278 | 105.3 |  |  |  |  | 1384 | P1_2-1139 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101367 | 23S | Proposed | P1 | 23 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.8 | 100.6 | 250 | 122.3 |  |  |  |  | 1384 | P1_2-1139 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1139 |  | SPS: Clarksdale
101368 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.6 |  |  |  |  | 1495 | P1_2-1250 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1250 |  |  | Facility: Radial
101369 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.1 | 109.1 | 112 | 98.3 |  |  |  |  | 1526 | P1_2-1281 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1281 |  |  | Facility: Radial
101370 | 23S | Proposed | P1 | 23 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.1 | 109.1 | 112 | 98.3 |  |  |  |  | 1529 | P1_2-1284 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1284 |  |  | Facility: Radial
101371 | 23S | Proposed | P1 | 23 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 153.3 | 110.1 | 159 | 96.4 |  |  |  |  | 1555 | P1_2-1311 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101372 | 23S | Proposed | P1 | 23 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 229.3 | 158.5 | 239 | 95.9 |  |  |  |  | 1577 | P1_2-1334 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1334 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101373 | 23S | Proposed | P1 | 23 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 233.3 | 158.5 | 239 | 97.6 |  |  |  |  | 1578 | P1_2-1335 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1335 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101374 | 23S | Proposed | P1 | 23 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 145.1 | 17.6 | 115 | 126.2 |  |  |  |  | 1584 | P1_2-1341 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341 |  |  | Contingency: invalid after Albright
101375 | 23S | Proposed | P1 | 23 | 337715 3MILTON 115 337721 3ALBRIGHT 115 1 | LN | 185.2 | 21.1 | 176 | 105.2 |  |  |  |  | 1584 | P1_2-1341 | 337715 | 337721 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341 |  |  | Contingency: invalid after Albright
101376 | 23S | Proposed | P1 | 23 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 153.3 | 110.1 | 159 | 96.4 |  |  |  |  | 1591 | P1_2-1348 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101377 | 23S | Proposed | P1 | 23 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 229.4 | 104.5 | 226 | 101.5 |  |  |  |  | 1800 | P1_2-1563 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101378 | 23S | Proposed | P1 | 23 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.9 | 48.6 | 157 | 96.1 |  |  |  |  | 1969 | P1_2-1732 | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1732 |  |  | No violation: below Rate A
101379 | 23S | Proposed | P0 | 24 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.5 | 18.5 | 19 | 97.6 |  |  |  |  | 0 | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101380 | 23S | Proposed | P0 | 24 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.2 | 37.2 | 39 | 95.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
101381 | 23S | Proposed | P0 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 109.1 | 109.1 | 112 | 97.4 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101382 | 23S | Proposed | P0 | 24 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.5 | 99.5 | 95 | 104.8 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101383 | 23S | Proposed | P1 | 24 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 288.2 | 200.1 | 278 | 103.7 |  |  |  |  | 324 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 |  | SPS: Clarksdale
101384 | 23S | Proposed | P1 | 24 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 298.4 | 200.1 | 278 | 107.4 |  |  |  |  | 325 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 |  | SPS: Clarksdale
101385 | 23S | Proposed | P1 | 24 | 337098 3CLRKD MUNI! 115 337099 3CLARKSDALE! 115 1 | LN | 292.8 | 91.3 | 278 | 105.3 |  |  |  |  | 327 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337099 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101386 | 23S | Proposed | P1 | 24 | 337098 3CLRKD MUNI! 115 337100 6CROSSROADS! 230 1 | TR | 305.8 | 100.6 | 250 | 122.3 |  |  |  |  | 327 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | 337098 | 337100 | 1 |  | 230 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 |  | SPS: Clarksdale
101387 | 23S | Proposed | P2 | 24 | 337126 3BATESVILLE! 115 337135 3SARDIS 115 1 | LN | 129.3 | 39.5 | 136 | 95.1 |  |  |  |  | 349 | 337138 3HERNANDO 115 337139 3GETWELL! 115 1 | 337126 | 337135 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 337138 3HERNANDO 115 337139 3GETWELL! 115 1 |  |  | No violation: below Rate A
101388 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.7 |  |  |  |  | 387 | Unit:337041 1ANDRUS U1 24.0 Id:1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | Unit:337041 1ANDRUS U1 24.0 Id:1 |  |  | Facility: Radial
101389 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.1 | 112 | 99.7 |  |  |  |  | 413 | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337040 6ANDRUS% 230 337594 6BAGBY 230 1 |  |  | Facility: Radial
101390 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.3 | 109.1 | 112 | 98.5 |  |  |  |  | 492 | 337579 3MONTCELO.E! 115 338656 3LACEY# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337579 3MONTCELO.E! 115 338656 3LACEY# 115 1 |  |  | Facility: Radial
101391 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.2 | 109.1 | 112 | 98.4 |  |  |  |  | 496 | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 337590 3HAMBURG 115 1 |  |  | Facility: Radial
101392 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.2 | 109.1 | 112 | 98.4 |  |  |  |  | 497 | 337581 3CROSSETT.N! 115 338640 3CROSSETT.X# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337581 3CROSSETT.N! 115 338640 3CROSSETT.X# 115 1 |  |  | Facility: Radial
101393 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.1 | 109.1 | 112 | 99.2 |  |  |  |  | 499 | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337583 3CROSSETT.S 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
101394 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.7 |  |  |  |  | 500 | 337590 3HAMBURG 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337590 3HAMBURG 115 338644 3MIST# 115 1 |  |  | Facility: Radial
101395 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.6 | 109.1 | 112 | 99.6 |  |  |  |  | 501 | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
101396 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.6 | 109.1 | 112 | 98.7 |  |  |  |  | 502 | 337591 3MONTROSE 115 338644 3MIST# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337591 3MONTROSE 115 338644 3MIST# 115 1 |  |  | Facility: Radial
101397 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.1 | 112 | 99.7 |  |  |  |  | 503 | 337592 3BAGBY! 115 337594 6BAGBY 230 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 337594 6BAGBY 230 1 |  |  | Facility: Radial
101398 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.7 | 109.1 | 112 | 99.7 |  |  |  |  | 506 | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337592 3BAGBY! 115 338641 3MONTROSE.E# 115 1 |  |  | Facility: Radial
101399 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.3 | 109.1 | 112 | 98.5 |  |  |  |  | 537 | 337620 3WOODWARD% 115 338660 3PINEBERGEN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337620 3WOODWARD% 115 338660 3PINEBERGEN# 115 1 |  |  | Facility: Radial
101400 | 23S | Proposed | P1 | 24 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 153.3 | 110.1 | 159 | 96.4 |  |  |  |  | 555 | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337643 8SHERIDAN% 500 337763 8MAGNETCOVE% 500 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101401 | 23S | Proposed | P1 | 24 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 229.3 | 158.5 | 239 | 95.9 |  |  |  |  | 600 | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 1 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101402 | 23S | Proposed | P1 | 24 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 233.3 | 158.5 | 239 | 97.6 |  |  |  |  | 601 | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 2 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337686 3ARKLAHOMA% 115 337740 3HS EHV-E! 115 2 |  | Project Approved | No violation: below Rate A | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101403 | 23S | Proposed | P1 | 24 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 153.3 | 110.1 | 159 | 96.4 |  |  |  |  | 638 | 337753 8HS EHV% 500 337763 8MAGNETCOVE% 500 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337753 8HS EHV% 500 337763 8MAGNETCOVE% 500 1 |  | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101404 | 23S | Proposed | P2 | 24 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 161.1 | 110.1 | 159 | 101.3 |  |  |  |  | 641 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
101405 | 23S | Proposed | P2 | 24 | 337801 3WOODLAWN% 115 337802 3BAUXITE 115 1 | LN | 159.7 | 51.7 | 159 | 100.4 |  |  |  |  | 641 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337801 | 337802 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 14-EAI-016-HZ | 2022-06-01 | Woodlawn to Bauxite 115 kV line - Upgrade line
101406 | 23S | Proposed | P1 | 24 | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 | LN | 285.7 | 205.1 | 298 | 95.9 |  |  |  |  | 644 | 337799 3MABLVALE-W! 115 337831 3LAWSON RD 115 1 | 337818 | 337821 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337799 3MABLVALE-W! 115 337831 3LAWSON RD 115 1 |  |  | No violation: below Rate A
101407 | 23S | Proposed | P1 | 24 | 337815 3MANN RD 115 337816 3LR CHICOT 115 1 | LN | 288.7 | 192.4 | 298 | 96.9 |  |  |  |  | 652 | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 | 337815 | 337816 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337804 3MABLVALE-E! 115 337820 3ALEXANDR AR 115 1 |  |  | No violation: below Rate A
101408 | 23S | Proposed | P1 | 24 | 337799 3MABLVALE-W! 115 337831 3LAWSON RD 115 1 | LN | 254.1 | 174 | 266 | 95.5 |  |  |  |  | 664 | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 | 337799 | 337831 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337818 3LR.S! 115 337821 3ROCK CREEK 115 1 |  |  | No violation: below Rate A
101409 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.3 | 109.1 | 112 | 98.5 |  |  |  |  | 979 | 338640 3CROSSETT.X# 115 338656 3LACEY# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 338640 3CROSSETT.X# 115 338656 3LACEY# 115 1 |  |  | Facility: Radial
101410 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 111.2 | 109.1 | 112 | 99.3 |  |  |  |  | 1055 | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337414 3STERL2% 115 338642 3MERIDIAN# 115 1 |  |  | Facility: Radial
101411 | 23S | Proposed | P1 | 24 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 110.5 | 109.1 | 112 | 98.6 |  |  |  |  | 1058 | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 337443 3N_BASTROP! 115 337581 3CROSSETT.N! 115 1 |  |  | Facility: Radial
101412 | 23S | Proposed | P1 | 24 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 94.1 | 44.5 | 98 | 96.1 |  |  |  |  | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Target Area | No violation: below Rate A | Rayburn-Mill Creek | TBD | Upgrade Rayburn-Mill Creek 138 kV
101413 | 23S | Proposed | P1 | 24 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | TR | 226.1 | 120.8 | 200 | 113 |  |  |  |  | 1722 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | 335136 | 335137 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 |  | Reduce PPG Plant
101414 | 23S | Proposed | P1 | 24 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 1 | TR | 226.1 | 120.8 | 200 | 113 |  |  |  |  | 1723 | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 | 335136 | 335137 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | 335136 6PPG! 230 335137 2PPG_GEN 69.0 2 |  | Reduce PPG Plant
101415 | 23S | Proposed | P1 | 24 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.6 | 52.6 | 56 | 95.8 |  |  |  |  | 1838 | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335380 4MEAUX! 138 335381 6MEAUX! 230 1 |  |  | No violation: below Rate A
101416 | 23S | Proposed | P1 | 24 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.7 | 52.6 | 56 | 95.8 |  |  |  |  | 2569 | 335381 6MEAUX! 230 500776 SELLRD6 230 1 | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 335381 6MEAUX! 230 500776 SELLRD6 230 1 |  |  | No violation: below Rate A
101417 | 23S | Proposed | P1 | 24 | 380008 8VOGTLE 500 380009 8W MCINTOSH 500 1 | LN | 2464.6 | 1829.2 | 2439 | 101 |  |  |  |  | 2940 | 380018 8SCHERER + 500 383008 8HANCOCK CO 500 1 | 380008 | 380009 | 1 |  | 500 | 500 | 346 | SOCO | 346 | SOCO | 380018 8SCHERER + 500 383008 8HANCOCK CO 500 1
101418 | 23S | Proposed | P1 | 24 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 229.4 | 104.5 | 226 | 101.5 |  |  |  |  | 4024 | 3Wnd: OPEN B$0054 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | 3Wnd: OPEN B$0054 1 |  |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
101419 | 23S | Proposed | P1 | 24 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | LN | 1685.1 | 1301.4 | 1732.1 | 97.3 |  |  |  |  | 4051 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 360065 | 360081 | 1 |  | 500 | 500 | 347 | TVA | 347 | TVA | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 |  |  | No violation: below Rate A
101420 | 23S | Proposed | P1 | 24 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | LN | 1816.1 | 1301.4 | 1732.1 | 104.8 |  |  |  |  | 4058 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | 360065 | 360081 | 1 |  | 500 | 500 | 347 | TVA | 347 | TVA | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1
101421 | 23S | Proposed | P1 | 24 | 360581 8PIN HOOK TN 500 990204 1.00 1 | TR | 1318.5 | 1011.8 | 1253.7 | 105.2 |  |  |  |  | 4071 | 3Wnd: OPEN B$0066 1 | 360581 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 3Wnd: OPEN B$0066 1
101422 | 23S | Proposed | P1 | 24 | 514880 NORTWST7 345 991461 NORTWST2 1.00 1 | TR | 486.3 | 346.4 | 493 | 98.6 |  |  |  |  | 4853 | 3Wnd: OPEN B$1462 NORTWST3 1 | 514880 | 991461 | 1 |  | 345 | 1 | 524 | OKGE | 524 | OKGE | 3Wnd: OPEN B$1462 NORTWST3 1 |  |  | No violation: below Rate A
101423 | 23S | Proposed | P0 | 25 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.5 | 18.5 | 19 | 97.6 |  |  |  |  | 0 | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101424 | 23S | Proposed | P0 | 25 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.2 | 37.2 | 39 | 95.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | Facility: Radial
101425 | 23S | Proposed | P0 | 25 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 109.1 | 109.1 | 112 | 97.4 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101426 | 23S | Proposed | P0 | 25 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 99.5 | 99.5 | 95 | 104.8 |  |  |  |  | 0 | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case ** |  |  | Facility: Radial
101427 | 18S | Approved | P3 | 31 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 131.5 | 75.1 | 115 | 114.4 |  |  |  |  | 2528 | P1_2-834_3GMEADW!,3BARATA!+G_G3TECHE! ID 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-834_3GMEADW!,3BARATA! | G_G3TECHE! ID 1 | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
101428 | 18S | Approved | P3 | 31 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | LN | 113.2 | 56.3 | 115 | 98.5 |  |  |  |  | 2528 | P1_2-834_3GMEADW!,3BARATA!+G_G3TECHE! ID 1 | 336080 | 336081 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-834_3GMEADW!,3BARATA! | G_G3TECHE! ID 1 | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
101429 | 18S | Approved | P3 | 31 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 131.1 | 75.1 | 115 | 114 |  |  |  |  | 2544 | P1_2-834_3GMEADW!,3BARATA!+G_HOUMA 3 ID 1 | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-834_3GMEADW!,3BARATA! | G_HOUMA 3 ID 1 | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
101430 | 18S | Approved | P3 | 31 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | LN | 113.4 | 56.3 | 115 | 98.6 |  |  |  |  | 2544 | P1_2-834_3GMEADW!,3BARATA!+G_HOUMA 3 ID 1 | 336080 | 336081 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-834_3GMEADW!,3BARATA! | G_HOUMA 3 ID 1 | Project Proposed | No violation: below Rate A | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
101431 | 18S | Approved | P3 | 31 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 37.1 | 35.6 | 39 | 95.2 |  |  |  |  | 3277 | P1_2-1178_3WINNSBORO!,3SWARTZ!+G_1NM G1 ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1178_3WINNSBORO!,3SWARTZ! | G_1NM G1 ID 1 |  | Facility: Radial
101432 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 197.3 | 75 | 219 | 90.1 |  |  |  |  | 3750 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+G_1WAT U3! ID 1 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101433 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 201.7 | 75 | 219 | 92.1 |  |  |  |  | 3771 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+G_1GGNS U1 ID 1 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101434 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 214.2 | 75 | 219 | 97.8 |  |  |  |  | 3781 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+106 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1ANDRUS U1 ID 1 |  | No violation: below Rate A
101435 | 18S | Approved | P3 | 31 | 337621 3WATSON CHPL 115 337622 3PINEBLUF.S! 115 1 | LN | 176.6 | 37.9 | 195 | 90.6 |  |  |  |  | 3781 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+106 | 337621 | 337622 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1ANDRUS U1 ID 1 |  | No violation: below Rate A
101436 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 201.4 | 75 | 219 | 91.9 |  |  |  |  | 3829 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+G_1L&D2 U1 ID 1 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1L&D2 U1 ID 1 |  | No violation: below Rate A
101437 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 200.1 | 75 | 219 | 91.4 |  |  |  |  | 3830 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+G_1L&D2 U2 ID 1 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1L&D2 U2 ID 1 |  | No violation: below Rate A
101438 | 18S | Approved | P3 | 31 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 201.4 | 75 | 219 | 91.9 |  |  |  |  | 3831 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+G_1L&D2 U3 ID 1 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1L&D2 U3 ID 1 |  | No violation: below Rate A
101439 | 18S | Approved | P3 | 31 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 105.4 | 104.3 | 112 | 94.1 |  |  |  |  | 4489 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+106 | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1313_8SHERIDAN%,8WHT BLUFF% | G_1ANDRUS U1 ID 1 |  | Facility: Radial
101440 | 18S | Approved | P3 | 31 | 337930 3MAYFLOWER% 115 337931 3MORGAN 115 1 | LN | 254.7 | 232.7 | 283 | 90 |  |  |  |  | 4534 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1M.HYD U1 ID 1 | 337930 | 337931 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1313_8SHERIDAN%,8WHT BLUFF% | G_1M.HYD U1 ID 1 |  | No violation: below Rate A
101441 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.8 | 39.2 | 106 | 90.4 |  |  |  |  | 4619 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1NM G1 ID 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1NM G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101442 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.4 | 39.2 | 106 | 90 |  |  |  |  | 4620 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1STFRG1 ID 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1STFRG1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101443 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.6 | 39.2 | 106 | 90.2 |  |  |  |  | 4726 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_3CLRKD MUNI! ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101444 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 107.9 | 46.2 | 106 | 101.8 |  |  |  |  | 4727 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101445 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.2 | 43.3 | 106 | 98.3 |  |  |  |  | 4727 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101446 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 98.7 | 40 | 106 | 93.1 |  |  |  |  | 4727 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101447 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.3 | 39.2 | 106 | 90.8 |  |  |  |  | 4727 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101448 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 107.9 | 46.2 | 106 | 101.8 |  |  |  |  | 4728 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101449 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.2 | 43.3 | 106 | 98.3 |  |  |  |  | 4728 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101450 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 98.7 | 40 | 106 | 93.1 |  |  |  |  | 4728 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101451 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.3 | 39.2 | 106 | 90.8 |  |  |  |  | 4728 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101452 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 107.9 | 46.2 | 106 | 101.8 |  |  |  |  | 4729 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101453 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.2 | 43.3 | 106 | 98.3 |  |  |  |  | 4729 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101454 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 98.7 | 40 | 106 | 93.1 |  |  |  |  | 4729 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101455 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.3 | 39.2 | 106 | 90.8 |  |  |  |  | 4729 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101456 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 107.9 | 46.2 | 106 | 101.8 |  |  |  |  | 4730 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+112 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101457 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.2 | 43.3 | 106 | 98.3 |  |  |  |  | 4730 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+112 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101458 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 98.7 | 40 | 106 | 93.1 |  |  |  |  | 4730 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+112 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101459 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.3 | 39.2 | 106 | 90.8 |  |  |  |  | 4730 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+112 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101460 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96 | 39.2 | 106 | 90.5 |  |  |  |  | 4731 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101461 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.4 | 46.2 | 106 | 102.3 |  |  |  |  | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101462 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.7 | 43.3 | 106 | 98.8 |  |  |  |  | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101463 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 99.2 | 40 | 106 | 93.6 |  |  |  |  | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101464 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.8 | 39.2 | 106 | 91.3 |  |  |  |  | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101465 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 110.1 | 46.2 | 106 | 103.9 |  |  |  |  | 4766 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101466 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 106.4 | 43.3 | 106 | 100.4 |  |  |  |  | 4766 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101467 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 100.9 | 40 | 106 | 95.2 |  |  |  |  | 4766 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101468 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 98.5 | 39.2 | 106 | 92.9 |  |  |  |  | 4766 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101469 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108 | 46.2 | 106 | 101.9 |  |  |  |  | 4768 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101470 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 104.3 | 43.3 | 106 | 98.4 |  |  |  |  | 4768 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101471 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 98.8 | 40 | 106 | 93.2 |  |  |  |  | 4768 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101472 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 96.3 | 39.2 | 106 | 90.9 |  |  |  |  | 4768 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101473 | 18S | Approved | P3 | 31 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.4 | 46.2 | 106 | 103.2 |  |  |  |  | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101474 | 18S | Approved | P3 | 31 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 105.6 | 43.3 | 106 | 99.7 |  |  |  |  | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101475 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 100.1 | 40 | 106 | 94.5 |  |  |  |  | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101476 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 97.7 | 39.2 | 106 | 92.1 |  |  |  |  | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101477 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.7 | 39.2 | 106 | 90.2 |  |  |  |  | 4789 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+171 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101478 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.7 | 39.2 | 106 | 90.2 |  |  |  |  | 4790 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+172 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101479 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.7 | 39.2 | 106 | 90.2 |  |  |  |  | 4791 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+173 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101480 | 18S | Approved | P3 | 31 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | LN | 95.6 | 39.2 | 106 | 90.2 |  |  |  |  | 4792 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+174 | 337964 | 338741 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
101481 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 229.5 | 107.4 | 226 | 101.6 |  |  |  |  | 5326 | P1_2-1563_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1NM G1 ID 1
101482 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 235.5 | 107.4 | 226 | 104.2 |  |  |  |  | 5471 | P1_2-1563_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1PLUM PT U1 ID 1
101483 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 231.8 | 107.4 | 226 | 102.6 |  |  |  |  | 5492 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 1
101484 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 231.8 | 107.4 | 226 | 102.6 |  |  |  |  | 5493 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 2
101485 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 231.8 | 107.4 | 226 | 102.6 |  |  |  |  | 5494 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 1
101486 | 18S | Approved | P3 | 31 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 231.8 | 107.4 | 226 | 102.6 |  |  |  |  | 5495 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 2
101487 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.7 | 177.6 | 225 | 91.9 |  |  |  |  | 6034 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1BCAJUN2_U1% ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1BCAJUN2_U1% ID 1 |  | No violation: below Rate A
101488 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 203.4 | 45.8 | 225 | 90.4 |  |  |  |  | 6034 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1BCAJUN2_U1% ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1BCAJUN2_U1% ID 1 |  | No violation: below Rate A
101489 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.7 | 177.6 | 225 | 91.9 |  |  |  |  | 6036 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1BCAJUN2_U3% ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1BCAJUN2_U3% ID 1 |  | No violation: below Rate A
101490 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 203.4 | 45.8 | 225 | 90.4 |  |  |  |  | 6036 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1BCAJUN2_U3% ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1BCAJUN2_U3% ID 1 |  | No violation: below Rate A
101491 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 204.2 | 45.8 | 225 | 90.8 |  |  |  |  | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 |  | No violation: below Rate A
101492 | 18S | Approved | P3 | 31 | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | LN | 207.9 | 38.2 | 225 | 92.4 |  |  |  |  | 6101 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303134 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101493 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 210.7 | 177.6 | 225 | 93.7 |  |  |  |  | 6101 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101494 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 215.9 | 45.8 | 225 | 95.9 |  |  |  |  | 6101 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101495 | 18S | Approved | P3 | 31 | 303134 4E_OPELUSAS! 138 335454 4COLTON 138 1 | LN | 205.4 | 38.2 | 225 | 91.3 |  |  |  |  | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303134 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101496 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 212.5 | 177.6 | 225 | 94.4 |  |  |  |  | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101497 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 203.6 | 169.1 | 225 | 90.5 |  |  |  |  | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101498 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 213.4 | 45.8 | 225 | 94.8 |  |  |  |  | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101499 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.2 | 177.6 | 225 | 91.6 |  |  |  |  | 6108 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1SOXY U1! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1SOXY U1! ID 1 |  | No violation: below Rate A
101500 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.7 | 177.6 | 225 | 92.3 |  |  |  |  | 6113 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GYP U3! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GYP U3! ID 1 |  | No violation: below Rate A
101501 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 205.8 | 45.8 | 225 | 91.4 |  |  |  |  | 6113 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GYP U3! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GYP U3! ID 1 |  | No violation: below Rate A
101502 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.8 | 177.6 | 225 | 91.5 |  |  |  |  | 6114 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GYP U1! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GYP U1! ID 1 |  | No violation: below Rate A
101503 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.9 | 177.6 | 225 | 92 |  |  |  |  | 6115 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GYP U2! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GYP U2! ID 1 |  | No violation: below Rate A
101504 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 204.3 | 45.8 | 225 | 90.8 |  |  |  |  | 6115 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GYP U2! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GYP U2! ID 1 |  | No violation: below Rate A
101505 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.3 | 177.6 | 225 | 91.2 |  |  |  |  | 6116 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL6 CT1 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL6 CT1 ID 1 |  | No violation: below Rate A
101506 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.3 | 177.6 | 225 | 91.2 |  |  |  |  | 6117 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL6 CT2 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL6 CT2 ID 1 |  | No violation: below Rate A
101507 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.4 | 177.6 | 225 | 91.3 |  |  |  |  | 6118 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL6 ST1 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL6 ST1 ID 1 |  | No violation: below Rate A
101508 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 208.9 | 177.6 | 225 | 92.8 |  |  |  |  | 6119 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101509 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 207.7 | 45.8 | 225 | 92.3 |  |  |  |  | 6119 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101510 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 209 | 177.6 | 225 | 92.9 |  |  |  |  | 6120 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101511 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 207.9 | 45.8 | 225 | 92.4 |  |  |  |  | 6120 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101512 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.5 | 177.6 | 225 | 91.3 |  |  |  |  | 6122 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1MICH U2! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1MICH U2! ID 1 |  | No violation: below Rate A
101513 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.5 | 177.6 | 225 | 92.2 |  |  |  |  | 6123 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1MICH U3! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1MICH U3! ID 1 |  | No violation: below Rate A
101514 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 205.2 | 45.8 | 225 | 91.2 |  |  |  |  | 6123 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1MICH U3! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1MICH U3! ID 1 |  | No violation: below Rate A
101515 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.1 | 177.6 | 225 | 92 |  |  |  |  | 6125 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GGNS U1 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101516 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 204.8 | 45.8 | 225 | 91 |  |  |  |  | 6125 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1GGNS U1 ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101517 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211 | 177.6 | 225 | 93.8 |  |  |  |  | 6212 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 |  | No violation: below Rate A
101518 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.6 | 177.6 | 225 | 91.4 |  |  |  |  | 6213 | P1_2-1654_COUGH 4!,PLAISAN4!+G_TECHE_BS! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_TECHE_BS! ID 1 |  | No violation: below Rate A
101519 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.8 | 177.6 | 225 | 91.9 |  |  |  |  | 6221 | P1_2-1654_COUGH 4!,PLAISAN4!+G_HARGIS1 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_HARGIS1 ID 1 |  | No violation: below Rate A
101520 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.8 | 177.6 | 225 | 91.9 |  |  |  |  | 6222 | P1_2-1654_COUGH 4!,PLAISAN4!+G_HARGIS2 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_HARGIS2 ID 1 |  | No violation: below Rate A
101521 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 208.7 | 177.6 | 225 | 92.7 |  |  |  |  | 6223 | P1_2-1654_COUGH 4!,PLAISAN4!+G_BONIN2 ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_BONIN2 ID 1 |  | No violation: below Rate A
101522 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 205.3 | 177.6 | 225 | 91.3 |  |  |  |  | 6226 | P1_2-1654_COUGH 4!,PLAISAN4!+G_MRGNCTY4 ID 4 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_MRGNCTY4 ID 4 |  | No violation: below Rate A
101523 | 18S | Approved | P3 | 31 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 202.5 | 45.8 | 225 | 90 |  |  |  |  | 6227 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 |  | No violation: below Rate A
101524 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 230.7 | 86.4 | 204 | 113.1 |  |  |  |  | 6280 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101525 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 207.7 | 63.3 | 188 | 110.5 |  |  |  |  | 6280 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101526 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 230.7 | 86.4 | 204 | 113.1 |  |  |  |  | 6281 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101527 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 207.7 | 63.3 | 188 | 110.5 |  |  |  |  | 6281 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101528 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.1 | 86.4 | 204 | 113.3 |  |  |  |  | 6402 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101529 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 208.1 | 63.3 | 188 | 110.7 |  |  |  |  | 6402 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101530 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.6 | 86.4 | 204 | 113.5 |  |  |  |  | 6403 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101531 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 208.6 | 63.3 | 188 | 111 |  |  |  |  | 6403 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101532 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 234.1 | 86.4 | 204 | 114.8 |  |  |  |  | 6426 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101533 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 211.1 | 63.3 | 188 | 112.3 |  |  |  |  | 6426 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101534 | 18S | Approved | P3 | 31 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 653 | 118.8 | 700 | 93.3 |  |  |  |  | 6434 | P1_2-1661_DOLHILL7%,SW SHV 7+G_G1WKRAFT! ID 3 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_G1WKRAFT! ID 3 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101535 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 233.3 | 86.4 | 204 | 114.4 |  |  |  |  | 6453 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101536 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 210.3 | 63.3 | 188 | 111.9 |  |  |  |  | 6453 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101537 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 230.6 | 86.4 | 204 | 113 |  |  |  |  | 6473 | P1_2-1661_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101538 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 207.6 | 63.3 | 188 | 110.4 |  |  |  |  | 6473 | P1_2-1661_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101539 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 235.2 | 86.4 | 204 | 115.3 |  |  |  |  | 6483 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101540 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.2 | 63.3 | 188 | 112.9 |  |  |  |  | 6483 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101541 | 18S | Approved | P3 | 31 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.2 | 118.8 | 700 | 93.2 |  |  |  |  | 6484 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101542 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 266.1 | 86.4 | 204 | 130.5 |  |  |  |  | 6484 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101543 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 242.9 | 63.3 | 188 | 129.2 |  |  |  |  | 6484 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101544 | 18S | Approved | P3 | 31 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 239.7 | 103.3 | 264 | 90.8 |  |  |  |  | 6484 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101545 | 18S | Approved | P3 | 31 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.7 | 118.8 | 700 | 93.1 |  |  |  |  | 6485 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101546 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 259.2 | 86.4 | 204 | 127 |  |  |  |  | 6485 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101547 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 236 | 63.3 | 188 | 125.5 |  |  |  |  | 6485 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101548 | 18S | Approved | P3 | 31 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.7 | 118.8 | 700 | 93.1 |  |  |  |  | 6486 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101549 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 259.2 | 86.4 | 204 | 127 |  |  |  |  | 6486 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101550 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 236 | 63.3 | 188 | 125.5 |  |  |  |  | 6486 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101551 | 18S | Approved | P3 | 31 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.6 | 118.8 | 700 | 93.1 |  |  |  |  | 6487 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101552 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 256.8 | 86.4 | 204 | 125.9 |  |  |  |  | 6487 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101553 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 233.7 | 63.3 | 188 | 124.3 |  |  |  |  | 6487 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101554 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 236.2 | 86.4 | 204 | 115.8 |  |  |  |  | 6488 | P1_2-1661_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101555 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 213.2 | 63.3 | 188 | 113.4 |  |  |  |  | 6488 | P1_2-1661_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101556 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.4 | 86.4 | 204 | 113.4 |  |  |  |  | 6489 | P1_2-1661_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101557 | 18S | Approved | P3 | 31 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 208.4 | 63.3 | 188 | 110.8 |  |  |  |  | 6489 | P1_2-1661_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101558 | 18S | Approved | P3 | 31 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 123.9 | 60.7 | 115 | 107.7 |  |  |  |  | 6915 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+192 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
101559 | 18S | Approved | P3 | 31 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 123.9 | 60.7 | 115 | 107.7 |  |  |  |  | 6916 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+193 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
101560 | 18S | Approved | P3 | 31 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 109.4 | 60.7 | 115 | 95.1 |  |  |  |  | 7151 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+192 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: below Rate A
101561 | 18S | Approved | P3 | 31 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 109.4 | 60.7 | 115 | 95.1 |  |  |  |  | 7152 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+193 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: below Rate A
101562 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 225.8 | 177.6 | 225 | 100.4 |  |  |  |  | 7197 | G_1BCAJUN2_U1% ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1BCAJUN2_U1% ID 1 | None
101563 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 217.2 | 169.1 | 225 | 96.5 |  |  |  |  | 7197 | G_1BCAJUN2_U1% ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1BCAJUN2_U1% ID 1 |  | No violation: below Rate A
101564 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 208.7 | 160.9 | 225 | 92.7 |  |  |  |  | 7197 | G_1BCAJUN2_U1% ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1BCAJUN2_U1% ID 1 |  | No violation: below Rate A
101565 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 221.7 | 143.8 | 206 | 107.6 |  |  |  |  | 7199 | G_1FRNTR 1! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101566 | 18S | Approved | P3 | 31 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 193 | 115.3 | 206 | 93.7 |  |  |  |  | 7199 | G_1FRNTR 1! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 1! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-013-CP | 2017-06-01 | Reconductor Egypt-Panorama 138 kV
101567 | 18S | Approved | P3 | 31 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 186.1 | 108.4 | 206 | 90.3 |  |  |  |  | 7199 | G_1FRNTR 1! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 1! ID 1 |  | No violation: below Rate A
101568 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 212.7 | 143.8 | 206 | 103.3 |  |  |  |  | 7200 | G_1FRNTR 1! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101569 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 261.7 | 99.8 | 243 | 107.7 |  |  |  |  | 7201 | G_1FRNTR 1! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1FRNTR 1! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101570 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 213 | 143.8 | 206 | 103.4 |  |  |  |  | 7202 | G_1FRNTR 1! ID 1+P1_2-177_4CONROE2!,4CONROE1! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-177_4CONROE2!,4CONROE1! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101571 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 221.7 | 143.8 | 206 | 107.6 |  |  |  |  | 7203 | G_1FRNTR 2! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101572 | 18S | Approved | P3 | 31 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 193 | 115.3 | 206 | 93.7 |  |  |  |  | 7203 | G_1FRNTR 2! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 2! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-013-CP | 2017-06-01 | Reconductor Egypt-Panorama 138 kV
101573 | 18S | Approved | P3 | 31 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 186.1 | 108.4 | 206 | 90.3 |  |  |  |  | 7203 | G_1FRNTR 2! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 2! ID 1 |  | No violation: below Rate A
101574 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 212.7 | 143.8 | 206 | 103.3 |  |  |  |  | 7204 | G_1FRNTR 2! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101575 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 261.7 | 99.8 | 243 | 107.7 |  |  |  |  | 7205 | G_1FRNTR 2! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1FRNTR 2! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101576 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 213 | 143.8 | 206 | 103.4 |  |  |  |  | 7206 | G_1FRNTR 2! ID 1+P1_2-177_4CONROE2!,4CONROE1! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-177_4CONROE2!,4CONROE1! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101577 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 284.6 | 99.8 | 243 | 117.1 |  |  |  |  | 7207 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101578 | 18S | Approved | P3 | 31 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 35.6 | 11 | 39 | 91.3 |  |  |  |  | 7208 | G_1G1LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
101579 | 18S | Approved | P3 | 31 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 35.7 | 11.1 | 39 | 91.6 |  |  |  |  | 7208 | G_1G1LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
101580 | 18S | Approved | P3 | 31 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 39.3 | 14.4 | 39 | 100.8 |  |  |  |  | 7208 | G_1G1LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
101581 | 18S | Approved | P3 | 31 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 41.8 | 17 | 39 | 107.1 |  |  |  |  | 7208 | G_1G1LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
101582 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 283.7 | 99.8 | 243 | 116.8 |  |  |  |  | 7209 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101583 | 18S | Approved | P3 | 31 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 35.6 | 11 | 39 | 91.2 |  |  |  |  | 7210 | G_1G2LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
101584 | 18S | Approved | P3 | 31 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 35.7 | 11.1 | 39 | 91.6 |  |  |  |  | 7210 | G_1G2LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
101585 | 18S | Approved | P3 | 31 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 39.3 | 14.4 | 39 | 100.7 |  |  |  |  | 7210 | G_1G2LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
101586 | 18S | Approved | P3 | 31 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 41.7 | 17 | 39 | 107 |  |  |  |  | 7210 | G_1G2LEWIS! ID 1+P1_2-224_4MEMORIL!,4MID CO% | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
101587 | 18S | Approved | P3 | 31 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | LN | 125.8 | 88.7 | 134 | 93.8 |  |  |  |  | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334316 | 334317 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
101588 | 18S | Approved | P3 | 31 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 257.2 | 87.8 | 220 | 116.9 |  |  |  |  | 7215 | G_1EXXONGT1! ID 1+P1_2-291_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-291_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
101589 | 18S | Approved | P3 | 31 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 262.8 | 103.6 | 220 | 119.4 |  |  |  |  | 7216 | G_1EXXONGT1! ID 1+P1_2-292_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-292_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
101590 | 18S | Approved | P3 | 31 | 334396 47NECHES! 138 334398 4HAMPTON 138 1 | LN | 264 | 152.5 | 287 | 92 |  |  |  |  | 7217 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334396 | 334398 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
101591 | 18S | Approved | P3 | 31 | 334398 4HAMPTON 138 334430 4SABINE! 138 1 | LN | 268.1 | 156.5 | 287 | 93.4 |  |  |  |  | 7217 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334398 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
101592 | 18S | Approved | P3 | 31 | 334396 47NECHES! 138 334397 4OILLA 138 1 | LN | 262.3 | 151.2 | 282 | 93 |  |  |  |  | 7218 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334396 | 334397 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
101593 | 18S | Approved | P3 | 31 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 266.1 | 154.9 | 282 | 94.4 |  |  |  |  | 7218 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
101594 | 18S | Approved | P3 | 31 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 200.3 | 103.6 | 220 | 91 |  |  |  |  | 7220 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 | Project Horizon | No violation: below Rate A | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
101595 | 18S | Approved | P3 | 31 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 208.3 | 103.6 | 220 | 94.7 |  |  |  |  | 7221 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 | Project Horizon | No violation: below Rate A | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
101596 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.2 | 192.4 | 262 | 93.2 |  |  |  |  | 7222 | G_1G3SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G3SABIN! ID 1 |  | No violation: below Rate A
101597 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81 | 37 | 80 | 101.3 |  |  |  |  | 7222 | G_1G3SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G3SABIN! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101598 | 18S | Approved | P3 | 31 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 288.8 | 176.1 | 287 | 100.6 |  |  |  |  | 7223 | G_1G4SABIN! ID 1+P1_2-303_4PNEC BK!,4SABINE! | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-303_4PNEC BK!,4SABINE! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
101599 | 18S | Approved | P3 | 31 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 293.3 | 167.1 | 288 | 101.8 |  |  |  |  | 7224 | G_1G4SABIN! ID 1+P1_2-304_4PNEC BK!,4SABINE! | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-304_4PNEC BK!,4SABINE! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
101600 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.6 | 192.4 | 262 | 93.4 |  |  |  |  | 7225 | G_1G4SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G4SABIN! ID 1 |  | No violation: below Rate A
101601 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.4 | 37 | 80 | 101.7 |  |  |  |  | 7225 | G_1G4SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G4SABIN! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101602 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.3 | 192.4 | 262 | 93.2 |  |  |  |  | 7226 | G_1G5SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G5SABIN! ID 1 |  | No violation: below Rate A
101603 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.1 | 37 | 80 | 101.4 |  |  |  |  | 7226 | G_1G5SABIN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1G5SABIN! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101604 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.7 | 192.4 | 262 | 93.4 |  |  |  |  | 7227 | G_1NELSON_G4! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1NELSON_G4! ID 1 |  | No violation: below Rate A
101605 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.2 | 37 | 80 | 101.5 |  |  |  |  | 7227 | G_1NELSON_G4! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1NELSON_G4! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101606 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 245 | 192.4 | 262 | 93.5 |  |  |  |  | 7228 | G_1NELSON_G6! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1NELSON_G6! ID 1 |  | No violation: below Rate A
101607 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.3 | 37 | 80 | 101.7 |  |  |  |  | 7228 | G_1NELSON_G6! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1NELSON_G6! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101608 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 234.5 | 177.6 | 225 | 104.2 |  |  |  |  | 7230 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 | None
101609 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 225.8 | 169.1 | 225 | 100.4 |  |  |  |  | 7230 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 | None
101610 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 217.3 | 160.9 | 225 | 96.6 |  |  |  |  | 7230 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101611 | 18S | Approved | P3 | 31 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1141 | 295 | 1069 | 106.7 |  |  |  |  | 7231 | G_1RVR_BND_G1! ID 1+P1_2-591_8WEBRE%,8BYULABUTTE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-591_8WEBRE%,8BYULABUTTE% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101612 | 18S | Approved | P3 | 31 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 628.2 | 425.9 | 672 | 93.5 |  |  |  |  | 7232 | G_1RVR_BND_G1! ID 1+P1_2-751_6COLY%,8COLY% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-751_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101613 | 18S | Approved | P3 | 31 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1248 | 295 | 1069 | 116.7 |  |  |  |  | 7232 | G_1RVR_BND_G1! ID 1+P1_2-751_6COLY%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-751_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101614 | 18S | Approved | P3 | 31 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 616.2 | 425.9 | 672 | 91.7 |  |  |  |  | 7233 | G_1RVR_BND_G1! ID 1+P1_2-774_6FANCY_PT%,8FANCY_PT% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101615 | 18S | Approved | P3 | 31 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1305.9 | 838.7 | 1186 | 110.1 |  |  |  |  | 7233 | G_1RVR_BND_G1! ID 1+P1_2-774_6FANCY_PT%,8FANCY_PT% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101616 | 18S | Approved | P3 | 31 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 95.9 | 94.8 | 93 | 103.1 |  |  |  |  | 7233 | G_1RVR_BND_G1! ID 1+P1_2-774_6FANCY_PT%,8FANCY_PT% | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 |  | Delta: No worse than P0
101617 | 18S | Approved | P3 | 31 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1293.1 | 295 | 1069 | 121 |  |  |  |  | 7234 | G_1RVR_BND_G1! ID 1+P1_2-776_8MCKNIGHT%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-776_8MCKNIGHT%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101618 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 236.8 | 177.6 | 225 | 105.3 |  |  |  |  | 7236 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 | None
101619 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 228.2 | 169.1 | 225 | 101.4 |  |  |  |  | 7236 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 | None
101620 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 219.8 | 160.9 | 225 | 97.7 |  |  |  |  | 7236 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101621 | 18S | Approved | P3 | 31 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 189 | 121.7 | 199 | 95 |  |  |  |  | 7237 | G_1WAT U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101622 | 18S | Approved | P3 | 31 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 210.8 | 142.2 | 199 | 105.9 |  |  |  |  | 7237 | G_1WAT U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101623 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 227.9 | 177.6 | 225 | 101.3 |  |  |  |  | 7242 | G_1NMIL U4! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U4! ID 1 | None
101624 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 219.3 | 169.1 | 225 | 97.5 |  |  |  |  | 7242 | G_1NMIL U4! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101625 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 210.8 | 160.9 | 225 | 93.7 |  |  |  |  | 7242 | G_1NMIL U4! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101626 | 18S | Approved | P3 | 31 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 184.3 | 121.7 | 199 | 92.6 |  |  |  |  | 7243 | G_1NMIL U4! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101627 | 18S | Approved | P3 | 31 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 206 | 142.2 | 199 | 103.5 |  |  |  |  | 7243 | G_1NMIL U4! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101628 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 228.2 | 177.6 | 225 | 101.4 |  |  |  |  | 7245 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 | None
101629 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 219.6 | 169.1 | 225 | 97.6 |  |  |  |  | 7245 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101630 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 211 | 160.9 | 225 | 93.8 |  |  |  |  | 7245 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101631 | 18S | Approved | P3 | 31 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 184.6 | 121.7 | 199 | 92.8 |  |  |  |  | 7246 | G_1NMIL U5! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101632 | 18S | Approved | P3 | 31 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 206.3 | 142.2 | 199 | 103.6 |  |  |  |  | 7246 | G_1NMIL U5! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101633 | 18S | Approved | P3 | 31 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 182.4 | 121.7 | 199 | 91.7 |  |  |  |  | 7248 | G_1MICH U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1MICH U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101634 | 18S | Approved | P3 | 31 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 204.1 | 142.2 | 199 | 102.5 |  |  |  |  | 7248 | G_1MICH U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1MICH U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101635 | 18S | Approved | P3 | 31 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 235.1 | 136.6 | 229 | 102.7 |  |  |  |  | 7249 | G_1MICH U3! ID 1+P1_2-951_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! | G_1MICH U3! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
101636 | 18S | Approved | P3 | 31 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 230 | 162.4 | 229 | 100.4 |  |  |  |  | 7250 | G_1MICH U3! ID 1+P1_2-952_39MILE%,3GRETNA! | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-952_39MILE%,3GRETNA! | G_1MICH U3! ID 1 | Project Horizon |  | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
101637 | 18S | Approved | P3 | 31 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 225.5 | 177.6 | 225 | 100.2 |  |  |  |  | 7251 | G_1GGNS U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1GGNS U1 ID 1 | None
101638 | 18S | Approved | P3 | 31 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 216.9 | 169.1 | 225 | 96.4 |  |  |  |  | 7251 | G_1GGNS U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101639 | 18S | Approved | P3 | 31 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 208.4 | 160.9 | 225 | 92.6 |  |  |  |  | 7251 | G_1GGNS U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101640 | 18S | Approved | P3 | 31 | 336907 3MIAMI ST 115 336938 3REX BRWN-W! 115 1 | LN | 295.4 | 226.5 | 320 | 92.3 |  |  |  |  | 7253 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336907 | 336938 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101641 | 18S | Approved | P3 | 31 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 645 | 347.1 | 600 | 107.5 |  |  |  |  | 7253 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101642 | 18S | Approved | P3 | 31 | 336938 3REX BRWN-W! 115 336939 3REX BRWN-C! 115 Z1 | LN | 292.9 | 129.1 | 319 | 91.8 |  |  |  |  | 7253 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336938 | 336939 | Z1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101643 | 18S | Approved | P3 | 31 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | LN | 424.1 | 160.5 | 462 | 91.8 |  |  |  |  | 7254 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 336866 | 337015 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101644 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 589.5 | 323 | 561 | 105.1 |  |  |  |  | 7254 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101645 | 18S | Approved | P3 | 31 | 337016 3PICKENS! 115 337018 3MIDWAY MS+ 115 1 | LN | 111.8 | 44.5 | 108 | 103.5 |  |  |  |  | 7254 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337016 | 337018 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101646 | 18S | Approved | P3 | 31 | 337028 3CONEHOMA 115 337031 3CARTHAGE MS 115 1 | LN | 100.9 | 47.3 | 108 | 93.4 |  |  |  |  | 7254 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337031 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101647 | 18S | Approved | P3 | 31 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 112.8 | 59.3 | 108 | 104.4 |  |  |  |  | 7254 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101648 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 576.8 | 323 | 561 | 102.8 |  |  |  |  | 7255 | G_1GGNS U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101649 | 18S | Approved | P3 | 31 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 159.6 | 83 | 161 | 99.1 |  |  |  |  | 7257 | G_1ANDRUS U1 ID 1+1267 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1031_3VICKSBURG!,3N.VICKSBRG! | G_1ANDRUS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
101650 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 643 | 323 | 561 | 114.6 |  |  |  |  | 7258 | G_1ANDRUS U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101651 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 | TR | 626.2 | 291.2 | 615 | 101.8 |  |  |  |  | 7259 | G_1ANDRUS U1 ID 1+P1_2-1098_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 1 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1098_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101652 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.5 | 323 | 561 | 101.3 |  |  |  |  | 7260 | G_3GREENWOOD! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_3GREENWOOD! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101653 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 563.9 | 323 | 561 | 100.5 |  |  |  |  | 7261 | G_1CLSBAU3 ID 6+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CLSBAU3 ID 6 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101654 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.3 | 192.4 | 262 | 93.2 |  |  |  |  | 7262 | G_1MURRY_U1&2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U1&2 ID 1 |  | No violation: below Rate A
101655 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.4 | 37 | 80 | 101.8 |  |  |  |  | 7262 | G_1MURRY_U1&2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U1&2 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101656 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.3 | 192.4 | 262 | 93.2 |  |  |  |  | 7263 | G_1MURRY_U3&4 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U3&4 ID 1 |  | No violation: below Rate A
101657 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.4 | 37 | 80 | 101.8 |  |  |  |  | 7263 | G_1MURRY_U3&4 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U3&4 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101658 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.3 | 192.4 | 262 | 93.2 |  |  |  |  | 7264 | G_1MURRY_U5&6 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U5&6 ID 1 |  | No violation: below Rate A
101659 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.4 | 37 | 80 | 101.8 |  |  |  |  | 7264 | G_1MURRY_U5&6 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U5&6 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101660 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.5 | 192.4 | 262 | 92.9 |  |  |  |  | 7265 | G_1MURRY_U7&8 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U7&8 ID 1 |  | No violation: below Rate A
101661 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.6 | 37 | 80 | 100.8 |  |  |  |  | 7265 | G_1MURRY_U7&8 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1MURRY_U7&8 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101662 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.3 | 192.4 | 262 | 91.7 |  |  |  |  | 7266 | G_1OUACHI_G1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G1! ID 1 |  | No violation: below Rate A
101663 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.6 | 37 | 80 | 100.8 |  |  |  |  | 7266 | G_1OUACHI_G1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G1! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101664 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.3 | 192.4 | 262 | 91.7 |  |  |  |  | 7267 | G_1OUACHI_G2! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G2! ID 1 |  | No violation: below Rate A
101665 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.6 | 37 | 80 | 100.8 |  |  |  |  | 7267 | G_1OUACHI_G2! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G2! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101666 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.3 | 192.4 | 262 | 91.7 |  |  |  |  | 7268 | G_1OUACHI_G3! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G3! ID 1 |  | No violation: below Rate A
101667 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.6 | 37 | 80 | 100.8 |  |  |  |  | 7268 | G_1OUACHI_G3! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1OUACHI_G3! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101668 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.1 | 192.4 | 262 | 91.7 |  |  |  |  | 7269 | G_1PERRYV_C1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_C1! ID 1 |  | No violation: below Rate A
101669 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.7 | 37 | 80 | 100.9 |  |  |  |  | 7269 | G_1PERRYV_C1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_C1! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101670 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.1 | 192.4 | 262 | 91.7 |  |  |  |  | 7270 | G_1PERRYV_C3! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_C3! ID 1 |  | No violation: below Rate A
101671 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.7 | 37 | 80 | 100.9 |  |  |  |  | 7270 | G_1PERRYV_C3! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_C3! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101672 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.2 | 192.4 | 262 | 91.7 |  |  |  |  | 7271 | G_1PERRYV_S1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_S1! ID 1 |  | No violation: below Rate A
101673 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.7 | 37 | 80 | 100.8 |  |  |  |  | 7271 | G_1PERRYV_S1! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1PERRYV_S1! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101674 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.6 | 192.4 | 262 | 91.8 |  |  |  |  | 7272 | G_1WHT BLUF U1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1WHT BLUF U1 ID 1 |  | No violation: below Rate A
101675 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.5 | 37 | 80 | 101.9 |  |  |  |  | 7272 | G_1WHT BLUF U1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1WHT BLUF U1 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101676 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.5 | 192.4 | 262 | 91.8 |  |  |  |  | 7273 | G_1WHT BLUF U2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1WHT BLUF U2 ID 1 |  | No violation: below Rate A
101677 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.6 | 37 | 80 | 102 |  |  |  |  | 7273 | G_1WHT BLUF U2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1WHT BLUF U2 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101678 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 241.2 | 192.4 | 262 | 92 |  |  |  |  | 7274 | G_1CATHRINE U4 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1CATHRINE U4 ID 1 |  | No violation: below Rate A
101679 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81 | 37 | 80 | 101.2 |  |  |  |  | 7274 | G_1CATHRINE U4 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1CATHRINE U4 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101680 | 18S | Approved | P3 | 31 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 287.8 | 129.5 | 239 | 120.4 |  |  |  |  | 7275 | G_1CATHRINE U4 ID 1+P1_2-1345_3HS EHV-E!,8HS EHV% | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1345_3HS EHV-E!,8HS EHV% | G_1CATHRINE U4 ID 1 | Project Approved |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
101681 | 18S | Approved | P3 | 31 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 186.7 | 92 | 176 | 106.1 |  |  |  |  | 7276 | G_1BLAKELY U1 ID 1+1569 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
101682 | 18S | Approved | P3 | 31 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 175.6 | 81 | 176 | 99.8 |  |  |  |  | 7276 | G_1BLAKELY U1 ID 1+1569 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
101683 | 18S | Approved | P3 | 31 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 185.7 | 91.1 | 176 | 105.5 |  |  |  |  | 7276 | G_1BLAKELY U1 ID 1+1569 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
101684 | 18S | Approved | P3 | 31 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 186.7 | 92 | 176 | 106.1 |  |  |  |  | 7277 | G_1BLAKELY U2 ID 1+1569 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
101685 | 18S | Approved | P3 | 31 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 175.6 | 81 | 176 | 99.8 |  |  |  |  | 7277 | G_1BLAKELY U2 ID 1+1569 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
101686 | 18S | Approved | P3 | 31 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 185.7 | 91.1 | 176 | 105.5 |  |  |  |  | 7277 | G_1BLAKELY U2 ID 1+1569 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
101687 | 18S | Approved | P3 | 31 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 188.6 | 92 | 176 | 107.2 |  |  |  |  | 7278 | G_1CARPENTR U1 ID 1+1569 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
101688 | 18S | Approved | P3 | 31 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 177.6 | 81 | 176 | 100.9 |  |  |  |  | 7278 | G_1CARPENTR U1 ID 1+1569 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
101689 | 18S | Approved | P3 | 31 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 187.7 | 91.1 | 176 | 106.6 |  |  |  |  | 7278 | G_1CARPENTR U1 ID 1+1569 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
101690 | 18S | Approved | P3 | 31 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 189.4 | 92 | 176 | 107.6 |  |  |  |  | 7279 | G_1CARPENTR U2 ID 1+1569 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
101691 | 18S | Approved | P3 | 31 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 178.3 | 81 | 176 | 101.3 |  |  |  |  | 7279 | G_1CARPENTR U2 ID 1+1569 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
101692 | 18S | Approved | P3 | 31 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 188.4 | 91.1 | 176 | 107.1 |  |  |  |  | 7279 | G_1CARPENTR U2 ID 1+1569 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
101693 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.7 | 192.4 | 262 | 91.9 |  |  |  |  | 7280 | G_1ANO U1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1ANO U1 ID 1 |  | No violation: below Rate A
101694 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.6 | 37 | 80 | 102 |  |  |  |  | 7280 | G_1ANO U1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1ANO U1 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101695 | 18S | Approved | P3 | 31 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.8 | 323 | 561 | 101.4 |  |  |  |  | 7281 | G_1ANO U2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANO U2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
101696 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 240.4 | 192.4 | 262 | 91.8 |  |  |  |  | 7282 | G_1ANO U2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1ANO U2 ID 1 |  | No violation: below Rate A
101697 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 82 | 37 | 80 | 102.5 |  |  |  |  | 7282 | G_1ANO U2 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_1ANO U2 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101698 | 18S | Approved | P3 | 31 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 312.4 | 180.1 | 266 | 117.4 |  |  |  |  | 7283 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101699 | 18S | Approved | P3 | 31 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 276.2 | 140.7 | 266 | 103.8 |  |  |  |  | 7283 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
101700 | 18S | Approved | P3 | 31 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 458.1 | 260.7 | 450 | 101.8 |  |  |  |  | 7283 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Generation redispatch: Turn on Ritchie unit 500 MW
101701 | 18S | Approved | P3 | 31 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 231.5 | 111.8 | 223 | 103.8 |  |  |  |  | 7284 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1
101702 | 18S | Approved | P3 | 31 | 337530 3CAMDEN MAG! 115 337536 3SMACKOVER 115 1 | LN | 100.5 | 19.6 | 98 | 102.5 |  |  |  |  | 7285 | G_1MCCLELAN U1 ID 1+1502 | 337530 | 337536 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1266_8MCNEIL%,8ETTA% | G_1MCCLELAN U1 ID 1
101703 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 210.4 | 143.8 | 206 | 102.1 |  |  |  |  | 7289 | G_G1DOLHIL! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_G1DOLHIL! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101704 | 18S | Approved | P3 | 31 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 75.4 | 30.3 | 77 | 98 |  |  |  |  | 7290 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101705 | 18S | Approved | P3 | 31 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 76.9 | 31.6 | 77 | 99.9 |  |  |  |  | 7290 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101706 | 18S | Approved | P3 | 31 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 79.4 | 37.5 | 77 | 103.1 |  |  |  |  | 7290 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101707 | 18S | Approved | P3 | 31 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 117.9 | 70.9 | 115 | 102.6 |  |  |  |  | 7291 | G_G1DOLHIL! ID 1+P1_2-1192_3MINDEN_LA!,3SAREPTA! | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101708 | 18S | Approved | P3 | 31 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 109.7 | 54.5 | 111 | 98.8 |  |  |  |  | 7292 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101709 | 18S | Approved | P3 | 31 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 127 | 70.9 | 115 | 110.5 |  |  |  |  | 7292 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101710 | 18S | Approved | P3 | 31 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 76.5 | 37.5 | 77 | 99.4 |  |  |  |  | 7292 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101711 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 245.6 | 192.4 | 262 | 93.7 |  |  |  |  | 7293 | G_G1DOLHIL! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101712 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83.1 | 37 | 80 | 103.8 |  |  |  |  | 7293 | G_G1DOLHIL! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1DOLHIL! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101713 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.2 | 192.4 | 262 | 93.2 |  |  |  |  | 7294 | G_G1NESBIT! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1NESBIT! ID 1 |  | No violation: below Rate A
101714 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 80.6 | 37 | 80 | 100.8 |  |  |  |  | 7294 | G_G1NESBIT! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1NESBIT! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101715 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 248.9 | 192.4 | 262 | 95 |  |  |  |  | 7295 | G_G2RODEMR! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G2RODEMR! ID 1 |  | No violation: below Rate A
101716 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83 | 37 | 80 | 103.8 |  |  |  |  | 7295 | G_G2RODEMR! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G2RODEMR! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101717 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 250.2 | 192.4 | 262 | 95.5 |  |  |  |  | 7296 | G_G3MADISN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G3MADISN! ID 1 |  | No violation: below Rate A
101718 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 83.8 | 37 | 80 | 104.7 |  |  |  |  | 7296 | G_G3MADISN! ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G3MADISN! ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101719 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 220.9 | 143.8 | 206 | 107.2 |  |  |  |  | 7306 | G_PIRKEY 1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101720 | 18S | Approved | P3 | 31 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 192.4 | 115.3 | 206 | 93.4 |  |  |  |  | 7306 | G_PIRKEY 1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_PIRKEY 1 ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-013-CP | 2017-06-01 | Reconductor Egypt-Panorama 138 kV
101721 | 18S | Approved | P3 | 31 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 185.5 | 108.4 | 206 | 90.1 |  |  |  |  | 7306 | G_PIRKEY 1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
101722 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 211.9 | 143.8 | 206 | 102.9 |  |  |  |  | 7307 | G_PIRKEY 1 ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101723 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 263.6 | 99.8 | 243 | 108.5 |  |  |  |  | 7308 | G_PIRKEY 1 ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_PIRKEY 1 ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101724 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 211.8 | 143.8 | 206 | 102.8 |  |  |  |  | 7309 | G_PIRKEY 1 ID 1+P1_2-177_4CONROE2!,4CONROE1! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-177_4CONROE2!,4CONROE1! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101725 | 18S | Approved | P3 | 31 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 103 | 54.5 | 111 | 92.7 |  |  |  |  | 7310 | G_PIRKEY 1 ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
101726 | 18S | Approved | P3 | 31 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 120.1 | 70.9 | 115 | 104.4 |  |  |  |  | 7310 | G_PIRKEY 1 ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101727 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.6 | 192.4 | 262 | 93 |  |  |  |  | 7311 | G_PIRKEY 1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
101728 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 82.1 | 37 | 80 | 102.6 |  |  |  |  | 7311 | G_PIRKEY 1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_PIRKEY 1 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101729 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 213.5 | 143.8 | 206 | 103.7 |  |  |  |  | 7312 | G_WELSH2-1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_WELSH2-1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101730 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 252 | 99.8 | 243 | 103.7 |  |  |  |  | 7313 | G_WELSH2-1 ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_WELSH2-1 ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101731 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.2 | 192.4 | 262 | 92.8 |  |  |  |  | 7314 | G_WELSH2-1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_WELSH2-1 ID 1 |  | No violation: below Rate A
101732 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.7 | 37 | 80 | 102.1 |  |  |  |  | 7314 | G_WELSH2-1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_WELSH2-1 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101733 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 213.5 | 143.8 | 206 | 103.7 |  |  |  |  | 7315 | G_WELSH3-1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_WELSH3-1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101734 | 18S | Approved | P3 | 31 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 252 | 99.8 | 243 | 103.7 |  |  |  |  | 7316 | G_WELSH3-1 ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_WELSH3-1 ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101735 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.2 | 192.4 | 262 | 92.8 |  |  |  |  | 7317 | G_WELSH3-1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_WELSH3-1 ID 1 |  | No violation: below Rate A
101736 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.7 | 37 | 80 | 102.1 |  |  |  |  | 7317 | G_WELSH3-1 ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_WELSH3-1 ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101737 | 18S | Approved | P3 | 31 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 212.3 | 143.8 | 206 | 103.1 |  |  |  |  | 7318 | G_TURKCOAL ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_TURKCOAL ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101738 | 18S | Approved | P3 | 31 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 242.9 | 192.4 | 262 | 92.7 |  |  |  |  | 7319 | G_TURKCOAL ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_TURKCOAL ID 1 |  | No violation: below Rate A
101739 | 18S | Approved | P3 | 31 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 81.8 | 37 | 80 | 102.3 |  |  |  |  | 7319 | G_TURKCOAL ID 1+P1_2-1214_3SWARTZ!,3STERLING% | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_TURKCOAL ID 1 | Project Approved |  | 11-ELL-003-2-CP | 2014-06-01 | NE Louisiana Improvement Project - Phase 2 Oak Ridge to new Dunn Substation - Construct new 115 kV Line (1272 ACSS) Add 115 kV breakers at Dunn Add 115 kV, 32.4 Mvar capacitor ba
101740 | 18W | Approved | P0 | 32 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 331.9 | 360 | 92.2 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
101741 | 18W | Approved | P0 | 32 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.1 | 35.1 | 39 | 90 |  |  |  |  | 0 | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101742 | 18W | Approved | P0 | 32 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 44.7 | 44.7 | 38 | 117.5 |  |  |  |  | 0 | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
101743 | 18W | Approved | P0 | 32 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 85.4 | 85.4 | 93 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
101744 | 18W | Approved | P0 | 32 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 19.9 | 19.9 | 20 | 99.4 |  |  |  |  | 0 | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
101745 | 18W | Approved | P0 | 32 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 335.4 | 335.4 | 360 | 93.2 |  |  |  |  | 0 | ** Base Case ** | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
101746 | 18W | Approved | P0 | 32 | 360614 8MAGNOL CC2 500 990014 1.00 2 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990014 | 2 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
101747 | 18W | Approved | P0 | 32 | 360614 8MAGNOL CC2 500 990199 1.00 3 | TR | 334.8 | 334.8 | 360 | 93 |  |  |  |  | 0 | ** Base Case ** | 360614 | 990199 | 3 |  | 500 | 1 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
101748 | 18W | Approved | P0 | 32 | 500120 B.BRID 2 69.0 500620 NICKTAP2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500120 | 500620 | 1 |  | 69 | 69 | 502 | CLEC | 502 | CLEC | ** Base Case ** |  |  | No violation: below Rate A
101749 | 18W | Approved | P0 | 32 | 500620 NICKTAP2 69.0 502413 ELKS 2 69.0 1 | LN | 25.7 | 25.7 | 28 | 91.8 |  |  |  |  | 0 | ** Base Case ** | 500620 | 502413 | 1 |  | 69 | 69 | 502 | CLEC | 503 | LAFA | ** Base Case ** |  |  | No violation: below Rate A
101750 | 18W | Approved | P3 | 32 | 334305 4BUNASW 138 334307 4BUNA! 138 1 | LN | 108.4 | 47.8 | 120 | 90.4 |  |  |  |  | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334305 | 334307 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | No violation: below Rate A | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
101751 | 18W | Approved | P3 | 32 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 121.2 | 59.9 | 120 | 101 |  |  |  |  | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
101752 | 18W | Approved | P3 | 32 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 128.7 | 67.2 | 127 | 101.4 |  |  |  |  | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
101753 | 18W | Approved | P3 | 32 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 35.7 | 18.9 | 39 | 91.6 |  |  |  |  | 2745 | P1_2-569_4MORIL!,2MORIL!+G_G3TECHE! ID 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-569_4MORIL!,2MORIL! | G_G3TECHE! ID 1 |  | No violation: below Rate A
101754 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1003.6 | 266.5 | 1069 | 93.9 |  |  |  |  | 2865 | P1_2-774_6FANCY_PT%,1RVR_BND_G1!+G_1WAT U3! ID 1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101755 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 999.3 | 266.5 | 1069 | 93.5 |  |  |  |  | 3520 | P1_2-879_6WATFRD%+G_1RVR_BND_G1! ID 1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-879_6WATFRD% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101756 | 18W | Approved | P3 | 32 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 340.8 | 335.4 | 360 | 94.7 |  |  |  |  | 6622 | P1_2-1567_8FREEPORTTN%,8CORDOVA TN!+134 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101757 | 18W | Approved | P3 | 32 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 341.9 | 335.4 | 360 | 95 |  |  |  |  | 6623 | P1_2-1567_8FREEPORTTN%,8CORDOVA TN!+135 | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101758 | 18W | Approved | P3 | 32 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 76.5 | 38.3 | 77 | 99.4 |  |  |  |  | 7746 | P1_2-1639_CLARN 6!,MESSICK6!+G_G1DOLHIL! ID 1 | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101759 | 18W | Approved | P3 | 32 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 77.8 | 39.5 | 77 | 101 |  |  |  |  | 7746 | P1_2-1639_CLARN 6!,MESSICK6!+G_G1DOLHIL! ID 1 | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101760 | 18W | Approved | P3 | 32 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 74.2 | 39.1 | 77 | 96.4 |  |  |  |  | 7746 | P1_2-1639_CLARN 6!,MESSICK6!+G_G1DOLHIL! ID 1 | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101761 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 238 | 90.1 | 204 | 116.7 |  |  |  |  | 8238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1BCAJUN2_U2% ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1BCAJUN2_U2% ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101762 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 215 | 66.9 | 233 | 92.3 |  |  |  |  | 8238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1BCAJUN2_U2% ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1BCAJUN2_U2% ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101763 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 238.6 | 90.1 | 204 | 117 |  |  |  |  | 8249 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101764 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 215.6 | 66.9 | 233 | 92.5 |  |  |  |  | 8249 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101765 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 238.6 | 90.1 | 204 | 117 |  |  |  |  | 8250 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101766 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 215.6 | 66.9 | 233 | 92.5 |  |  |  |  | 8250 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101767 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 238.7 | 90.1 | 204 | 117 |  |  |  |  | 8364 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101768 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 215.7 | 66.9 | 233 | 92.6 |  |  |  |  | 8364 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101769 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239.1 | 90.1 | 204 | 117.2 |  |  |  |  | 8365 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101770 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 216.1 | 66.9 | 233 | 92.8 |  |  |  |  | 8365 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101771 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 241.7 | 90.1 | 204 | 118.5 |  |  |  |  | 8388 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101772 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 218.6 | 66.9 | 233 | 93.8 |  |  |  |  | 8388 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101773 | 18W | Approved | P3 | 32 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648.3 | 101.8 | 700 | 92.6 |  |  |  |  | 8396 | P1_2-1664_DOLHILL7%,SW SHV 7+G_G1WKRAFT! ID 3 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_G1WKRAFT! ID 3 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101774 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 242.4 | 90.1 | 204 | 118.8 |  |  |  |  | 8412 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101775 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 219.4 | 66.9 | 233 | 94.2 |  |  |  |  | 8412 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101776 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 237.8 | 90.1 | 204 | 116.6 |  |  |  |  | 8431 | P1_2-1664_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101777 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 214.8 | 66.9 | 233 | 92.2 |  |  |  |  | 8431 | P1_2-1664_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101778 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 242.8 | 90.1 | 204 | 119 |  |  |  |  | 8442 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101779 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 219.7 | 66.9 | 233 | 94.3 |  |  |  |  | 8442 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101780 | 18W | Approved | P3 | 32 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.9 | 101.8 | 700 | 92.6 |  |  |  |  | 8443 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101781 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 269.8 | 90.1 | 204 | 132.3 |  |  |  |  | 8443 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101782 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 246.6 | 66.9 | 233 | 105.8 |  |  |  |  | 8443 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101783 | 18W | Approved | P3 | 32 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 238.6 | 102.5 | 264 | 90.4 |  |  |  |  | 8443 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101784 | 18W | Approved | P3 | 32 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.3 | 101.8 | 700 | 92.5 |  |  |  |  | 8444 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101785 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 260.8 | 90.1 | 204 | 127.8 |  |  |  |  | 8444 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101786 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 237.7 | 66.9 | 233 | 102 |  |  |  |  | 8444 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101787 | 18W | Approved | P3 | 32 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.3 | 101.8 | 700 | 92.5 |  |  |  |  | 8445 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101788 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 260.8 | 90.1 | 204 | 127.8 |  |  |  |  | 8445 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101789 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 237.7 | 66.9 | 233 | 102 |  |  |  |  | 8445 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101790 | 18W | Approved | P3 | 32 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 101.8 | 700 | 92.4 |  |  |  |  | 8446 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101791 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 256.5 | 90.1 | 204 | 125.7 |  |  |  |  | 8446 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101792 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 233.4 | 66.9 | 233 | 100.2 |  |  |  |  | 8446 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101793 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 244.7 | 90.1 | 204 | 120 |  |  |  |  | 8447 | P1_2-1664_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101794 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 221.7 | 66.9 | 233 | 95.1 |  |  |  |  | 8447 | P1_2-1664_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101795 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239 | 90.1 | 204 | 117.1 |  |  |  |  | 8448 | P1_2-1664_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101796 | 18W | Approved | P3 | 32 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 216 | 66.9 | 233 | 92.7 |  |  |  |  | 8448 | P1_2-1664_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101797 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 186.4 | 133 | 206 | 90.5 |  |  |  |  | 8465 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1FRNTR 1! ID 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1FRNTR 1! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101798 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 186.4 | 133 | 206 | 90.5 |  |  |  |  | 8466 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1FRNTR 2! ID 1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1FRNTR 2! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101799 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 141.9 | 113.6 | 150 | 94.6 |  |  |  |  | 8729 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+67 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101800 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 141.8 | 113.6 | 150 | 94.5 |  |  |  |  | 8732 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+70 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: below Rate A
101801 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 141.8 | 113.6 | 150 | 94.5 |  |  |  |  | 8836 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+174 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G7COUGH! ID 1 |  | No violation: below Rate A
101802 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 141.8 | 113.6 | 150 | 94.5 |  |  |  |  | 8837 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+175 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G7-1COUGH! ID 1 |  | No violation: below Rate A
101803 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 208.3 | 133 | 206 | 101.1 |  |  |  |  | 9142 | G_1FRNTR 1! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101804 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 208.3 | 133 | 206 | 101.1 |  |  |  |  | 9147 | G_1FRNTR 2! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101805 | 18W | Approved | P3 | 32 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 261.8 | 90.8 | 243 | 107.7 |  |  |  |  | 9156 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101806 | 18W | Approved | P3 | 32 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 260.9 | 90.8 | 243 | 107.4 |  |  |  |  | 9174 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
101807 | 18W | Approved | P3 | 32 | 334280 4DOUCETT! 138 334315 4WOODVILLE 138 1 | LN | 133.1 | 98.3 | 145 | 91.8 |  |  |  |  | 9191 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334280 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
101808 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 117.9 | 52.7 | 120 | 98.2 |  |  |  |  | 9191 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
101809 | 18W | Approved | P3 | 32 | 334314 4URLAND! 138 334315 4WOODVILLE 138 1 | LN | 136.9 | 101.7 | 145 | 94.4 |  |  |  |  | 9191 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334314 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
101810 | 18W | Approved | P3 | 32 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 232.3 | 76.6 | 220 | 105.6 |  |  |  |  | 9200 | G_1EXXONGT1! ID 1+P1_2-291_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-291_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
101811 | 18W | Approved | P3 | 32 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 237.3 | 90.4 | 220 | 107.8 |  |  |  |  | 9201 | G_1EXXONGT1! ID 1+P1_2-292_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-292_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
101812 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 490.9 | 314.6 | 470 | 104.4 |  |  |  |  | 9230 | G_1G3SABIN! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G3SABIN! ID 1 | Reduce PPG Plant
101813 | 18W | Approved | P3 | 32 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 338.7 | 331.9 | 360 | 94.1 |  |  |  |  | 9251 | G_1G4SABIN! ID 1+P1_2-101_8COTNWOOD2!,8HARTBRG% | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-101_8COTNWOOD2!,8HARTBRG% | G_1G4SABIN! ID 1 |  | No violation: below Rate A
101814 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 431 | 314.6 | 470 | 91.7 |  |  |  |  | 9256 | G_1G4SABIN! ID 1+P1_2-318_6SABINE%,1G5SABIN! | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-318_6SABINE%,1G5SABIN! | G_1G4SABIN! ID 1 |  | No violation: below Rate A
101815 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 540.5 | 314.6 | 470 | 115 |  |  |  |  | 9257 | G_1G4SABIN! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
101816 | 18W | Approved | P3 | 32 | 335135 6VERDINE% 230 335136 6PPG! 230 1 | LN | 423.4 | 214.9 | 470 | 90.1 |  |  |  |  | 9257 | G_1G4SABIN! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335135 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 |  | No violation: below Rate A
101817 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 431 | 314.6 | 470 | 91.7 |  |  |  |  | 9293 | G_1G5SABIN! ID 1+P1_2-317_6SABINE%,1G4SABIN! | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-317_6SABINE%,1G4SABIN! | G_1G5SABIN! ID 1 |  | No violation: below Rate A
101818 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 509.9 | 314.6 | 470 | 108.5 |  |  |  |  | 9294 | G_1G5SABIN! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G5SABIN! ID 1 | Reduce PPG Plant
101819 | 18W | Approved | P3 | 32 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 526.6 | 187.4 | 560 | 94 |  |  |  |  | 9358 | G_1NELSON_G4! ID 1+P1_2-486_6NELSON%,1NELSON_G6! | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-486_6NELSON%,1NELSON_G6! | G_1NELSON_G4! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
101820 | 18W | Approved | P3 | 32 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 526.6 | 187.4 | 560 | 94 |  |  |  |  | 9396 | G_1NELSON_G6! ID 1+P1_2-485_6NELSON%,1NELSON_G4! | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-485_6NELSON%,1NELSON_G4! | G_1NELSON_G6! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
101821 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 996.2 | 266.5 | 1069 | 93.2 |  |  |  |  | 9571 | G_1RVR_BND_G1! ID 1+P1_2-82_8BIG_CAJUN2%,8WEBRE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-82_8BIG_CAJUN2%,8WEBRE% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101822 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.1 |  |  |  |  | 9595 | G_1RVR_BND_G1! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101823 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 9595 | G_1RVR_BND_G1! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101824 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.3 |  |  |  |  | 9727 | G_1RVR_BND_G1! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101825 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 97.1 |  |  |  |  | 9936 | G_1RVR_BND_G1! ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101826 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 9936 | G_1RVR_BND_G1! ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101827 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 431.1 | 314.6 | 470 | 91.7 |  |  |  |  | 9937 | G_1RVR_BND_G1! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101828 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 96.9 |  |  |  |  | 9979 | G_1RVR_BND_G1! ID 1+719 | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101829 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 204.9 | 171.5 | 225 | 91.1 |  |  |  |  | 10023 | G_1RVR_BND_G1! ID 1+P1_2-544_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-544_4RICHARD%,4SCOTT_1! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101830 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 209.1 | 171.5 | 225 | 93 |  |  |  |  | 10024 | G_1RVR_BND_G1! ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101831 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 228.8 | 171.5 | 225 | 101.7 |  |  |  |  | 10027 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 | None
101832 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 220.6 | 163.5 | 225 | 98 |  |  |  |  | 10027 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101833 | 18W | Approved | P3 | 32 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 210 | 152.8 | 225 | 93.4 |  |  |  |  | 10027 | G_1RVR_BND_G1! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101834 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 185.4 | 113.5 | 191 | 97 |  |  |  |  | 10044 | G_1RVR_BND_G1! ID 1+P1_2-565_4MEAUX!,6MEAUX! | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101835 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 185.4 | 113.5 | 191 | 97.1 |  |  |  |  | 10045 | G_1RVR_BND_G1! ID 1+P1_2-566_6MEAUX!,SELLRD6% | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101836 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1121.7 | 266.5 | 1069 | 104.9 |  |  |  |  | 10069 | G_1RVR_BND_G1! ID 1+P1_2-591_8WEBRE%,8BYULABUTTE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-591_8WEBRE%,8BYULABUTTE% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101837 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 969.9 | 266.5 | 1069 | 90.7 |  |  |  |  | 10102 | G_1RVR_BND_G1! ID 1+843 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-624_6WILLOW_GL%,8WILLOW_GL% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101838 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 642.4 | 449.9 | 672 | 95.6 |  |  |  |  | 10230 | G_1RVR_BND_G1! ID 1+P1_2-752_6COLY%,8COLY% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-752_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101839 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1199.5 | 266.5 | 1069 | 112.2 |  |  |  |  | 10230 | G_1RVR_BND_G1! ID 1+P1_2-752_6COLY%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-752_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101840 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 633.4 | 449.9 | 672 | 94.3 |  |  |  |  | 10252 | G_1RVR_BND_G1! ID 1+P1_2-775_6FANCY_PT%,8FANCY_PT% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101841 | 18W | Approved | P3 | 32 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1245 | 790.9 | 1186 | 105 |  |  |  |  | 10252 | G_1RVR_BND_G1! ID 1+P1_2-775_6FANCY_PT%,8FANCY_PT% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101842 | 18W | Approved | P3 | 32 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 86.6 | 85.4 | 93 | 93.1 |  |  |  |  | 10252 | G_1RVR_BND_G1! ID 1+P1_2-775_6FANCY_PT%,8FANCY_PT% | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-775_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101843 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1270.9 | 266.5 | 1069 | 118.9 |  |  |  |  | 10254 | G_1RVR_BND_G1! ID 1+P1_2-777_8MCKNIGHT%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-777_8MCKNIGHT%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101844 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 655.4 | 449.9 | 672 | 97.5 |  |  |  |  | 10258 | G_1RVR_BND_G1! ID 1+1000 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-781_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101845 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 983.4 | 266.5 | 1069 | 92 |  |  |  |  | 10258 | G_1RVR_BND_G1! ID 1+1000 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-781_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101846 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 655.4 | 449.9 | 672 | 97.5 |  |  |  |  | 10268 | G_1RVR_BND_G1! ID 1+1010 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-791_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101847 | 18W | Approved | P3 | 32 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 983.4 | 266.5 | 1069 | 92 |  |  |  |  | 10268 | G_1RVR_BND_G1! ID 1+1010 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-791_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101848 | 18W | Approved | P3 | 32 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 188.3 | 128 | 199 | 94.6 |  |  |  |  | 10340 | G_1RVR_BND_G1! ID 1+P1_2-866_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-866_6ADMSCRK%,8FRANKLIN% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101849 | 18W | Approved | P3 | 32 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 261.8 | 212.1 | 278 | 94.2 |  |  |  |  | 10604 | G_1RVR_BND_G1! ID 1+1354 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1RVR_BND_G1! ID 1 | SPS: Clarksdale | No violation: below Rate A
101850 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 146.9 | 93.5 | 159 | 92.4 |  |  |  |  | 10776 | G_1RVR_BND_G1! ID 1+1533 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1314_8SHERIDAN%,8MAGNETCOVE% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101851 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 146.8 | 93.5 | 159 | 92.3 |  |  |  |  | 10813 | G_1RVR_BND_G1! ID 1+1570 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101852 | 18W | Approved | P3 | 32 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.7 | 17 | 159 | 92.3 |  |  |  |  | 11179 | G_1RVR_BND_G1! ID 1+P1_2-1735_FULTON!,HOPE 3! | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101853 | 18W | Approved | P3 | 32 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.7 | 21 | 157 | 96 |  |  |  |  | 11179 | G_1RVR_BND_G1! ID 1+P1_2-1735_FULTON!,HOPE 3! | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101854 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 148.4 | 113.6 | 150 | 98.9 |  |  |  |  | 11344 | G_1RVR_BND_G1! ID 1+2117 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101855 | 18W | Approved | P3 | 32 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 104.4 | 49 | 115 | 90.8 |  |  |  |  | 11344 | G_1RVR_BND_G1! ID 1+2117 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
101856 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.2 |  |  |  |  | 11496 | G_1WAT U3! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101857 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 11496 | G_1WAT U3! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101858 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.3 | 52.7 | 120 | 95.3 |  |  |  |  | 11628 | G_1WAT U3! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101859 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.2 |  |  |  |  | 11837 | G_1WAT U3! ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101860 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 11837 | G_1WAT U3! ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101861 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 430.2 | 314.6 | 470 | 91.5 |  |  |  |  | 11838 | G_1WAT U3! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101862 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.8 |  |  |  |  | 11880 | G_1WAT U3! ID 1+P1_2-500_2LK_CH_BULK!,2CHLOMAL! | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101863 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.8 | 171.5 | 225 | 91.9 |  |  |  |  | 11924 | G_1WAT U3! ID 1+P1_2-544_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-544_4RICHARD%,4SCOTT_1! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101864 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 211.1 | 171.5 | 225 | 93.8 |  |  |  |  | 11925 | G_1WAT U3! ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101865 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 203 | 163.5 | 225 | 90.2 |  |  |  |  | 11925 | G_1WAT U3! ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101866 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 231.1 | 171.5 | 225 | 102.7 |  |  |  |  | 11928 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 | None
101867 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 222.8 | 163.5 | 225 | 99 |  |  |  |  | 11928 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101868 | 18W | Approved | P3 | 32 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 212.4 | 152.8 | 225 | 94.4 |  |  |  |  | 11928 | G_1WAT U3! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101869 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 181.5 | 113.5 | 191 | 95 |  |  |  |  | 11945 | G_1WAT U3! ID 1+P1_2-565_4MEAUX!,6MEAUX! | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101870 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 181.5 | 113.5 | 191 | 95 |  |  |  |  | 11946 | G_1WAT U3! ID 1+P1_2-566_6MEAUX!,SELLRD6% | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101871 | 18W | Approved | P3 | 32 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1091.5 | 790.9 | 1186 | 92 |  |  |  |  | 12044 | G_1WAT U3! ID 1+P1_2-665_8WILLOW_GL%,8COLY% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-665_8WILLOW_GL%,8COLY% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
101872 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 614 | 449.9 | 672 | 91.4 |  |  |  |  | 12131 | G_1WAT U3! ID 1+P1_2-752_6COLY%,8COLY% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-752_6COLY%,8COLY% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101873 | 18W | Approved | P3 | 32 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 95.6 | 44.6 | 100 | 95.6 |  |  |  |  | 12140 | G_1WAT U3! ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101874 | 18W | Approved | P3 | 32 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 94.4 | 44 | 100 | 94.4 |  |  |  |  | 12140 | G_1WAT U3! ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101875 | 18W | Approved | P3 | 32 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 20.9 | 19.9 | 20 | 104.5 |  |  |  |  | 12144 | G_1WAT U3! ID 1+P1_2-765_2FRANCIS!,2PORT_HUD_B! | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WAT U3! ID 1 | Project Proposed |  | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
101876 | 18W | Approved | P3 | 32 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 273.8 | 155.5 | 300 | 91.3 |  |  |  |  | 12148 | G_1WAT U3! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101877 | 18W | Approved | P3 | 32 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 274.6 | 157.1 | 300 | 91.5 |  |  |  |  | 12149 | G_1WAT U3! ID 1+P1_2-770_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-770_4PORT_HUD!,6PORT_HUD% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101878 | 18W | Approved | P3 | 32 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | LN | 552.8 | 307.4 | 593 | 93.2 |  |  |  |  | 12151 | G_1WAT U3! ID 1+P1_2-772_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 2 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-772_6PORT_HUD%,6FANCY_PT% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101879 | 18W | Approved | P3 | 32 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 556.1 | 313.9 | 593 | 93.8 |  |  |  |  | 12152 | G_1WAT U3! ID 1+P1_2-773_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-773_6PORT_HUD%,6FANCY_PT% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101880 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 634 | 449.9 | 672 | 94.3 |  |  |  |  | 12159 | G_1WAT U3! ID 1+P1_2-781_6IBERVIL%,6BYULABUTTE! | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-781_6IBERVIL%,6BYULABUTTE! | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101881 | 18W | Approved | P3 | 32 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 634 | 449.9 | 672 | 94.3 |  |  |  |  | 12169 | G_1WAT U3! ID 1+P1_2-791_8BYULABUTTE%,6BYULABUTTE! | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-791_8BYULABUTTE%,6BYULABUTTE! | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
101882 | 18W | Approved | P3 | 32 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 183 | 112.3 | 199 | 91.9 |  |  |  |  | 12241 | G_1WAT U3! ID 1+P1_2-866_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-866_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101883 | 18W | Approved | P3 | 32 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 198.5 | 128 | 199 | 99.7 |  |  |  |  | 12241 | G_1WAT U3! ID 1+P1_2-866_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-866_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
101884 | 18W | Approved | P3 | 32 | 336136 6BOGALUS! 230 500025 BARKERS 6 230 1 | LN | 400 | 215.6 | 439 | 91.1 |  |  |  |  | 12244 | G_1WAT U3! ID 1+P1_2-869_6BOGALUS!,NSLID 6! | 336136 | 500025 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-869_6BOGALUS!,NSLID 6! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101885 | 18W | Approved | P3 | 32 | 336938 3REX BRWN-W! 115 336939 3REX BRWN-C! 115 Z1 | LN | 293.7 | 169.7 | 319 | 92.1 |  |  |  |  | 12413 | G_1WAT U3! ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336938 | 336939 | Z1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101886 | 18W | Approved | P3 | 32 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 262.2 | 212.1 | 278 | 94.3 |  |  |  |  | 12506 | G_1WAT U3! ID 1+P1_2-1135_3DELTA SES%,3CLARKSDALE! | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1WAT U3! ID 1 | SPS: Clarksdale | No violation: below Rate A
101887 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 148.6 | 93.5 | 159 | 93.4 |  |  |  |  | 12678 | G_1WAT U3! ID 1+P1_2-1314_8SHERIDAN%,8MAGNETCOVE% | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1314_8SHERIDAN%,8MAGNETCOVE% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101888 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 148.5 | 93.5 | 159 | 93.4 |  |  |  |  | 12715 | G_1WAT U3! ID 1+P1_2-1351_8HS EHV%,8MAGNETCOVE% | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1WAT U3! ID 1 |  | No violation: below Rate A
101889 | 18W | Approved | P3 | 32 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.7 | 17 | 159 | 92.3 |  |  |  |  | 13082 | G_1WAT U3! ID 1+P1_2-1735_FULTON!,HOPE 3! | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101890 | 18W | Approved | P3 | 32 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.7 | 21 | 157 | 96 |  |  |  |  | 13082 | G_1WAT U3! ID 1+P1_2-1735_FULTON!,HOPE 3! | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! | G_1WAT U3! ID 1 |  | No violation: below Rate A
101891 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 148.3 | 113.6 | 150 | 98.9 |  |  |  |  | 13247 | G_1WAT U3! ID 1+2117 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: below Rate A
101892 | 18W | Approved | P3 | 32 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 104.4 | 49 | 115 | 90.8 |  |  |  |  | 13247 | G_1WAT U3! ID 1+2117 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: below Rate A
101893 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 221 | 171.5 | 225 | 98.2 |  |  |  |  | 13443 | G_1NMIL U4! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101894 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 212.8 | 163.5 | 225 | 94.6 |  |  |  |  | 13443 | G_1NMIL U4! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U4! ID 1 |  | No violation: below Rate A
101895 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 221.5 | 171.5 | 225 | 98.4 |  |  |  |  | 13593 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101896 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 213.3 | 163.5 | 225 | 94.8 |  |  |  |  | 13593 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101897 | 18W | Approved | P3 | 32 | 335376 4ACADIA_GSU! 138 335377 4SCANLAN 138 1 | LN | 202.8 | 152.8 | 225 | 90.1 |  |  |  |  | 13593 | G_1NMIL U5! ID 1+P1_2-548_8RICHARD%,8WELLS% | 335376 | 335377 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
101898 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.1 |  |  |  |  | 13909 | G_1GGNS U1 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101899 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 13909 | G_1GGNS U1 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101900 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.3 |  |  |  |  | 14041 | G_1GGNS U1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101901 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 97.1 |  |  |  |  | 14250 | G_1GGNS U1 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101902 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 14250 | G_1GGNS U1 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101903 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 433.7 | 314.6 | 470 | 92.3 |  |  |  |  | 14251 | G_1GGNS U1 ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101904 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 97 |  |  |  |  | 14293 | G_1GGNS U1 ID 1+P1_2-500_2LK_CH_BULK!,2CHLOMAL! | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101905 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 206.5 | 171.5 | 225 | 91.8 |  |  |  |  | 14338 | G_1GGNS U1 ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101906 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 220 | 171.5 | 225 | 97.8 |  |  |  |  | 14341 | G_1GGNS U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101907 | 18W | Approved | P3 | 32 | 335375 4COL_ACADMY! 138 335376 4ACADIA_GSU! 138 1 | LN | 211.9 | 163.5 | 225 | 94.2 |  |  |  |  | 14341 | G_1GGNS U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335375 | 335376 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101908 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 185.5 | 113.5 | 191 | 97.1 |  |  |  |  | 14358 | G_1GGNS U1 ID 1+P1_2-565_4MEAUX!,6MEAUX! | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101909 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 185.5 | 113.5 | 191 | 97.1 |  |  |  |  | 14359 | G_1GGNS U1 ID 1+P1_2-566_6MEAUX!,SELLRD6% | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101910 | 18W | Approved | P3 | 32 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 92.4 | 44.6 | 100 | 92.4 |  |  |  |  | 14553 | G_1GGNS U1 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101911 | 18W | Approved | P3 | 32 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 91.2 | 44 | 100 | 91.2 |  |  |  |  | 14553 | G_1GGNS U1 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101912 | 18W | Approved | P3 | 32 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 534.2 | 313.9 | 593 | 90.1 |  |  |  |  | 14565 | G_1GGNS U1 ID 1+P1_2-773_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-773_6PORT_HUD%,6FANCY_PT% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101913 | 18W | Approved | P3 | 32 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 592.7 | 301.5 | 600 | 98.8 |  |  |  |  | 14826 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101914 | 18W | Approved | P3 | 32 | 336938 3REX BRWN-W! 115 336939 3REX BRWN-C! 115 Z1 | LN | 331.1 | 169.7 | 319 | 103.8 |  |  |  |  | 14826 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336938 | 336939 | Z1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101915 | 18W | Approved | P3 | 32 | 337016 3PICKENS! 115 337018 3MIDWAY MS+ 115 1 | LN | 102.9 | 38.5 | 108 | 95.3 |  |  |  |  | 14873 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337016 | 337018 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101916 | 18W | Approved | P3 | 32 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 104.3 | 56.1 | 108 | 96.6 |  |  |  |  | 14873 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
101917 | 18W | Approved | P3 | 32 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 263.6 | 212.1 | 278 | 94.8 |  |  |  |  | 14920 | G_1GGNS U1 ID 1+P1_2-1135_3DELTA SES%,3CLARKSDALE! | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1GGNS U1 ID 1 | SPS: Clarksdale | No violation: below Rate A
101918 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 152.3 | 93.5 | 159 | 95.8 |  |  |  |  | 15092 | G_1GGNS U1 ID 1+P1_2-1314_8SHERIDAN%,8MAGNETCOVE% | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1314_8SHERIDAN%,8MAGNETCOVE% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101919 | 18W | Approved | P3 | 32 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 152.3 | 93.5 | 159 | 95.8 |  |  |  |  | 15129 | G_1GGNS U1 ID 1+P1_2-1351_8HS EHV%,8MAGNETCOVE% | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101920 | 18W | Approved | P3 | 32 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.7 | 17 | 159 | 92.3 |  |  |  |  | 15497 | G_1GGNS U1 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101921 | 18W | Approved | P3 | 32 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.6 | 21 | 157 | 96 |  |  |  |  | 15497 | G_1GGNS U1 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101922 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 147.6 | 113.6 | 150 | 98.4 |  |  |  |  | 15662 | G_1GGNS U1 ID 1+2117 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101923 | 18W | Approved | P3 | 32 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 105 | 49 | 115 | 91.3 |  |  |  |  | 15662 | G_1GGNS U1 ID 1+2117 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1GGNS U1 ID 1 |  | No violation: below Rate A
101924 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 207.1 | 171.5 | 225 | 92 |  |  |  |  | 16161 | G_1ANO U2 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1ANO U2 ID 1 |  | No violation: below Rate A
101925 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.1 |  |  |  |  | 16382 | G_1ISES U1 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101926 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 16382 | G_1ISES U1 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101927 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.3 | 133 | 206 | 91.4 |  |  |  |  | 16433 | G_1ISES U1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101928 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.4 |  |  |  |  | 16514 | G_1ISES U1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101929 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 97.1 |  |  |  |  | 16723 | G_1ISES U1 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101930 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 16723 | G_1ISES U1 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101931 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 439.5 | 314.6 | 470 | 93.5 |  |  |  |  | 16724 | G_1ISES U1 ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1ISES U1 ID 1 |  | No violation: below Rate A
101932 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.7 |  |  |  |  | 16766 | G_1ISES U1 ID 1+P1_2-500_2LK_CH_BULK!,2CHLOMAL! | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101933 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 203.6 | 171.5 | 225 | 90.5 |  |  |  |  | 16811 | G_1ISES U1 ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101934 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 209.2 | 171.5 | 225 | 93 |  |  |  |  | 16814 | G_1ISES U1 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1ISES U1 ID 1 |  | No violation: below Rate A
101935 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.7 | 113.5 | 191 | 97.7 |  |  |  |  | 16831 | G_1ISES U1 ID 1+P1_2-565_4MEAUX!,6MEAUX! | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101936 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.4 | 113.5 | 191 | 97.6 |  |  |  |  | 16832 | G_1ISES U1 ID 1+P1_2-566_6MEAUX!,SELLRD6% | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101937 | 18W | Approved | P3 | 32 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 92.5 | 44.6 | 100 | 92.5 |  |  |  |  | 17026 | G_1ISES U1 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1ISES U1 ID 1 |  | No violation: below Rate A
101938 | 18W | Approved | P3 | 32 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 91.3 | 44 | 100 | 91.3 |  |  |  |  | 17026 | G_1ISES U1 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1ISES U1 ID 1 |  | No violation: below Rate A
101939 | 18W | Approved | P3 | 32 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 534.7 | 313.9 | 593 | 90.2 |  |  |  |  | 17038 | G_1ISES U1 ID 1+P1_2-773_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-773_6PORT_HUD%,6FANCY_PT% | G_1ISES U1 ID 1 |  | No violation: below Rate A
101940 | 18W | Approved | P3 | 32 | 500510 MADISON6 230 500520 MANDEV 6 230 1 | LN | 409.9 | 249.6 | 449 | 91.3 |  |  |  |  | 17241 | G_1ISES U1 ID 1+P1_2-981_6MICHO%,FRONTST6! | 500510 | 500520 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-981_6MICHO%,FRONTST6! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101941 | 18W | Approved | P3 | 32 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 259.5 | 212.1 | 278 | 93.4 |  |  |  |  | 17393 | G_1ISES U1 ID 1+P1_2-1135_3DELTA SES%,3CLARKSDALE! | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1ISES U1 ID 1 | SPS: Clarksdale | No violation: below Rate A
101942 | 18W | Approved | P3 | 32 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.6 | 17 | 159 | 92.2 |  |  |  |  | 17962 | G_1ISES U1 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101943 | 18W | Approved | P3 | 32 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.6 | 21 | 157 | 95.9 |  |  |  |  | 17962 | G_1ISES U1 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! | G_1ISES U1 ID 1 |  | No violation: below Rate A
101944 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 147.7 | 113.6 | 150 | 98.5 |  |  |  |  | 18127 | G_1ISES U1 ID 1+2117 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U1 ID 1 |  | No violation: below Rate A
101945 | 18W | Approved | P3 | 32 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 105 | 49 | 115 | 91.3 |  |  |  |  | 18127 | G_1ISES U1 ID 1+2117 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U1 ID 1 |  | No violation: below Rate A
101946 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32.1 | 26 | 33 | 97.1 |  |  |  |  | 18235 | G_1ISES U2 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101947 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 18235 | G_1ISES U2 ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101948 | 18W | Approved | P3 | 32 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 188.2 | 133 | 206 | 91.4 |  |  |  |  | 18286 | G_1ISES U2 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
101949 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 52.7 | 120 | 95.4 |  |  |  |  | 18367 | G_1ISES U2 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101950 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 32 | 26 | 33 | 97.1 |  |  |  |  | 18576 | G_1ISES U2 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101951 | 18W | Approved | P3 | 32 | 335253 2LACASSINE 69.0 335254 2CARTER! 69.0 1 | LN | 29.8 | 22.7 | 33 | 90.3 |  |  |  |  | 18576 | G_1ISES U2 ID 1+P1_2-457_6CARLYSS%,6BOUDOIN% | 335253 | 335254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-457_6CARLYSS%,6BOUDOIN% | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101952 | 18W | Approved | P3 | 32 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 439.5 | 314.6 | 470 | 93.5 |  |  |  |  | 18577 | G_1ISES U2 ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1ISES U2 ID 1 |  | No violation: below Rate A
101953 | 18W | Approved | P3 | 32 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.9 | 26 | 33 | 96.7 |  |  |  |  | 18619 | G_1ISES U2 ID 1+P1_2-500_2LK_CH_BULK!,2CHLOMAL! | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-500_2LK_CH_BULK!,2CHLOMAL! | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
101954 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 203.5 | 171.5 | 225 | 90.5 |  |  |  |  | 18664 | G_1ISES U2 ID 1+P1_2-545_4RICHARD%,4SCOTT_1! | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-545_4RICHARD%,4SCOTT_1! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101955 | 18W | Approved | P3 | 32 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 209.1 | 171.5 | 225 | 92.9 |  |  |  |  | 18667 | G_1ISES U2 ID 1+P1_2-548_8RICHARD%,8WELLS% | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-548_8RICHARD%,8WELLS% | G_1ISES U2 ID 1 |  | No violation: below Rate A
101956 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.7 | 113.5 | 191 | 97.7 |  |  |  |  | 18684 | G_1ISES U2 ID 1+P1_2-565_4MEAUX!,6MEAUX! | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101957 | 18W | Approved | P3 | 32 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 186.5 | 113.5 | 191 | 97.6 |  |  |  |  | 18685 | G_1ISES U2 ID 1+P1_2-566_6MEAUX!,SELLRD6% | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1ISES U2 ID 1 | Project Proposed | No violation: below Rate A | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
101958 | 18W | Approved | P3 | 32 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 92.5 | 44.6 | 100 | 92.5 |  |  |  |  | 18879 | G_1ISES U2 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1ISES U2 ID 1 |  | No violation: below Rate A
101959 | 18W | Approved | P3 | 32 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 91.3 | 44 | 100 | 91.3 |  |  |  |  | 18879 | G_1ISES U2 ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1ISES U2 ID 1 |  | No violation: below Rate A
101960 | 18W | Approved | P3 | 32 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 534.7 | 313.9 | 593 | 90.2 |  |  |  |  | 18891 | G_1ISES U2 ID 1+P1_2-773_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-773_6PORT_HUD%,6FANCY_PT% | G_1ISES U2 ID 1 |  | No violation: below Rate A
101961 | 18W | Approved | P3 | 32 | 500510 MADISON6 230 500520 MANDEV 6 230 1 | LN | 409.7 | 249.6 | 449 | 91.2 |  |  |  |  | 19094 | G_1ISES U2 ID 1+P1_2-981_6MICHO%,FRONTST6! | 500510 | 500520 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-981_6MICHO%,FRONTST6! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101962 | 18W | Approved | P3 | 32 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 259 | 212.1 | 278 | 93.2 |  |  |  |  | 19246 | G_1ISES U2 ID 1+P1_2-1135_3DELTA SES%,3CLARKSDALE! | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1ISES U2 ID 1 | SPS: Clarksdale | No violation: below Rate A
101963 | 18W | Approved | P3 | 32 | 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | LN | 146.6 | 17 | 159 | 92.2 |  |  |  |  | 19823 | G_1ISES U2 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338874 | 338875 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1735_FULTON!,HOPE 3! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101964 | 18W | Approved | P3 | 32 | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | LN | 150.6 | 21 | 157 | 95.9 |  |  |  |  | 19823 | G_1ISES U2 ID 1+P1_2-1735_FULTON!,HOPE 3! | 338875 | 503912 | 1 |  | 115 | 115 | 327 | EES-EAI | 520 | AEPW | P1_2-1735_FULTON!,HOPE 3! | G_1ISES U2 ID 1 |  | No violation: below Rate A
101965 | 18W | Approved | P3 | 32 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 147.7 | 113.6 | 150 | 98.5 |  |  |  |  | 19988 | G_1ISES U2 ID 1+2117 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | No violation: below Rate A
101966 | 18W | Approved | P3 | 32 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 105 | 49 | 115 | 91.3 |  |  |  |  | 19988 | G_1ISES U2 ID 1+2117 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | No violation: below Rate A
101967 | 18W | Approved | P3 | 32 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 115 | 52.7 | 120 | 95.8 |  |  |  |  | 20090 | G_G1DOLHIL! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
101968 | 18W | Approved | P3 | 32 | 334314 4URLAND! 138 334315 4WOODVILLE 138 1 | LN | 133.2 | 101.7 | 145 | 91.9 |  |  |  |  | 20090 | G_G1DOLHIL! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334314 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
101969 | 18W | Approved | P3 | 32 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 83 | 38.3 | 77 | 107.7 |  |  |  |  | 20115 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101970 | 18W | Approved | P3 | 32 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 84.2 | 39.5 | 77 | 109.3 |  |  |  |  | 20115 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101971 | 18W | Approved | P3 | 32 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 79.6 | 39.1 | 77 | 103.3 |  |  |  |  | 20115 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101972 | 18W | Approved | P3 | 32 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 110.8 | 51.2 | 111 | 99.8 |  |  |  |  | 20116 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101973 | 18W | Approved | P3 | 32 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 127.1 | 66 | 115 | 110.5 |  |  |  |  | 20116 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101974 | 18W | Approved | P3 | 32 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 80.2 | 39.1 | 77 | 104.2 |  |  |  |  | 20116 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101975 | 18W | Approved | P3 | 32 | 337365 3SPRINGHILL 115 337500 3TAYLOR 115 1 | LN | 112.4 | 27.9 | 120 | 93.7 |  |  |  |  | 20116 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337365 | 337500 | 1 |  | 115 | 115 | 351 | EES | 327 | EES-EAI | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101976 | 18W | Approved | P3 | 32 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 75.9 | 38.3 | 77 | 98.6 |  |  |  |  | 20127 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101977 | 18W | Approved | P3 | 32 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 77.2 | 39.5 | 77 | 100.2 |  |  |  |  | 20127 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101978 | 18W | Approved | P3 | 32 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 73.6 | 39.1 | 77 | 95.6 |  |  |  |  | 20127 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101979 | 18W | Approved | P3 | 32 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 101.1 | 51.2 | 111 | 91.1 |  |  |  |  | 20354 | G_PIRKEY 1 ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
101980 | 18W | Approved | P3 | 32 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 117.1 | 66 | 115 | 101.8 |  |  |  |  | 20354 | G_PIRKEY 1 ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
101981 | 18W | Approved | P3 | 32 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 70.4 | 39.1 | 77 | 91.5 |  |  |  |  | 20354 | G_PIRKEY 1 ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
101982 | 18L | Approved | P0 | 33 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101.5 | 101.5 | 112 | 90.7 |  |  |  |  | 0 | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | Facility: Radial
101983 | 18L | Approved | P0 | 33 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 333.1 | 360 | 92.5 |  |  |  |  | 0 | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
101984 | 18L | Approved | P0 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.2 | 35.2 | 39 | 90.4 |  |  |  |  | 0 | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
101985 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 310.6 | 225.6 | 278 | 111.7 |  |  |  |  | 5985 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+108 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! | G_1WHT BLUF U1 ID 1 | SPS: Clarksdale
101986 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 310.5 | 225.6 | 278 | 111.7 |  |  |  |  | 5992 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+115 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! | G_1LSPWRU1 ID 1 | SPS: Clarksdale
101987 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 306.8 | 225.6 | 278 | 110.4 |  |  |  |  | 6132 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+97 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1SLSBAU3 ID 5 | SPS: Clarksdale
101988 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 307.1 | 225.6 | 278 | 110.5 |  |  |  |  | 6143 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+108 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1WHT BLUF U1 ID 1 | SPS: Clarksdale
101989 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 307 | 225.6 | 278 | 110.4 |  |  |  |  | 6150 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+115 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1LSPWRU1 ID 1 | SPS: Clarksdale
101990 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.4 |  |  |  |  | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 |  | Facility: Radial
101991 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.4 |  |  |  |  | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 |  | Facility: Radial
101992 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.4 | 35.2 | 39 | 103.7 |  |  |  |  | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 |  | Facility: Radial
101993 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.4 |  |  |  |  | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 |  | Facility: Radial
101994 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.4 |  |  |  |  | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 |  | Facility: Radial
101995 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.4 |  |  |  |  | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 |  | Facility: Radial
101996 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.5 | 35.2 | 39 | 103.9 |  |  |  |  | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 |  | Facility: Radial
101997 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.3 |  |  |  |  | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 |  | Facility: Radial
101998 | 18L | Approved | P3 | 33 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 40.3 | 35.2 | 39 | 103.3 |  |  |  |  | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 |  | Facility: Radial
101999 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 235.2 | 77.3 | 204 | 115.3 |  |  |  |  | 12457 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1BCAJUN2_U2% ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1BCAJUN2_U2% ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102000 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.8 | 54.8 | 233 | 91.3 |  |  |  |  | 12457 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1BCAJUN2_U2% ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1BCAJUN2_U2% ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102001 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.9 | 77.3 | 204 | 113.7 |  |  |  |  | 12467 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102002 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.9 | 77.3 | 204 | 113.7 |  |  |  |  | 12468 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102003 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.5 | 77.3 | 204 | 113.5 |  |  |  |  | 12561 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102004 | 18L | Approved | P3 | 33 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 112.8 | 35.8 | 125 | 90.2 |  |  |  |  | 12562 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U2 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102005 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 232 | 77.3 | 204 | 113.7 |  |  |  |  | 12562 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U2 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102006 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 235.1 | 77.3 | 204 | 115.2 |  |  |  |  | 12584 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102007 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.6 | 54.8 | 233 | 91.2 |  |  |  |  | 12584 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102008 | 18L | Approved | P3 | 33 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 75 | 700 | 92.4 |  |  |  |  | 12590 | P1_2-1664_DOLHILL7%, SW SHV 7+G_G1WKRAFT! ID 3 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_G1WKRAFT! ID 3 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102009 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.4 | 77.3 | 204 | 113.4 |  |  |  |  | 12600 | P1_2-1664_DOLHILL7%, SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102010 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 234.2 | 77.3 | 204 | 114.8 |  |  |  |  | 12602 | P1_2-1664_DOLHILL7%, SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102011 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 211.7 | 54.8 | 233 | 90.9 |  |  |  |  | 12602 | P1_2-1664_DOLHILL7%, SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102012 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 241.9 | 77.3 | 204 | 118.6 |  |  |  |  | 12603 | P1_2-1664_DOLHILL7%, SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102013 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 219.1 | 54.8 | 233 | 94.1 |  |  |  |  | 12603 | P1_2-1664_DOLHILL7%, SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102014 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 243.9 | 77.3 | 204 | 119.5 |  |  |  |  | 12604 | P1_2-1664_DOLHILL7%, SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102015 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 221.4 | 54.8 | 233 | 95 |  |  |  |  | 12604 | P1_2-1664_DOLHILL7%, SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102016 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 234.8 | 77.3 | 204 | 115.1 |  |  |  |  | 12605 | P1_2-1664_DOLHILL7%, SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102017 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.3 | 54.8 | 233 | 91.1 |  |  |  |  | 12605 | P1_2-1664_DOLHILL7%, SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102018 | 18L | Approved | P3 | 33 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.6 | 77.3 | 204 | 113.5 |  |  |  |  | 12606 | P1_2-1664_DOLHILL7%, SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
102019 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 513.8 | 323.7 | 470 | 109.3 |  |  |  |  | 13267 | G_1G4SABIN! ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
102020 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 485.3 | 323.7 | 470 | 103.3 |  |  |  |  | 13270 | G_1G5SABIN! ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G5SABIN! ID 1 | Reduce PPG Plant
102021 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 13737 | G_1ATTALA S1 ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1ATTALA S1 ID 1 |  | No violation: below Rate A
102022 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.1 | 323.7 | 470 | 95.5 |  |  |  |  | 13986 | G_1ATTALA S1 ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1ATTALA S1 ID 1 |  | No violation: below Rate A
102023 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 14340 | G_1ATTALA S1 ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1ATTALA S1 ID 1 |  | No violation: below Rate A
102024 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 262.9 | 225.6 | 278 | 94.6 |  |  |  |  | 14530 | G_1ATTALA S1 ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1ATTALA S1 ID 1 | SPS: Clarksdale | No violation: below Rate A
102025 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 15382 | G_1SLSBAU3 ID 5+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1SLSBAU3 ID 5 |  | No violation: below Rate A
102026 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.4 | 323.7 | 470 | 95.6 |  |  |  |  | 15633 | G_1SLSBAU3 ID 5+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1SLSBAU3 ID 5 |  | No violation: below Rate A
102027 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 16006 | G_1SLSBAU3 ID 5+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1SLSBAU3 ID 5 |  | No violation: below Rate A
102028 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 266 | 225.6 | 278 | 95.7 |  |  |  |  | 16269 | G_1SLSBAU3 ID 5+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1SLSBAU3 ID 5 | SPS: Clarksdale | No violation: below Rate A
102029 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 17199 | G_1WHT BLUF U1 ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1WHT BLUF U1 ID 1 |  | No violation: below Rate A
102030 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.9 | 323.7 | 470 | 95.7 |  |  |  |  | 17450 | G_1WHT BLUF U1 ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1WHT BLUF U1 ID 1 |  | No violation: below Rate A
102031 | 18L | Approved | P3 | 33 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 338.2 | 333.1 | 360 | 94 |  |  |  |  | 17475 | G_1WHT BLUF U1 ID 1+P1_2-483_6NELSON%, 8NELSON% | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-483_6NELSON%,8NELSON% | G_1WHT BLUF U1 ID 1 |  | Facility: GSU
102032 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 17824 | G_1WHT BLUF U1 ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1WHT BLUF U1 ID 1 |  | No violation: below Rate A
102033 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 265 | 225.6 | 278 | 95.3 |  |  |  |  | 18101 | G_1WHT BLUF U1 ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1WHT BLUF U1 ID 1 | SPS: Clarksdale | No violation: below Rate A
102034 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 19007 | G_1PERRYV_C1! ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1PERRYV_C1! ID 1 |  | No violation: below Rate A
102035 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.3 | 323.7 | 470 | 95.6 |  |  |  |  | 19258 | G_1PERRYV_C1! ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1PERRYV_C1! ID 1 |  | No violation: below Rate A
102036 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 19632 | G_1PERRYV_C1! ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1PERRYV_C1! ID 1 |  | No violation: below Rate A
102037 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 262.8 | 225.6 | 278 | 94.5 |  |  |  |  | 19909 | G_1PERRYV_C1! ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1PERRYV_C1! ID 1 | SPS: Clarksdale | No violation: below Rate A
102038 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 20829 | G_1ISES U1 ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1ISES U1 ID 1 |  | No violation: below Rate A
102039 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.7 | 323.7 | 470 | 95.7 |  |  |  |  | 21080 | G_1ISES U1 ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1ISES U1 ID 1 |  | No violation: below Rate A
102040 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 21454 | G_1ISES U1 ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1ISES U1 ID 1 |  | No violation: below Rate A
102041 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 263.6 | 225.6 | 278 | 94.8 |  |  |  |  | 21731 | G_1ISES U1 ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1ISES U1 ID 1 | SPS: Clarksdale | No violation: below Rate A
102042 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 22640 | G_1ISES U2 ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1ISES U2 ID 1 |  | No violation: below Rate A
102043 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.7 | 323.7 | 470 | 95.7 |  |  |  |  | 22891 | G_1ISES U2 ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1ISES U2 ID 1 |  | No violation: below Rate A
102044 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 23265 | G_1ISES U2 ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1ISES U2 ID 1 |  | No violation: below Rate A
102045 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 263.4 | 225.6 | 278 | 94.8 |  |  |  |  | 23542 | G_1ISES U2 ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1ISES U2 ID 1 | SPS: Clarksdale | No violation: below Rate A
102046 | 18L | Approved | P3 | 33 | 334208 4JACINTO% 138 334231 4PELCNRD! 138 1 | LN | 194.2 | 131.6 | 206 | 94.3 |  |  |  |  | 24456 | G_1LSPWRU1 ID 1+P1_2-198_4SHEPERD!, 4PELCNRD! | 334208 | 334231 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-198_4SHEPERD!,4PELCNRD! | G_1LSPWRU1 ID 1 |  | No violation: below Rate A
102047 | 18L | Approved | P3 | 33 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 449.4 | 323.7 | 470 | 95.6 |  |  |  |  | 24707 | G_1LSPWRU1 ID 1+P1_2-458_6CARLYSS%, 6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1LSPWRU1 ID 1 |  | No violation: below Rate A
102048 | 18L | Approved | P3 | 33 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 105.4 | 69.5 | 115 | 91.6 |  |  |  |  | 25080 | G_1LSPWRU1 ID 1+P1_2-835_3GMEADW!, 3BARATA! | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-835_3GMEADW!,3BARATA! | G_1LSPWRU1 ID 1 |  | No violation: below Rate A
102049 | 18L | Approved | P3 | 33 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 264.6 | 225.6 | 278 | 95.2 |  |  |  |  | 25342 | G_1LSPWRU1 ID 1+1293 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1135_3DELTA SES%,3CLARKSDALE! | G_1LSPWRU1 ID 1 | SPS: Clarksdale | No violation: below Rate A
102050 | 18S | Approved | P2 | 34 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 419.1 | 294.3 | 448 | 93.5 |  |  |  |  | 4 | 8MABELVALE% - 8WRIGHTSVLE% 500 1+ 8MABELVALE% 500/ | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-8MABELVALE%_500_B5926 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
102051 | 18S | Approved | P2 | 34 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 407 | 294.3 | 448 | 90.8 |  |  |  |  | 5 | 8MABELVALE% - 8ANO% 500 1+ 8MABELVALE% 500/115 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-8MABELVALE%_500_B5914 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
102052 | 18S | Approved | P2 | 34 | 337804 3MABLVALE-E! 115 337808 8MABELVALE% 500 2 | TR | 446.7 | 294.3 | 448 | 99.7 |  |  |  |  | 6 | 8MABELVALE% - 8MAYFLOWER% 500 1 + 8MABELVALE% 500 | 337804 | 337808 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-8MABELVALE%_500_B5906 |  | Project Proposed | No violation: below Rate A | 12-EAI-019-CP | 2016-06-01 | Replace Mabelvale 500-115 kV autos
102053 | 18S | Approved | P2 | 34 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 494.4 | 235.3 | 420 | 117.7 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-8MAYFLOWER%500_B8105 |  | Project Proposed |  | 12-EAI-021-CP | 2017-12-01 | Reconfigure Mayflower 500 kV bus to eliminate breaker failure impact on transformers
102054 | 18S | Approved | P2 | 34 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 379.5 | 180.1 | 266 | 142.7 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102055 | 18S | Approved | P2 | 34 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 348.1 | 140.7 | 266 | 130.8 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102056 | 18S | Approved | P2 | 34 | 338007 3BEEBE 115 338756 3WARD# 115 1 | LN | 247.2 | 48.5 | 266 | 92.9 |  |  |  |  | 8 | ISES 161kV bus #1 | 338007 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102057 | 18S | Approved | P2 | 34 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 135.6 | 107.7 | 148 | 91.6 |  |  |  |  | 8 | ISES 161kV bus #1 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed | No violation: below Rate A | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102058 | 18S | Approved | P2 | 34 | 338130 5CALICO ROCK 161 505448 NORFORK5 161 1 | LN | 150.4 | 77.5 | 148 | 101.6 |  |  |  |  | 8 | ISES 161kV bus #1 | 338130 | 505448 | 1 |  | 161 | 161 | 327 | EES-EAI | 515 | SWPA | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102059 | 18S | Approved | P2 | 34 | 336525 3SMITHDALE+ 115 336526 3ARLINGTON+ 115 1 | LN | 153.9 | 99.2 | 161 | 95.6 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336525 | 336526 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102060 | 18S | Approved | P2 | 34 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 160.6 | 105.7 | 161 | 99.8 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102061 | 18S | Approved | P2 | 34 | 336551 3MCCOMB! 115 336552 3NORFIELD+ 115 1 | LN | 193.1 | 103.1 | 199 | 97 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336551 | 336552 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102062 | 18S | Approved | P2 | 34 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 213.4 | 121.7 | 199 | 107.2 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102063 | 18S | Approved | P2 | 34 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 235.5 | 142.2 | 199 | 118.3 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102064 | 18S | Approved | P2 | 34 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 180 | 178.7 | 193 | 93.3 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | Facility: Radial | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102065 | 18S | Approved | P6 | 34 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | LN | 110.5 | 71.3 | 115 | 96.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 303325 | 337331 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102066 | 18S | Approved | P6 | 34 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | LN | 136.8 | 49.2 | 120 | 114 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336500 | 336785 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102067 | 18S | Approved | P6 | 34 | 336785 3FAYETTE 115 336786 3LORMAN+ 115 1 | LN | 159 | 64.8 | 161 | 98.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336785 | 336786 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102068 | 18S | Approved | P6 | 34 | 336786 3LORMAN+ 115 336788 3PORTGIBSON! 115 1 | LN | 170.5 | 75.9 | 161 | 105.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336786 | 336788 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102069 | 18S | Approved | P6 | 34 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 203.2 | 103.7 | 161 | 126.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102070 | 18S | Approved | P6 | 34 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | LN | 224.2 | 126.8 | 199 | 112.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336790 | 336800 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102071 | 18S | Approved | P6 | 34 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 299 | 122.2 | 239 | 125.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
102072 | 18S | Approved | P6 | 34 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 183.3 | 83 | 161 | 113.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
102073 | 18S | Approved | P6 | 34 | 336804 3VICKSBURG! 115 336805 3WATERWAYS 115 1 | LN | 344.2 | 90.4 | 239 | 144 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336804 | 336805 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102074 | 18S | Approved | P6 | 34 | 336805 3WATERWAYS 115 336806 3E.VICKSBRG+ 115 1 | LN | 333.1 | 80.1 | 260 | 128.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336805 | 336806 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102075 | 18S | Approved | P6 | 34 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 312.6 | 60.9 | 161 | 194.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102076 | 18S | Approved | P6 | 34 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 302.4 | 51.3 | 161 | 187.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102077 | 18S | Approved | P6 | 34 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 261.9 | 23.7 | 161 | 162.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102078 | 18S | Approved | P6 | 34 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 181.6 | 178.7 | 193 | 94.1 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | Facility: Radial | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102079 | 18S | Approved | P6 | 34 | 336960 3SE.VICKSBRG 115 336961 3BOVINA 115 1 | LN | 173.9 | 73.8 | 176 | 98.8 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336960 | 336961 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102080 | 18S | Approved | P6 | 34 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 166 | 53 | 111 | 149.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102081 | 18S | Approved | P6 | 34 | 336966 3REDWOOD+ 115 336967 3ONWARD+ 115 1 | LN | 109.2 | 45.9 | 120 | 91 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336966 | 336967 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102082 | 18S | Approved | P6 | 34 | 336967 3ONWARD+ 115 336968 3ROLING FRK! 115 1 | LN | 105.8 | 42.5 | 111 | 95.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336967 | 336968 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102083 | 18S | Approved | P6 | 34 | 336974 3TINSLEY+ 115 336976 3FLOWERS+ 115 1 | LN | 158.8 | 46.1 | 161 | 98.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336974 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102084 | 18S | Approved | P6 | 34 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 122.7 | 82.5 | 115 | 106.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102085 | 18S | Approved | P3 | 34 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | LN | 290.8 | 211.5 | 320 | 90.9 |  |  |  |  | 11 | 6GYPSY% 230/115 1+ 1WAT U3! 25.0 Id:1 | 336220 | 336230 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | 6GYPSY% 230/115 1 | 1WATU3! 25.0 Id:1 |  | No violation: below Rate A
102086 | 18S | Approved | P3 | 34 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 634.7 | 425.9 | 672 | 94.5 |  |  |  |  | 12 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G1_G2_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G1_G2_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102087 | 18S | Approved | P3 | 34 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 621.3 | 425.9 | 672 | 92.5 |  |  |  |  | 13 | 8BYULABUTTE% 500/230 1 + 1WILL_GL_G4 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8BYULABUTTE% 500/230 1 | 1WILL_GL_G4 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102088 | 18S | Approved | P3 | 34 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1293.1 | 295 | 1069 | 121 |  |  |  |  | 16 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102089 | 18S | Approved | P3 | 34 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 616.2 | 425.9 | 672 | 91.7 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102090 | 18S | Approved | P3 | 34 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1305.9 | 838.7 | 1186 | 110.1 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102091 | 18S | Approved | P3 | 34 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 95.9 | 94.8 | 93 | 103.1 |  |  |  |  | 17 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 |  | Delta: No worse than P0
102092 | 18S | Approved | P3 | 34 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 226.8 | 168.7 | 243 | 93.3 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
102093 | 18S | Approved | P3 | 34 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 206.9 | 86.5 | 206 | 100.5 |  |  |  |  | 18 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
102094 | 18S | Approved | P3 | 34 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 221.7 | 143.8 | 206 | 107.6 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id:1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
102095 | 18S | Approved | P3 | 34 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 193 | 115.3 | 206 | 93.7 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id:1 | Project Proposed | No violation: below Rate A | 13-ETI-013-CP | 2017-06-01 | Reconductor Egypt-Panorama 138 kV
102096 | 18S | Approved | P3 | 34 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 186.1 | 108.4 | 206 | 90.3 |  |  |  |  | 19 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id:1 |  | No violation: below Rate A
102097 | 18S | Approved | P3 | 34 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 242.2 | 143.8 | 206 | 117.6 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
102098 | 18S | Approved | P3 | 34 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 213.5 | 115.3 | 206 | 103.6 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! |  | Contingency: P1+2G1; internal study
102099 | 18S | Approved | P3 | 34 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 206.5 | 108.4 | 206 | 100.3 |  |  |  |  | 20 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! |  | Contingency: P1+2G1; internal study
102100 | 18S | Approved | P3 | 34 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 226.8 | 168.7 | 243 | 93.3 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2230 1 | 1G1LEWIS! 22.0 Id:1 |  | No violation: below Rate A
102101 | 18S | Approved | P3 | 34 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 207 | 86.5 | 206 | 100.5 |  |  |  |  | 21 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
102102 | 18S | Approved | P3 | 34 | 334360 6HELBIG! 230 334364 6GEOTOWN! 230 1 | LN | 319.2 | 148 | 351 | 91 |  |  |  |  | 26 | 6CHINA% - 6SABINE% 230 1 + 1G1LEWIS! 22.0 Id:1 | 334360 | 334364 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 6CHINA% - 6SABINE% 230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
102103 | 18S | Approved | P3 | 34 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.9 | 331.8 | 360 | 92.8 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 |  | Facility: GSU
102104 | 18S | Approved | P3 | 34 | 334325 8HARTBRG% 500 334363 6HARTBRG! 230 1 | TR | 739 | 288 | 801 | 92.3 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334325 | 334363 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
102105 | 18S | Approved | P3 | 34 | 334360 6HELBIG! 230 334361 6MCLEWIS 230 1 | LN | 657.5 | 218.9 | 681 | 96.6 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334360 | 334361 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
102106 | 18S | Approved | P3 | 34 | 334362 6INLAND 230 334363 6HARTBRG! 230 1 | LN | 719.5 | 277.9 | 797 | 90.3 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 334362 | 334363 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
102107 | 18S | Approved | P3 | 34 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 425.9 | 258.9 | 470 | 90.6 |  |  |  |  | 27 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 |  | No violation: below Rate A
102109 | 18S | Approved | P3 | 34 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 196.4 | 143.8 | 206 | 95.3 |  |  |  |  | 29 | 7GRIMES% - CROCKET7 345 1 +1FRNTR 1! 18.0 Id:1 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 7GRIMES% - CROCKET7 345 1 | 1FRNTR 1!18.0 Id:1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
102110 | 18S | Approved | P1 | 34 | 334252 26L594TAP 69.0 334254 2QUALTY 69.0 1 | LN | 26.7 | 2.4 | 29.3 | 91 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334252 | 334254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102111 | 18S | Approved | P1 | 34 | 334254 2QUALTY 69.0 334255 2BATSON! 69.0 NO | LN | 27.2 | 0 | 29.3 | 92.8 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334254 | 334255 | NO |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102112 | 18S | Approved | P1 | 34 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 36.7 | 11.9 | 29.3 | 125.3 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102113 | 18S | Approved | P1 | 34 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 37.4 | 12 | 29.3 | 127.6 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102114 | 18S | Approved | P1 | 34 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 37.9 | 12.2 | 29.3 | 129.3 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102115 | 18S | Approved | P1 | 34 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 38.5 | 12.2 | 29.3 | 131.4 |  |  |  |  | 30 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102116 | 18S | Approved | P1 | 34 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 27.4 | 11.9 | 29.3 | 93.4 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102117 | 18S | Approved | P1 | 34 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 28.2 | 12 | 29.3 | 96.4 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102118 | 18S | Approved | P1 | 34 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 28.8 | 12.2 | 29.3 | 98.3 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102119 | 18S | Approved | P1 | 34 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 29.5 | 12.2 | 29.3 | 100.8 |  |  |  |  | 33 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102120 | 18S | Approved | P3 | 34 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.2 | 331.8 | 360 | 92.5 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 |  | Facility: GSU
102121 | 18S | Approved | P3 | 34 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 658.9 | 301.7 | 560 | 117.7 |  |  |  |  | 35 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
102122 | 18W | Approved | P2 | 35 | 337930 3MAYFLOWER% 115 337937 8MAYFLOWER% 500 3 | TR | 380.4 | 181.2 | 420 | 90.6 |  |  |  |  | 7 | 8MAYFLOWER% 500/115 1 + 8MAYFLOWER% 500/115 2 | 337930 | 337937 | 3 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-8MAYFLOWER%500_B8105 |  | Project Proposed | No violation: below Rate A | 12-EAI-021-CP | 2017-12-01 | Reconfigure Mayflower 500 kV bus to eliminate breaker failure impact on transformers
102123 | 18W | Approved | P2 | 35 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 298.3 | 145.9 | 266 | 112.1 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102124 | 18W | Approved | P2 | 35 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 272.2 | 115.8 | 266 | 102.3 |  |  |  |  | 8 | ISES 161kV bus #1 | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
102125 | 18W | Approved | P2 | 35 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | LN | 145.4 | 91.3 | 161 | 90.3 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336526 | 336559 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102126 | 18W | Approved | P2 | 35 | 336551 3MCCOMB! 115 336552 3NORFIELD+ 115 1 | LN | 189.8 | 95.4 | 199 | 95.4 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336551 | 336552 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102127 | 18W | Approved | P2 | 35 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 206.4 | 112.3 | 199 | 103.7 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102128 | 18W | Approved | P2 | 35 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 222.1 | 128 | 199 | 111.6 |  |  |  |  | 9 | 8MCKNIGHT% - 8FRANKLIN% 500 1 + 8BOGALUS - 8FRANKL | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P2_3-8FRANKLIN%_500_J2416 |  | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102129 | 18W | Approved | P6 | 35 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | LN | 113.3 | 35 | 120 | 94.4 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336500 | 336785 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102130 | 18W | Approved | P6 | 35 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 166.9 | 78.9 | 161 | 103.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102131 | 18W | Approved | P6 | 35 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | LN | 184.8 | 98.7 | 199 | 92.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336790 | 336800 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
102132 | 18W | Approved | P6 | 35 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 251.5 | 94.8 | 239 | 105.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
102133 | 18W | Approved | P6 | 35 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 151.2 | 61.8 | 161 | 93.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
102134 | 18W | Approved | P6 | 35 | 336804 3VICKSBURG! 115 336805 3WATERWAYS 115 1 | LN | 295.4 | 69.9 | 239 | 123.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336804 | 336805 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102135 | 18W | Approved | P6 | 35 | 336805 3WATERWAYS 115 336806 3E.VICKSBRG+ 115 1 | LN | 284.7 | 59.9 | 260 | 109.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336805 | 336806 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102136 | 18W | Approved | P6 | 35 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 269.7 | 45.9 | 161 | 167.5 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102137 | 18W | Approved | P6 | 35 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 262.3 | 39 | 161 | 162.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102138 | 18W | Approved | P6 | 35 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 230.6 | 18.6 | 161 | 143.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102139 | 18W | Approved | P6 | 35 | 336961 3BOVINA 115 336976 3FLOWERS+ 115 1 | LN | 137.6 | 36.4 | 111 | 124 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336961 | 336976 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102140 | 18W | Approved | P6 | 35 | 360613 8MAGNOL CC1 500 990204 1.00 1 | TR | 334.4 | 335.4 | 360 | 92.9 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 360613 | 990204 | 1 |  | 500 | 1 | 347 | TVA | 347 | TVA | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102141 | 18W | Approved | P3 | 35 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1270.9 | 266.5 | 1069 | 118.9 |  |  |  |  | 13 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102142 | 18W | Approved | P3 | 35 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 633.4 | 449.9 | 672 | 94.3 |  |  |  |  | 14 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102143 | 18W | Approved | P3 | 35 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1245 | 790.9 | 1186 | 105 |  |  |  |  | 14 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102144 | 18W | Approved | P3 | 35 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 86.6 | 85.4 | 93 | 93.1 |  |  |  |  | 14 | 8FANCY_PT% 500/230 1 + 1RVR_BND_G1!21.5 Id:1 | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 8FANCY_PT% 500/230 1 | 1RVR_BND_G1!21.5 Id:1 |  | No violation: below Rate A
102145 | 18W | Approved | P3 | 35 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 186.9 | 77.9 | 206 | 90.7 |  |  |  |  | 15 | PORTER 230/138 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | PORTER 230/138 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
102146 | 18W | Approved | P3 | 35 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 208.3 | 133 | 206 | 101.1 |  |  |  |  | 16 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1! 18.0 Id | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1! 18.0 Id:1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
102147 | 18W | Approved | P3 | 35 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 228.4 | 133 | 206 | 110.9 |  |  |  |  | 17 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
102148 | 18W | Approved | P3 | 35 | 334073 4EGYPT 138 334074 4PANORAM 138 1 | LN | 202.8 | 107.9 | 206 | 98.5 |  |  |  |  | 17 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334073 | 334074 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! |  | No violation: below Rate A
102149 | 18W | Approved | P3 | 35 | 334074 4PANORAM 138 334075 4LONGMIR! 138 1 | LN | 196.8 | 102.1 | 206 | 95.5 |  |  |  |  | 17 | 4LEWIS% - 4CANEYCREEK! 138 1 + 1FRNTR 1!& 1FRNTR 2 | 334074 | 334075 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4LEWIS% - 4CANEYCREEK! 138 1 | 1FRNTR 1!& 1FRNTR 2! |  | No violation: below Rate A
102150 | 18W | Approved | P3 | 35 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 186.9 | 77.9 | 206 | 90.7 |  |  |  |  | 18 | 6PORTER% - 6CHPTSR2 230 1 + 1G1LEWIS! 22.0 Id:1 | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 6PORTER% - 6CHPTSR2230 1 | 1G1LEWIS! 22.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
102151 | 18W | Approved | P3 | 35 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 335.1 | 331.9 | 360 | 93.1 |  |  |  |  | 24 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 |  | No violation: below Rate A
102152 | 18W | Approved | P3 | 35 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 472.3 | 314.6 | 470 | 100.5 |  |  |  |  | 24 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 | Reduce PPG Plant
102153 | 18W | Approved | P3 | 35 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 261.4 | 150 | 288 | 90.8 |  |  |  |  | 25 | 4PNEC BK! - 4SABINE! 138 1 +1G4SABIN! 24.0 Id:1 | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | 4PNEC BK! - 4SABINE! 138 1 | 1G4SABIN! 24.0 Id:1 | Project Proposed | No violation: below Rate A | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
102154 | 18W | Approved | P1 | 35 | 334252 26L594TAP 69.0 334254 2QUALTY 69.0 1 | LN | 27.4 | 2.4 | 29.3 | 93.5 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334252 | 334254 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102155 | 18W | Approved | P1 | 35 | 334254 2QUALTY 69.0 334255 2BATSON! 69.0 NO | LN | 27.7 | 0 | 29.3 | 94.4 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334254 | 334255 | NO |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102156 | 18W | Approved | P1 | 35 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 37.5 | 11.6 | 29.3 | 127.9 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102157 | 18W | Approved | P1 | 35 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 37.9 | 11.7 | 29.3 | 129.4 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102158 | 18W | Approved | P1 | 35 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 38.2 | 11.9 | 29.3 | 130.5 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102159 | 18W | Approved | P1 | 35 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 38.7 | 11.8 | 29.3 | 132 |  |  |  |  | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
102160 | 18W | Approved | P1 | 35 | 334255 2BATSON! 69.0 334256 26L102TAP 69.0 1 | LN | 28.4 | 11.6 | 29.3 | 97.1 |  |  |  |  | 30 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334255 | 334256 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102161 | 18W | Approved | P1 | 35 | 334256 26L102TAP 69.0 334258 2TRANSCO 69.0 1 | LN | 29.1 | 11.7 | 29.3 | 99.2 |  |  |  |  | 30 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334256 | 334258 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed | No violation: below Rate A | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102162 | 18W | Approved | P1 | 35 | 334258 2TRANSCO 69.0 334259 2DOME 69.0 1 | LN | 29.4 | 11.9 | 29.3 | 100.5 |  |  |  |  | 30 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334258 | 334259 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102163 | 18W | Approved | P1 | 35 | 334259 2DOME 69.0 334260 2SOURLAK! 69.0 1 | LN | 30.1 | 11.8 | 29.3 | 102.6 |  |  |  |  | 30 | 2RAYWOOD! - 2DAISETA! 69.0 1 + Batson - Quality Mi | 334259 | 334260 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | 2RAYWOOD! - 2DAISETA! 69.0 1,Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-02-CP | 2019-06-01 | Construct Raywood-Daisetta 2nd 69 kV line (extend line 440 approximately 2.2 miles to Daisetta subst
102164 | 18W | Approved | P3 | 35 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.1 | 331.9 | 360 | 92.5 |  |  |  |  | 31 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4! | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4! |  | No violation: below Rate A
102165 | 18W | Approved | P3 | 35 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 336.7 | 331.9 | 360 | 93.5 |  |  |  |  | 32 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 |  | No violation: below Rate A
102166 | 18W | Approved | P3 | 35 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 756.3 | 187.4 | 560 | 135.1 |  |  |  |  | 32 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
102167 | 18L | Approved | P2 | 36 | 337619 3WOODWARD-S! 115 337647 3ARSENAL D 115 1 | LN | 335.1 | 124.4 | 239 | 140.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337619 | 337647 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102168 | 18L | Approved | P2 | 36 | 337620 3WOODWARD-N! 115 337644 3PINEBLUF IN 115 1 | LN | 303.4 | 91.9 | 239 | 126.9 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337620 | 337644 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102169 | 18L | Approved | P2 | 36 | 337644 3PINEBLUF IN 115 337645 3WHITE HALL 115 1 | LN | 331.8 | 121.2 | 266 | 124.8 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337644 | 337645 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102170 | 18L | Approved | P2 | 36 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | LN | 341.6 | 131.1 | 266 | 128.4 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337645 | 337646 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102171 | 18L | Approved | P2 | 36 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 351.7 | 140.7 | 266 | 132.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102172 | 18L | Approved | P2 | 36 | 337647 3ARSENAL D 115 337648 3WHT BLUFF! 115 1 | LN | 341.6 | 130.7 | 253 | 135 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337647 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102173 | 18L | Approved | P2 | 36 | 337648 3WHT BLUFF! 115 337649 3HENSLEY 115 1 | LN | 264.5 | 27.7 | 253 | 104.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337649 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102174 | 18L | Approved | P2 | 36 | 337648 3WHT BLUFF! 115 337650 8WHT BLUF-XF 500 1 | TR | 659.6 | 155.4 | 420 | 157.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337650 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102175 | 18L | Approved | P2 | 36 | 337648 3WHT BLUFF! 115 337650 8WHT BLUF-XF 500 2 | TR | 659.6 | 155.4 | 420 | 157.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337650 | 2 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102176 | 18L | Approved | P2 | 36 | 337648 3WHT BLUFF! 115 337859 3WRIGHTSVLE! 115 1 | LN | 333.8 | 7.6 | 253 | 131.9 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337648 | 337859 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102177 | 18L | Approved | P2 | 36 | 337649 3HENSLEY 115 337855 3ARCH ST 115 1 | LN | 261.1 | 24.5 | 253 | 103.2 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337649 | 337855 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102178 | 18L | Approved | P2 | 36 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | LN | 1294.2 | 304 | 840 | 154.1 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337650 | 337651 | 1 |  | 500 | 500 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed |  | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102179 | 18L | Approved | P2 | 36 | 337804 3MABLVALE-E! 115 338750 3SARDIS# 115 1 | LN | 239 | 2.2 | 253 | 94.5 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337804 | 338750 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102180 | 18L | Approved | P2 | 36 | 337855 3ARCH ST 115 338750 3SARDIS# 115 1 | LN | 249 | 12.2 | 253 | 98.4 |  |  |  |  | 1 | 8SHERIDAN% - 8WHT BLUFF% 500 1 +8WHT BLUFF% - 8KE | 337855 | 338750 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P2_3-White_Bluff_500_B7914 |  | Project Proposed | No violation: below Rate A | 11-EAI-017-CP | 2015-06-01 | Construct White Bluff 230 kV ring bus for Woodward line; Reconfigure White Bluff 500 kV
102181 | 18L | Approved | P6 | 36 | 336806 3E.VICKSBRG+ 115 336808 3EDWARDS 115 1 | LN | 178 | 21 | 161 | 110.6 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336806 | 336808 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102182 | 18L | Approved | P6 | 36 | 336808 3EDWARDS 115 336809 3BOLTON MS 115 1 | LN | 172.8 | 16.9 | 161 | 107.3 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336808 | 336809 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed |  | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102183 | 18L | Approved | P6 | 36 | 336809 3BOLTON MS 115 336880 3R.BRASWELL% 115 1 | LN | 150.1 | 20.7 | 161 | 93.2 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 336809 | 336880 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102184 | 18L | Approved | P6 | 36 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 102.7 | 101.5 | 112 | 91.7 |  |  |  |  | 10 | 8FRANKLIN% - 8GGNS% 500 1+8BXTRWILSON% - 8R.BRASWE | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | 8FRANKLIN% - 8GGNS% 500 1 | 8BXTRWILSON% - 8R.BRASWELL% 500 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102185 | 18L | Approved | P3 | 36 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 984.3 | 135.4 | 1069 | 92.1 |  |  |  |  | 13 | 8MCKNIGHT% - 8COLY% 500 1 +1RVR_BND_G1!21.5 Id:1 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8MCKNIGHT% - 8COLY% 500 1 | 1RVR_BND_G1!21.5 Id:1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102186 | 18L | Approved | P3 | 36 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 442.7 | 323.7 | 470 | 94.2 |  |  |  |  | 24 | 8CYPRESS% - 8HARTBRG% 500 1 +1G4SABIN! 24.0 Id:1 | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1G4SABIN! 24.0 Id:1 |  | No violation: below Rate A
102187 | 18L | Approved | P3 | 36 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 25 | 4PNEC BK! - 4SABINE! 138 1 +1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 4PNEC BK! - 4SABINE! 138 1 | 1G4SABIN! 24.0 Id:1 |  | Facility: GSU
102188 | 18L | Approved | P3 | 36 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 28 | 6MID CO% - 6P AC BK% 230 1 + 1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 6MID CO% - 6P AC BK% 230 1 | 1G4SABIN! 24.0 Id:1 |  | Facility: GSU
102189 | 18L | Approved | P3 | 36 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 333.1 | 360 | 92.2 |  |  |  |  | 29 | 6P AC BK% - 6KOLBS% 230 1 + 1G4SABIN! 24.0 Id:1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 6P AC BK%- 6KOLBS% 230 1 | 1G4SABIN! 24.0 Id:1 |  | Facility: GSU
102190 | 18L | Approved | P3 | 36 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 333.1 | 360 | 92.2 |  |  |  |  | 31 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4! | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4! |  | Facility: GSU
102191 | 18L | Approved | P3 | 36 | 335190 6NELSON% 230 335192 8NELSON% 500 1 | TR | 703.5 | 173.9 | 560 | 125.6 |  |  |  |  | 32 | 8CYPRESS% - 8HARTBRG% 500 1 +1NELSON_G4&6 | 335190 | 335192 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | 8CYPRESS% - 8HARTBRG% 500 1 | 1NELSON_G4&6 | Project Proposed |  | 14-EGL-005-CP | 2017-06-01 | Install Nelson 2nd 500-230 kV transformer (relocate Willow Glen units)
102192 | 15S | Approved | P0 | 37 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 332 | 360 | 92.2 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
102193 | 18S | Proposed | P1 | 59 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 195.5 | 62 | 188 | 104 |  |  |  |  | 2767 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230
102193 | 15S | Approved | P0 | 37 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.2 | 35.2 | 39 | 90.1 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
102194 | 18S | Proposed | P1 | 59 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 218.4 | 85 | 204 | 107 |  |  |  |  | 2767 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
102194 | 15S | Approved | P0 | 37 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 34.3 | 34.3 | 38 | 90.3 | [5 empty] | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
102195 | 18S | Proposed | P1 | 60 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 218.4 | 85 | 204 | 107 |  |  |  |  | 1885 | P1_2-1661 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1661 |  | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
102195 | 15S | Approved | P0 | 37 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 87.4 | 87.4 | 93 | 94 | [5 empty] | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
102196 | 18S | Proposed | P1 | 60 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 195.5 | 62 | 188 | 104 |  |  |  |  | 1885 | P1_2-1661 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661 |  | Project External |  | Messick 500/230
102197 | 18W | Approved | P1 | 53 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 238.4 | 79 | 233 | 102.3 |  |  |  |  | 2715 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230
102196 | 15S | Approved | P0 | 37 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.2 | 35.2 | 39 | 90.2 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
102197 | 15S | Approved | P0 | 37 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100.7 | 100.7 | 95 | 106 | [5 empty] | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case **
102198 | 18W | Approved | P1 | 54 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 238.4 | 79 | 233 | 102.3 |  |  |  |  | 1879 | P1_2-1664 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664 |  | Project External |  | Messick 500/230
102199 | 15S | Proposed | P1 | 55 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 228.3 | 88.7 | 204 | 111.9 |  |  |  |  | 2735 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230
102200 | 15S | Proposed | P1 | 55 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 205.3 | 65.6 | 188 | 109.2 |  |  |  |  | 2735 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230
102201 | 15S | Proposed | P1 | 56 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 228.3 | 88.7 | 204 | 111.9 |  |  |  |  | 1876 | P1_2-1656 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656 |  | Project External |  | Messick 500/230
102201 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.8 | 128.6 | 191 | 103.6 |  |  |  |  | 78 | P1_2-559_4MEAUX!,6MEAUX!+G_1ACADIA_S26! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559_4MEAUX!,6MEAUX! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102202 | 15S | Proposed | P1 | 56 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 205.3 | 65.6 | 188 | 109.2 |  |  |  |  | 1876 | P1_2-1656 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656 |  | Project External |  | Messick 500/230
102202 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.8 | 128.6 | 191 | 103.5 |  |  |  |  | 79 | P1_2-559_4MEAUX!,6MEAUX!+G_1ACADIA_C25! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559_4MEAUX!,6MEAUX! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102203 | 18L | Proposed | P1 | 57 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 225 | 79.8 | 204 | 110.3 |  |  |  |  | 2714 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project External |  | Messick 500/230
102203 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.8 | 128.6 | 191 | 103.5 |  |  |  |  | 80 | P1_2-559_4MEAUX!,6MEAUX!+G_1ACADIA_C24! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559_4MEAUX!,6MEAUX! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102204 | 18L | Proposed | P1 | 58 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 225 | 79.8 | 204 | 110.3 |  |  |  |  | 1814 | P1_2-1664 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1664 |  | Project External |  | Messick 500/230
102207 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.9 | 128.6 | 191 | 103.6 |  |  |  |  | 84 | P1_2-559_4MEAUX!,6MEAUX!+G_G3MADISN! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-559_4MEAUX!,6MEAUX! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102212 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.8 | 128.6 | 191 | 103.6 |  |  |  |  | 89 | P1_2-560_6MEAUX!,SELLRD6%+G_1ACADIA_S26! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-560_6MEAUX!,SELLRD6% | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102218 | 15S | Approved | P3 | 37 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 197.9 | 128.6 | 191 | 103.6 |  |  |  |  | 95 | P1_2-560_6MEAUX!,SELLRD6%+G_G3MADISN! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-560_6MEAUX!,SELLRD6% | G_G3MADISN! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102223 | 15S | Approved | P3 | 37 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 35.6 | 21 | 39 | 91.4 |  |  |  |  | 98 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_1RVR_BND_G1! ID 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-573_2MORIL!,2NEW_IBERIA! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
102224 | 15S | Approved | P3 | 37 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 35.8 | 21 | 39 | 91.8 |  |  |  |  | 99 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_1WAT U3! ID 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-573_2MORIL!,2NEW_IBERIA! | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
102225 | 15S | Approved | P3 | 37 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 36.5 | 21 | 39 | 93.5 |  |  |  |  | 100 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_G3TECHE! ID 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-573_2MORIL!,2NEW_IBERIA! | G_G3TECHE! ID 1 | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
102226 | 15S | Approved | P3 | 37 | 335411 2HOLIDAY 69.0 335412 2LAFAYETTE! 69.0 1 | LN | 35.7 | 21 | 39 | 91.6 |  |  |  |  | 101 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_LABBE2 ID 1 | 335411 | 335412 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-573_2MORIL!,2NEW_IBERIA! | G_LABBE2 ID 1 | Project Proposed | No violation: below Rate A | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
102238 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 87.7 | 53.1 | 80 | 109.7 |  |  |  |  | 119 | P1_2-1209_3SWARTZ!,3STERLING%+G_1ANO U2 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_1ANO U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102239 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 88.6 | 53.1 | 80 | 110.7 |  |  |  |  | 120 | P1_2-1209_3SWARTZ!,3STERLING%+G_G1DOLHIL! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_G1DOLHIL! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102240 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 87.9 | 53.1 | 80 | 109.9 |  |  |  |  | 121 | P1_2-1209_3SWARTZ!,3STERLING%+G_G1NESBIT! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_G1NESBIT! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102241 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 88.3 | 53.1 | 80 | 110.4 |  |  |  |  | 122 | P1_2-1209_3SWARTZ!,3STERLING%+G_G2RODEMR! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_G2RODEMR! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102242 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 88.9 | 53.1 | 80 | 111.2 |  |  |  |  | 123 | P1_2-1209_3SWARTZ!,3STERLING%+G_G3MADISN! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_G3MADISN! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102243 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 87.9 | 53.1 | 80 | 109.9 |  |  |  |  | 124 | P1_2-1209_3SWARTZ!,3STERLING%+G_PIRKEY 1 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_PIRKEY 1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102246 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 87.7 | 53.1 | 80 | 109.6 |  |  |  |  | 127 | P1_2-1209_3SWARTZ!,3STERLING%+G_TURKCOAL ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1209_3SWARTZ!,3STERLING% | G_TURKCOAL ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102261 | 15S | Approved | P3 | 37 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 98.4 | 53.1 | 80 | 123.1 |  |  |  |  | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102278 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.9 | 80.5 | 239 | 123.4 |  |  |  |  | 169 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CLSBAU3 ID 6 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CLSBAU3 ID 6 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102279 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 506.2 | 295.5 | 550 | 92 |  |  |  |  | 169 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CLSBAU3 ID 6 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CLSBAU3 ID 6 |  | No violation: below Rate A
102280 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 301.2 | 80.5 | 239 | 126 |  |  |  |  | 170 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1REMMEL UA ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1REMMEL UA ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102281 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 511.6 | 295.5 | 550 | 93 |  |  |  |  | 170 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1REMMEL UA ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1REMMEL UA ID 1 |  | No violation: below Rate A
102282 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 309.4 | 80.5 | 239 | 129.5 |  |  |  |  | 171 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1BLAKELY U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1BLAKELY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102283 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 528.4 | 295.5 | 550 | 96.1 |  |  |  |  | 171 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1BLAKELY U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1BLAKELY U1 ID 1 |  | No violation: below Rate A
102284 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 309.4 | 80.5 | 239 | 129.5 |  |  |  |  | 172 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1BLAKELY U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1BLAKELY U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102285 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 528.4 | 295.5 | 550 | 96.1 |  |  |  |  | 172 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1BLAKELY U2 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1BLAKELY U2 ID 1 |  | No violation: below Rate A
102286 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 301.9 | 80.5 | 239 | 126.3 |  |  |  |  | 173 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CARPENTR U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CARPENTR U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102287 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 522.3 | 295.5 | 550 | 95 |  |  |  |  | 173 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CARPENTR U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CARPENTR U1 ID 1 |  | No violation: below Rate A
102288 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 302.2 | 80.5 | 239 | 126.4 |  |  |  |  | 174 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CARPENTR U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CARPENTR U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102289 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 523 | 295.5 | 550 | 95.1 |  |  |  |  | 174 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CARPENTR U2 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CARPENTR U2 ID 1 |  | No violation: below Rate A
102290 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 300.3 | 80.5 | 239 | 125.7 |  |  |  |  | 175 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ANO U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ANO U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102291 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 502.6 | 295.5 | 550 | 91.4 |  |  |  |  | 175 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ANO U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ANO U1 ID 1 |  | No violation: below Rate A
102292 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 301.7 | 80.5 | 239 | 126.2 |  |  |  |  | 176 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ANO U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ANO U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102293 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 502.2 | 295.5 | 550 | 91.3 |  |  |  |  | 176 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ANO U2 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ANO U2 ID 1 |  | No violation: below Rate A
102294 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 296.3 | 80.5 | 239 | 124 |  |  |  |  | 177 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ISES U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ISES U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102295 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 502.3 | 295.5 | 550 | 91.3 |  |  |  |  | 177 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ISES U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ISES U1 ID 1 |  | No violation: below Rate A
102296 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 295.2 | 80.5 | 239 | 123.5 |  |  |  |  | 178 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ISES U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ISES U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102297 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 499.9 | 295.5 | 550 | 90.9 |  |  |  |  | 178 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1ISES U2 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1ISES U2 ID 1 |  | No violation: below Rate A
102298 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.9 | 80.5 | 239 | 123.4 |  |  |  |  | 179 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1PLUM PT U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1PLUM PT U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102299 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 503.2 | 295.5 | 550 | 91.5 |  |  |  |  | 179 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1PLUM PT U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1PLUM PT U1 ID 1 |  | No violation: below Rate A
102300 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.8 | 80.5 | 239 | 123.3 |  |  |  |  | 180 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1M.HYD U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1M.HYD U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102301 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 505.4 | 295.5 | 550 | 91.9 |  |  |  |  | 180 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1M.HYD U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1M.HYD U1 ID 1 |  | No violation: below Rate A
102302 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.8 | 80.5 | 239 | 123.4 |  |  |  |  | 181 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1L&D2 U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1L&D2 U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102303 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 506.5 | 295.5 | 550 | 92.1 |  |  |  |  | 181 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1L&D2 U1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1L&D2 U1 ID 1 |  | No violation: below Rate A
102304 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.8 | 80.5 | 239 | 123.4 |  |  |  |  | 182 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1L&D2 U3 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1L&D2 U3 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102305 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 506.5 | 295.5 | 550 | 92.1 |  |  |  |  | 182 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1L&D2 U3 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1L&D2 U3 ID 1 |  | No violation: below Rate A
102306 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 295.6 | 80.5 | 239 | 123.7 |  |  |  |  | 183 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CAL G1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CAL G1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102307 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 508.3 | 295.5 | 550 | 92.4 |  |  |  |  | 183 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_1CAL G1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_1CAL G1 ID 1 |  | No violation: below Rate A
102316 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 295.4 | 80.5 | 239 | 123.6 |  |  |  |  | 188 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_FLINTCR1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_FLINTCR1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102317 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 509.8 | 295.5 | 550 | 92.7 |  |  |  |  | 188 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_FLINTCR1 ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_FLINTCR1 ID 1 |  | No violation: below Rate A
102318 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 294.9 | 80.5 | 239 | 123.4 |  |  |  |  | 189 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_MUSKOG4G ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_MUSKOG4G ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102319 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337753 8HS EHV% 500 1 | TR | 510.2 | 295.5 | 550 | 92.8 |  |  |  |  | 189 | P1_2-1340_3HS EHV-E!,8HS EHV%+G_MUSKOG4G ID 1 | 337685 | 337753 | 1 |  | 500 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1340_3HS EHV-E!,8HS EHV% | G_MUSKOG4G ID 1 |  | No violation: below Rate A
102326 | 15S | Approved | P3 | 37 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 100 | 57.2 | 106 | 94.3 |  |  |  |  | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
102327 | 15S | Approved | P3 | 37 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 99.8 | 57.2 | 106 | 94.1 |  |  |  |  | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
102328 | 15S | Approved | P3 | 37 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 99.8 | 57.2 | 106 | 94.1 |  |  |  |  | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
102329 | 15S | Approved | P3 | 37 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 99.8 | 57.2 | 106 | 94.1 |  |  |  |  | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
102330 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 245.9 | 117.6 | 226 | 108.8 |  |  |  |  | 199 | P1_2-1558_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1NM G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102331 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 252 | 117.6 | 226 | 111.5 |  |  |  |  | 200 | P1_2-1558_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1PLUM PT U1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102332 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 241.4 | 117.6 | 226 | 106.8 |  |  |  |  | 201 | P1_2-1558_8FREEPORTTN%+G_1CAL G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CAL G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102333 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 248.4 | 117.6 | 226 | 109.9 |  |  |  |  | 202 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F1HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102334 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 248.4 | 117.6 | 226 | 109.9 |  |  |  |  | 203 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F1HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102335 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 248.4 | 117.6 | 226 | 109.9 |  |  |  |  | 204 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F2HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102336 | 15S | Approved | P3 | 37 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 248.3 | 117.6 | 226 | 109.9 |  |  |  |  | 205 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F2HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
102337 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352 | 253.1 | 335 | 105.1 |  |  |  |  | 295 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102338 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352 | 253.1 | 335 | 105.1 |  |  |  |  | 296 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102339 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.6 | 253.1 | 335 | 107.1 |  |  |  |  | 297 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102340 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.2 | 253.1 | 335 | 107.5 |  |  |  |  | 298 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility
102341 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360 | 253.1 | 335 | 107.5 |  |  |  |  | 299 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility
102342 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.1 | 253.1 | 335 | 105.1 |  |  |  |  | 300 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102343 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352 | 253.1 | 335 | 105.1 |  |  |  |  | 301 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102344 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352 | 253.1 | 335 | 105.1 |  |  |  |  | 302 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102345 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351 | 253.1 | 335 | 104.8 |  |  |  |  | 303 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1DOW_AEP_1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1DOW_AEP_1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102346 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.2 | 253.1 | 335 | 104.5 |  |  |  |  | 304 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102347 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351 | 253.1 | 335 | 104.8 |  |  |  |  | 305 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102348 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.2 | 253.1 | 335 | 104.8 |  |  |  |  | 306 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102349 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.9 | 253.1 | 335 | 104.8 |  |  |  |  | 307 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102350 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.9 | 253.1 | 335 | 104.8 |  |  |  |  | 308 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102351 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.2 | 253.1 | 335 | 104.5 |  |  |  |  | 309 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102352 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.9 | 253.1 | 335 | 105.6 |  |  |  |  | 310 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102353 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354 | 253.1 | 335 | 105.7 |  |  |  |  | 311 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102354 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.4 | 253.1 | 335 | 104.6 |  |  |  |  | 312 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102355 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 253.1 | 335 | 104.7 |  |  |  |  | 313 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102356 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.7 | 253.1 | 335 | 104.4 |  |  |  |  | 314 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102357 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 381.5 | 253.1 | 335 | 113.9 |  |  |  |  | 315 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
102358 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.6 | 253.1 | 335 | 105 |  |  |  |  | 316 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102359 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.6 | 253.1 | 335 | 105 |  |  |  |  | 317 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102360 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 384.7 | 253.1 | 335 | 114.8 |  |  |  |  | 318 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility
102361 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.5 |  |  |  |  | 319 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102362 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.5 |  |  |  |  | 320 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102363 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.5 |  |  |  |  | 321 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102364 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 357.7 | 253.1 | 335 | 106.8 |  |  |  |  | 322 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1SOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102365 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 253.1 | 335 | 104.7 |  |  |  |  | 323 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102366 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 253.1 | 335 | 104.7 |  |  |  |  | 324 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102367 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.9 | 253.1 | 335 | 108.6 |  |  |  |  | 325 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U3! ID 1 |  | No violation: CLECO facility
102368 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 355.7 | 253.1 | 335 | 106.2 |  |  |  |  | 326 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102369 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 253.1 | 335 | 107.5 |  |  |  |  | 327 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U2! ID 1 |  | No violation: CLECO facility
102370 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.6 |  |  |  |  | 328 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102371 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.6 |  |  |  |  | 329 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102372 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.5 | 253.1 | 335 | 105.8 |  |  |  |  | 330 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102373 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.7 | 253.1 | 335 | 110.1 |  |  |  |  | 331 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
102374 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.3 | 253.1 | 335 | 110.2 |  |  |  |  | 332 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
102375 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.4 | 253.1 | 335 | 104.9 |  |  |  |  | 333 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102376 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.8 | 253.1 | 335 | 105.9 |  |  |  |  | 334 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1MICH U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102377 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.2 | 253.1 | 335 | 108.4 |  |  |  |  | 335 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1MICH U3! ID 1 |  | No violation: CLECO facility
102378 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.9 | 253.1 | 335 | 105.1 |  |  |  |  | 336 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102379 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.3 | 253.1 | 335 | 108.8 |  |  |  |  | 337 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GGNS U1 ID 1 |  | No violation: CLECO facility
102380 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.6 | 253.1 | 335 | 105.6 |  |  |  |  | 338 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102381 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.5 | 253.1 | 335 | 104.3 |  |  |  |  | 339 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1HINDS G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102382 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.5 | 253.1 | 335 | 104.6 |  |  |  |  | 340 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1REX BRWN U4 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1REX BRWN U4 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102383 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.8 | 253.1 | 335 | 104.4 |  |  |  |  | 341 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102384 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.8 | 253.1 | 335 | 104.4 |  |  |  |  | 342 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102385 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.8 | 253.1 | 335 | 104.4 |  |  |  |  | 343 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102386 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.5 | 253.1 | 335 | 104.9 |  |  |  |  | 344 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102387 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 366.6 | 253.1 | 335 | 109.4 |  |  |  |  | 345 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G3TECHE! ID 1 |  | No violation: CLECO facility
102388 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.3 | 253.1 | 335 | 104.6 |  |  |  |  | 346 | P1_2-1637_COCODR 6%,VILPLT 6!+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102389 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 355.2 | 253.1 | 335 | 106 |  |  |  |  | 347 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1 ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102390 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.2 | 253.1 | 335 | 105.4 |  |  |  |  | 348 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102391 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.2 | 253.1 | 335 | 105.4 |  |  |  |  | 349 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102392 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.8 | 253.1 | 335 | 104.4 |  |  |  |  | 350 | P1_2-1637_COCODR 6%,VILPLT 6!+G_LABBE1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_LABBE1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102393 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.4 | 253.1 | 335 | 104.6 |  |  |  |  | 351 | P1_2-1637_COCODR 6%,VILPLT 6!+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102394 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.5 | 253.1 | 335 | 104.9 |  |  |  |  | 352 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HARGIS1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102395 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.5 | 253.1 | 335 | 104.9 |  |  |  |  | 353 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HARGIS2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102396 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.6 | 253.1 | 335 | 104.4 |  |  |  |  | 354 | P1_2-1637_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102397 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.4 | 253.1 | 335 | 104.6 |  |  |  |  | 355 | P1_2-1637_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102398 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.6 | 253.1 | 335 | 104.4 |  |  |  |  | 356 | P1_2-1637_COCODR 6%,VILPLT 6!+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102399 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.3 | 253.1 | 335 | 104.9 |  |  |  |  | 357 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HOUMA 3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102400 | 15S | Approved | P3 | 37 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 206.9 | 21.6 | 225 | 92 |  |  |  |  | 362 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
102401 | 15S | Approved | P3 | 37 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 204.5 | 21.6 | 225 | 90.9 |  |  |  |  | 363 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 |  | No violation: below Rate A
102418 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 115.2 | 39.5 | 125 | 92.1 |  |  |  |  | 372 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102419 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 653 | 65.8 | 700 | 93.3 |  |  |  |  | 372 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102420 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 250.2 | 98.8 | 204 | 122.6 |  |  |  |  | 372 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230
102421 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 232.2 | 75.5 | 188 | 123.5 |  |  |  |  | 372 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230
102422 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 114.5 | 39.5 | 125 | 91.6 |  |  |  |  | 373 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102423 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 653 | 65.8 | 700 | 93.3 |  |  |  |  | 373 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102424 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 251 | 98.8 | 204 | 123 |  |  |  |  | 373 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230
102425 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 233.1 | 75.5 | 188 | 124 |  |  |  |  | 373 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230
102430 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 114.8 | 39.5 | 125 | 91.9 |  |  |  |  | 375 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102431 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 653.1 | 65.8 | 700 | 93.3 |  |  |  |  | 375 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102432 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 251.1 | 98.8 | 204 | 123.1 |  |  |  |  | 375 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230
102433 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 233.1 | 75.5 | 188 | 124 |  |  |  |  | 375 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230
102434 | 15S | Approved | P3 | 37 | 500140 CARROLL6 230 500150 CARROLL4 138 1 | TR | 375.2 | 156.1 | 400 | 93.8 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500140 | 500150 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102435 | 15S | Approved | P3 | 37 | 500150 CARROLL4 138 500762 REDRVRTAP4 138 1 | LN | 243 | 98.1 | 264 | 92.1 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500150 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102436 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 655.9 | 65.8 | 700 | 93.7 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102437 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 280.1 | 98.8 | 204 | 137.3 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
102438 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 265.3 | 75.5 | 188 | 141.1 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
102439 | 15S | Approved | P3 | 37 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 253.7 | 109.8 | 264 | 96.1 |  |  |  |  | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102440 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 112.6 | 39.5 | 125 | 90.1 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102441 | 15S | Approved | P3 | 37 | 500140 CARROLL6 230 500150 CARROLL4 138 1 | TR | 369.9 | 156.1 | 400 | 92.5 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500140 | 500150 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102442 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 655.1 | 65.8 | 700 | 93.6 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102443 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 271.5 | 98.8 | 204 | 133.1 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
102444 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 255.4 | 75.5 | 188 | 135.8 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
102445 | 15S | Approved | P3 | 37 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 247 | 109.8 | 264 | 93.6 |  |  |  |  | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102446 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 112.6 | 39.5 | 125 | 90.1 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102447 | 15S | Approved | P3 | 37 | 500140 CARROLL6 230 500150 CARROLL4 138 1 | TR | 369.9 | 156.1 | 400 | 92.5 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500140 | 500150 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102448 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 655.1 | 65.8 | 700 | 93.6 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102449 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 271.5 | 98.8 | 204 | 133.1 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
102450 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 255.4 | 75.5 | 188 | 135.8 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
102451 | 15S | Approved | P3 | 37 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 247 | 109.8 | 264 | 93.6 |  |  |  |  | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102452 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 113.2 | 39.5 | 125 | 90.6 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
102453 | 15S | Approved | P3 | 37 | 500140 CARROLL6 230 500150 CARROLL4 138 1 | TR | 370.8 | 156.1 | 400 | 92.7 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500140 | 500150 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
102454 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 655.2 | 65.8 | 700 | 93.6 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
102455 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 272 | 98.8 | 204 | 133.3 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
102456 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 255.9 | 75.5 | 188 | 136.1 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
102457 | 15S | Approved | P3 | 37 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 247.3 | 109.8 | 264 | 93.7 |  |  |  |  | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
102458 | 15S | Approved | P3 | 37 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 114.8 | 39.5 | 125 | 91.8 |  |  |  |  | 380 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
102459 | 15S | Approved | P3 | 37 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 653.1 | 65.8 | 700 | 93.3 |  |  |  |  | 380 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
102460 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 252 | 98.8 | 204 | 123.5 |  |  |  |  | 380 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230
102461 | 15S | Approved | P3 | 37 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 234.1 | 75.5 | 188 | 124.5 |  |  |  |  | 380 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230
102466 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341 | 253.1 | 335 | 101.8 |  |  |  |  | 382 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102467 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341 | 253.1 | 335 | 101.8 |  |  |  |  | 383 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102468 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.6 | 253.1 | 335 | 103.8 |  |  |  |  | 384 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102469 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.1 | 253.1 | 335 | 104.2 |  |  |  |  | 385 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102470 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349 | 253.1 | 335 | 104.2 |  |  |  |  | 386 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102471 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341.2 | 253.1 | 335 | 101.9 |  |  |  |  | 387 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102472 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341.1 | 253.1 | 335 | 101.8 |  |  |  |  | 388 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102473 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341.1 | 253.1 | 335 | 101.8 |  |  |  |  | 389 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102474 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.1 | 253.1 | 335 | 101.5 |  |  |  |  | 390 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1DOW_AEP_1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1DOW_AEP_1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102475 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.2 | 253.1 | 335 | 101.3 |  |  |  |  | 391 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102476 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340 | 253.1 | 335 | 101.5 |  |  |  |  | 392 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102477 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.3 | 253.1 | 335 | 101.6 |  |  |  |  | 393 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102478 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.9 | 253.1 | 335 | 101.5 |  |  |  |  | 394 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102479 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.9 | 253.1 | 335 | 101.5 |  |  |  |  | 395 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102480 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.2 | 253.1 | 335 | 101.3 |  |  |  |  | 396 | P1_2-1721_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102481 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.9 | 253.1 | 335 | 102.4 |  |  |  |  | 397 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102482 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343 | 253.1 | 335 | 102.4 |  |  |  |  | 398 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102483 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.4 | 253.1 | 335 | 101.3 |  |  |  |  | 399 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102484 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.9 | 253.1 | 335 | 101.5 |  |  |  |  | 400 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102485 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.7 | 253.1 | 335 | 101.1 |  |  |  |  | 401 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102486 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.5 | 253.1 | 335 | 110.6 |  |  |  |  | 402 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
102487 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.7 | 253.1 | 335 | 101.7 |  |  |  |  | 403 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1WAT U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102488 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.7 | 253.1 | 335 | 101.7 |  |  |  |  | 404 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1WAT U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102489 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.7 | 253.1 | 335 | 111.5 |  |  |  |  | 405 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility
102490 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.6 | 253.1 | 335 | 102.3 |  |  |  |  | 406 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102491 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.6 | 253.1 | 335 | 102.3 |  |  |  |  | 407 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GOXY U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102492 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.6 | 253.1 | 335 | 102.3 |  |  |  |  | 408 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GOXY U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102493 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.7 | 253.1 | 335 | 103.5 |  |  |  |  | 409 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1SOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102494 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.9 | 253.1 | 335 | 101.5 |  |  |  |  | 410 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102495 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.9 | 253.1 | 335 | 101.5 |  |  |  |  | 411 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102496 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.9 | 253.1 | 335 | 105.3 |  |  |  |  | 412 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102497 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.7 | 253.1 | 335 | 102.9 |  |  |  |  | 413 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102498 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.2 | 253.1 | 335 | 104.2 |  |  |  |  | 414 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102499 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.6 | 253.1 | 335 | 102.3 |  |  |  |  | 415 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102500 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.6 | 253.1 | 335 | 102.3 |  |  |  |  | 416 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102501 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343.5 | 253.1 | 335 | 102.5 |  |  |  |  | 417 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102502 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 357.7 | 253.1 | 335 | 106.8 |  |  |  |  | 418 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL U4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102503 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.3 | 253.1 | 335 | 106.9 |  |  |  |  | 419 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL U5! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102504 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.5 | 253.1 | 335 | 101.6 |  |  |  |  | 420 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102505 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343.8 | 253.1 | 335 | 102.6 |  |  |  |  | 421 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1MICH U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102506 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.2 | 253.1 | 335 | 105.1 |  |  |  |  | 422 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1MICH U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102507 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341 | 253.1 | 335 | 101.8 |  |  |  |  | 423 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102508 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.1 | 253.1 | 335 | 105.4 |  |  |  |  | 424 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GGNS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102509 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.7 | 253.1 | 335 | 102.3 |  |  |  |  | 425 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102510 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.6 | 253.1 | 335 | 101.4 |  |  |  |  | 426 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1REX BRWN U4 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1REX BRWN U4 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102511 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.8 | 253.1 | 335 | 101.1 |  |  |  |  | 427 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102512 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.8 | 253.1 | 335 | 101.1 |  |  |  |  | 428 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102513 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.8 | 253.1 | 335 | 101.1 |  |  |  |  | 429 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102514 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.6 | 253.1 | 335 | 101.7 |  |  |  |  | 430 | P1_2-1721_VILPLT 6!,WELLS 6%+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102515 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 355.6 | 253.1 | 335 | 106.2 |  |  |  |  | 431 | P1_2-1721_VILPLT 6!,WELLS 6%+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G3TECHE! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102516 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.4 | 253.1 | 335 | 101.3 |  |  |  |  | 432 | P1_2-1721_VILPLT 6!,WELLS 6%+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102517 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.2 | 253.1 | 335 | 102.7 |  |  |  |  | 433 | P1_2-1721_VILPLT 6!,WELLS 6%+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1 ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102518 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.2 | 253.1 | 335 | 102.2 |  |  |  |  | 434 | P1_2-1721_VILPLT 6!,WELLS 6%+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102519 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.2 | 253.1 | 335 | 102.1 |  |  |  |  | 435 | P1_2-1721_VILPLT 6!,WELLS 6%+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102520 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.8 | 253.1 | 335 | 101.1 |  |  |  |  | 436 | P1_2-1721_VILPLT 6!,WELLS 6%+G_LABBE1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_LABBE1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102521 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.5 | 253.1 | 335 | 101.3 |  |  |  |  | 437 | P1_2-1721_VILPLT 6!,WELLS 6%+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102522 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.5 | 253.1 | 335 | 101.6 |  |  |  |  | 438 | P1_2-1721_VILPLT 6!,WELLS 6%+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_HARGIS1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102523 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.5 | 253.1 | 335 | 101.6 |  |  |  |  | 439 | P1_2-1721_VILPLT 6!,WELLS 6%+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_HARGIS2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102524 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.7 | 253.1 | 335 | 101.1 |  |  |  |  | 440 | P1_2-1721_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102525 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.5 | 253.1 | 335 | 101.3 |  |  |  |  | 441 | P1_2-1721_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102526 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.7 | 253.1 | 335 | 101.1 |  |  |  |  | 442 | P1_2-1721_VILPLT 6!,WELLS 6%+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102527 | 15S | Approved | P3 | 37 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 340.4 | 253.1 | 335 | 101.6 |  |  |  |  | 443 | P1_2-1721_VILPLT 6!,WELLS 6%+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_HOUMA 3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
102528 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 150.5 | 91 | 150 | 100.3 |  |  |  |  | 444 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102529 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 154 | 93.1 | 150 | 102.7 |  |  |  |  | 444 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102530 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 175.9 | 91 | 150 | 117.3 |  |  |  |  | 445 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
102531 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 180 | 93.1 | 150 | 120 |  |  |  |  | 445 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
102532 | 15S | Approved | P3 | 37 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.4 | 49.6 | 115 | 102.1 |  |  |  |  | 445 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
102533 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 175.9 | 91 | 150 | 117.3 |  |  |  |  | 446 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
102534 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 180 | 93.1 | 150 | 120 |  |  |  |  | 446 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
102535 | 15S | Approved | P3 | 37 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.4 | 49.6 | 115 | 102.1 |  |  |  |  | 446 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
102536 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 136 | 93.1 | 150 | 90.7 |  |  |  |  | 447 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+69 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102537 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 136.1 | 93.1 | 150 | 90.7 |  |  |  |  | 448 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102538 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 158.2 | 91 | 150 | 105.5 |  |  |  |  | 449 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102539 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 161.9 | 93.1 | 150 | 108 |  |  |  |  | 449 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102540 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 158.2 | 91 | 150 | 105.5 |  |  |  |  | 450 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102541 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 161.9 | 93.1 | 150 | 108 |  |  |  |  | 450 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102542 | 15S | Approved | P3 | 37 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 264.7 | 96.2 | 243 | 108.9 |  |  |  |  | 452 | G_1G1LEWIS! ID 1+P1_2-170_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-170_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
102543 | 15S | Approved | P3 | 37 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.6 | 13.8 | 39 | 96.5 |  |  |  |  | 453 | G_1G1LEWIS! ID 1+P1_2-218_4MEMORIL!,4MID CO% | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
102544 | 15S | Approved | P3 | 37 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.1 | 16.2 | 39 | 102.8 |  |  |  |  | 453 | G_1G1LEWIS! ID 1+P1_2-218_4MEMORIL!,4MID CO% | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
102545 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 485.6 | 330.3 | 470 | 103.3 |  |  |  |  | 454 | G_1G1LEWIS! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G1LEWIS! ID 1 | Reduce PPG Plant
102546 | 15S | Approved | P3 | 37 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 263.9 | 96.2 | 243 | 108.6 |  |  |  |  | 456 | G_1G2LEWIS! ID 1+P1_2-170_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-170_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
102547 | 15S | Approved | P3 | 37 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.6 | 13.8 | 39 | 96.4 |  |  |  |  | 457 | G_1G2LEWIS! ID 1+P1_2-218_4MEMORIL!,4MID CO% | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
102548 | 15S | Approved | P3 | 37 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40 | 16.2 | 39 | 102.7 |  |  |  |  | 457 | G_1G2LEWIS! ID 1+P1_2-218_4MEMORIL!,4MID CO% | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-218_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
102549 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 485.2 | 330.3 | 470 | 103.2 |  |  |  |  | 458 | G_1G2LEWIS! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G2LEWIS! ID 1 | Reduce PPG Plant
102550 | 15S | Approved | P3 | 37 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 248.8 | 85.6 | 220 | 113.1 |  |  |  |  | 462 | G_1EXXONGT1! ID 1+P1_2-285_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-285_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
102551 | 15S | Approved | P3 | 37 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 254 | 101 | 220 | 115.4 |  |  |  |  | 463 | G_1EXXONGT1! ID 1+P1_2-286_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-286_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
102552 | 15S | Approved | P3 | 37 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 254.8 | 147.1 | 282 | 90.4 |  |  |  |  | 465 | G_1EXXONGT1! ID 1+P1_2-288_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-288_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
102553 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 491.9 | 330.3 | 470 | 104.7 |  |  |  |  | 468 | G_1G1SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G1SABIN! ID 1 | Reduce PPG Plant
102554 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 491.9 | 330.3 | 470 | 104.7 |  |  |  |  | 469 | G_1G2SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G2SABIN! ID 1 | Reduce PPG Plant
102555 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 520.3 | 330.3 | 470 | 110.7 |  |  |  |  | 471 | G_1G3SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G3SABIN! ID 1 | Reduce PPG Plant
102556 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 495.6 | 330.3 | 470 | 105.5 |  |  |  |  | 472 | G_1G4SABIN! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
102558 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 498.1 | 330.3 | 470 | 106 |  |  |  |  | 473 | G_1G4SABIN! ID 1+P1_2-253_8CYPRESS%,8HARTBRG% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-253_8CYPRESS%,8HARTBRG% | G_1G4SABIN! ID 1 | Reduce PPG Plant
102559 | 15S | Approved | P3 | 37 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 288.9 | 163.9 | 288 | 100.3 |  |  |  |  | 474 | G_1G4SABIN! ID 1+P1_2-298_4PNEC BK!,4SABINE! | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-298_4PNEC BK!,4SABINE! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
102560 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 568 | 330.3 | 470 | 120.8 |  |  |  |  | 475 | G_1G4SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
102561 | 15S | Approved | P3 | 37 | 335135 6VERDINE% 230 335136 6PPG! 230 1 | LN | 446.2 | 224.5 | 470 | 94.9 |  |  |  |  | 475 | G_1G4SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335135 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 |  | No violation: below Rate A
102562 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 478.1 | 330.3 | 470 | 101.7 |  |  |  |  | 476 | G_1G5SABIN! ID 1+P1_2-253_8CYPRESS%,8HARTBRG% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-253_8CYPRESS%,8HARTBRG% | G_1G5SABIN! ID 1 | Reduce PPG Plant
102563 | 15S | Approved | P3 | 37 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 541.3 | 330.3 | 470 | 115.2 |  |  |  |  | 477 | G_1G5SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G5SABIN! ID 1 | Reduce PPG Plant
102564 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 675.5 | 477 | 672 | 100.5 |  |  |  |  | 478 | G_1CARVLE_C2! ID 1+P1_2-775_6IBERVIL%,6BYULABUTTE! | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102565 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 675.5 | 477 | 672 | 100.5 |  |  |  |  | 479 | G_1CARVLE_C2! ID 1+1017 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102566 | 15S | Approved | P3 | 37 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1186.2 | 300.5 | 1069 | 111 |  |  |  |  | 481 | G_1RVR_BND_G1! ID 1+P1_2-585_8WEBRE%,8BYULABUTTE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-585_8WEBRE%,8BYULABUTTE% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102567 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 673.6 | 477 | 672 | 100.2 |  |  |  |  | 482 | G_1RVR_BND_G1! ID 1+P1_2-746_6COLY%,8COLY% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-746_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102568 | 15S | Approved | P3 | 37 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1248 | 300.5 | 1069 | 116.7 |  |  |  |  | 482 | G_1RVR_BND_G1! ID 1+P1_2-746_6COLY%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-746_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102569 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 665.7 | 477 | 672 | 99.1 |  |  |  |  | 483 | G_1RVR_BND_G1! ID 1+P1_2-769_6FANCY_PT%,8FANCY_PT% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-769_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102570 | 15S | Approved | P3 | 37 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1283.4 | 815.4 | 1186 | 108.2 |  |  |  |  | 483 | G_1RVR_BND_G1! ID 1+P1_2-769_6FANCY_PT%,8FANCY_PT% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-769_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102571 | 15S | Approved | P3 | 37 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1301.3 | 300.5 | 1069 | 121.7 |  |  |  |  | 484 | G_1RVR_BND_G1! ID 1+P1_2-771_8MCKNIGHT%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-771_8MCKNIGHT%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102572 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 687 | 477 | 672 | 102.2 |  |  |  |  | 485 | G_1RVR_BND_G1! ID 1+1007 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102573 | 15S | Approved | P3 | 37 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1025.9 | 300.5 | 1069 | 96 |  |  |  |  | 485 | G_1RVR_BND_G1! ID 1+1007 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102574 | 15S | Approved | P3 | 37 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 687 | 477 | 672 | 102.2 |  |  |  |  | 486 | G_1RVR_BND_G1! ID 1+1017 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
102575 | 15S | Approved | P3 | 37 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1025.9 | 300.5 | 1069 | 96 |  |  |  |  | 486 | G_1RVR_BND_G1! ID 1+1017 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
102576 | 15S | Approved | P3 | 37 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 183.6 | 120.5 | 199 | 92.3 |  |  |  |  | 487 | G_1WAT U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102577 | 15S | Approved | P3 | 37 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 206.4 | 141.5 | 199 | 103.7 |  |  |  |  | 487 | G_1WAT U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102578 | 15S | Approved | P3 | 37 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 179.7 | 120.5 | 199 | 90.3 |  |  |  |  | 489 | G_1NMIL U4! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102579 | 15S | Approved | P3 | 37 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 202.3 | 141.5 | 199 | 101.6 |  |  |  |  | 489 | G_1NMIL U4! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102580 | 15S | Approved | P3 | 37 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 180 | 120.5 | 199 | 90.5 |  |  |  |  | 490 | G_1NMIL U5! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102581 | 15S | Approved | P3 | 37 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 202.6 | 141.5 | 199 | 101.8 |  |  |  |  | 490 | G_1NMIL U5! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102582 | 15S | Approved | P3 | 37 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 200.6 | 141.5 | 199 | 100.8 |  |  |  |  | 491 | G_1MICH U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1MICH U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
102583 | 15S | Approved | P3 | 37 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 232.3 | 135.2 | 229 | 101.5 |  |  |  |  | 492 | G_1MICH U3! ID 1+P1_2-946_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-946_39MILE%,3WSTWGO! | G_1MICH U3! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
102584 | 15S | Approved | P3 | 37 | 336800 3BXTRWILSON% 115 336804 3VICKSBURG! 115 1 | LN | 243.4 | 129.5 | 239 | 101.9 |  |  |  |  | 493 | G_1ANDRUS U1 ID 1+1251 | 336800 | 336804 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1019_3BXTRWILSON%,3VICKSBURG! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 13-EMI-001-CP | 2013-06-01 | Upgrade Vicksburg 115 kV CTs on B.Wilson ckt 1 (ckt without Spencer Potash on it)
102585 | 15S | Approved | P3 | 37 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 171.4 | 85.6 | 161 | 106.4 |  |  |  |  | 494 | G_1ANDRUS U1 ID 1+1258 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1026_3VICKSBURG!,3N.VICKSBRG! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
102586 | 15S | Approved | P3 | 37 | 336960 3SE.VICKSBRG 115 336961 3BOVINA 115 1 | LN | 159.6 | 75.9 | 176 | 90.7 |  |  |  |  | 494 | G_1ANDRUS U1 ID 1+1258 | 336960 | 336961 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1026_3VICKSBURG!,3N.VICKSBRG! | G_1ANDRUS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-005-CP | 2018-06-01 | Construct Johnson Rd 115 kV Sw Station; Rebuild E.Vicksburg-Johnson-R.Braswell 115 kV; Rebuild SE Vi
102587 | 15S | Approved | P3 | 37 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 625.1 | 282.1 | 561 | 111.4 |  |  |  |  | 495 | G_1ANDRUS U1 ID 1+P1_2-1092_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1092_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
102588 | 15S | Approved | P3 | 37 | 337645 3WHITE HALL 115 337646 3ARSENAL C 115 1 | LN | 254.8 | 169.3 | 266 | 95.8 |  |  |  |  | 496 | G_1ANDRUS U1 ID 1+1518 | 337645 | 337646 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1286_3WOODWARD-S!,3WHT BLUFF! | G_1ANDRUS U1 ID 1 |  | No violation: below Rate A
102589 | 15S | Approved | P3 | 37 | 337646 3ARSENAL C 115 337648 3WHT BLUFF! 115 1 | LN | 269.4 | 181 | 266 | 101.3 |  |  |  |  | 496 | G_1ANDRUS U1 ID 1+1518 | 337646 | 337648 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1286_3WOODWARD-S!,3WHT BLUFF! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
102590 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 177.8 | 95.5 | 176 | 101 |  |  |  |  | 500 | G_1CARPENTR U1 ID 1+1560 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
102591 | 15S | Approved | P3 | 37 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 165.2 | 84.4 | 176 | 93.8 |  |  |  |  | 500 | G_1CARPENTR U1 ID 1+1560 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
102592 | 15S | Approved | P3 | 37 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 175.2 | 94 | 176 | 99.5 |  |  |  |  | 500 | G_1CARPENTR U1 ID 1+1560 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
102593 | 15S | Approved | P3 | 37 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 178.6 | 95.5 | 176 | 101.5 |  |  |  |  | 501 | G_1CARPENTR U2 ID 1+1560 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
102594 | 15S | Approved | P3 | 37 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 165.9 | 84.4 | 176 | 94.2 |  |  |  |  | 501 | G_1CARPENTR U2 ID 1+1560 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
102595 | 15S | Approved | P3 | 37 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 175.9 | 94 | 176 | 99.9 |  |  |  |  | 501 | G_1CARPENTR U2 ID 1+1560 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1328_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed | No violation: below Rate A | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
102596 | 15S | Approved | P3 | 37 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 292.7 | 166.2 | 266 | 110 |  |  |  |  | 502 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
102597 | 15S | Approved | P3 | 37 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 257.4 | 128.2 | 266 | 96.8 |  |  |  |  | 502 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
102598 | 15S | Approved | P3 | 37 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 438.6 | 245.8 | 450 | 97.5 |  |  |  |  | 502 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Generation redispatch: Turn on Ritchie unit 500 MW | No violation: below Rate A
102599 | 15S | Approved | P3 | 37 | 337530 3CAMDEN MAG! 115 337536 3SMACKOVER 115 1 | LN | 99.2 | 16.5 | 98 | 101.2 |  |  |  |  | 503 | G_1MCCLELAN U1 ID 1+1493 | 337530 | 337536 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1261_3MCNEIL!,3CAMDEN MAG! | G_1MCCLELAN U1 ID 1
102600 | 15S | Approved | P3 | 37 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 85.7 | 34.1 | 77 | 111.3 |  |  |  |  | 510 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102601 | 15S | Approved | P3 | 37 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 89.2 | 35.5 | 77 | 115.8 |  |  |  |  | 510 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102602 | 15S | Approved | P3 | 37 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 85.7 | 36.8 | 77 | 111.3 |  |  |  |  | 510 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102603 | 15S | Approved | P3 | 37 | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 | LN | 69.4 | 20.6 | 77 | 90.1 |  |  |  |  | 510 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337349 | 337350 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
102604 | 15S | Approved | P3 | 37 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 103.7 | 49.1 | 111 | 93.4 |  |  |  |  | 511 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
102605 | 15S | Approved | P3 | 37 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 122.1 | 65.3 | 115 | 106.1 |  |  |  |  | 511 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102606 | 15S | Approved | P3 | 37 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 405.4 | 241 | 414 | 97.9 |  |  |  |  | 511 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
102607 | 15S | Approved | P3 | 37 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 76 | 36.8 | 77 | 98.7 |  |  |  |  | 511 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
102608 | 15S | Approved | P3 | 37 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 77.3 | 34.1 | 77 | 100.4 |  |  |  |  | 512 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102609 | 15S | Approved | P3 | 37 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 80.2 | 35.5 | 77 | 104.1 |  |  |  |  | 512 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102610 | 15S | Approved | P3 | 37 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 78.5 | 36.8 | 77 | 102 |  |  |  |  | 512 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102611 | 15S | Approved | P3 | 37 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 78 | 34.1 | 77 | 101.3 |  |  |  |  | 513 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102612 | 15S | Approved | P3 | 37 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 80.8 | 35.5 | 77 | 105 |  |  |  |  | 513 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102613 | 15S | Approved | P3 | 37 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 79.2 | 36.8 | 77 | 102.9 |  |  |  |  | 513 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
102614 | 15S | Approved | P3 | 37 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 395.2 | 234.6 | 386 | 102.4 |  |  |  |  | 514 | G_G1DOLHIL! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
102615 | 15S | Approved | P3 | 37 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 311.5 | 162 | 336 | 92.7 |  |  |  |  | 514 | G_G1DOLHIL! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
102616 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 146.9 | 91 | 150 | 97.9 |  |  |  |  | 516 | G_HARGIS1 ID 1+2122 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102617 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 150.4 | 93.1 | 150 | 100.2 |  |  |  |  | 516 | G_HARGIS1 ID 1+2122 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102618 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 146.9 | 91 | 150 | 97.9 |  |  |  |  | 517 | G_HARGIS2 ID 1+2122 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102619 | 15S | Approved | P3 | 37 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 150.4 | 93.1 | 150 | 100.2 |  |  |  |  | 517 | G_HARGIS2 ID 1+2122 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 168MVA
102620 | 23S | Approved | P0 | 38 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.9 | 331.9 | 360 | 92.2 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
102621 | 23S | Approved | P0 | 38 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.1 | 18.1 | 19 | 95.2 | [5 empty] | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
102622 | 23S | Approved | P0 | 38 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.3 | 35.3 | 39 | 90.5 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
102623 | 23S | Approved | P0 | 38 | 335094 2MOSSVILLE! 69.0 335102 2CANAL_LA 69.0 1 | LN | 40.1 | 40.1 | 38 | 105.7 | [5 empty] | ** Base Case ** | 335094 | 335102 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 11-EGL-016-01-CP | 2013-12-01 | Upgrade Mossville-Canal 69 kV Phase 1
102624 | 23S | Approved | P0 | 38 | 335217 2CHLOMAL! 69.0 335253 2LACASSINE 69.0 1 | LN | 31.2 | 31.2 | 33 | 94.6 | [5 empty] | ** Base Case ** | 335217 | 335253 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
102625 | 23S | Approved | P0 | 38 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.8 | 53.8 | 56 | 96 | [5 empty] | ** Base Case ** | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
102626 | 23S | Approved | P0 | 38 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 109.3 | 109.3 | 93 | 117.6 | [5 empty] | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
102627 | 23S | Approved | P0 | 38 | 335787 2MCMANUS 69.0 335788 2BRADY_HGHTS69.0 1 | LN | 20.3 | 20.3 | 20 | 101.6 | [5 empty] | ** Base Case ** | 335787 | 335788 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed |  | 12-EGL-004-CP | 2016-12-01 | Upgrade McManus-Brady Heights 69 kV
102628 | 23S | Approved | P0 | 38 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179.6 | 179.6 | 193 | 93.1 | [5 empty] | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | No violation: below Rate A
102629 | 23S | Approved | P0 | 38 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38 | 38 | 39 | 97.4 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
102630 | 23S | Approved | P0 | 38 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 106.5 | 106.5 | 112 | 95.1 | [5 empty] | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
102631 | 23S | Approved | P0 | 38 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 547.5 | 547.5 | 598 | 91.6 | [5 empty] | ** Base Case ** | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
102632 | 23S | Approved | P0 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100.7 | 100.7 | 95 | 106 | [5 empty] | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case **
102633 | 23S | Approved | P3 | 38 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 222 | 89.2 | 233 | 95.3 |  |  |  |  | 1 | P1_2-113_4LEBLANC!,4MORIL!+G_1WAT U3! ID 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-113_4LEBLANC!,4MORIL! | G_1WAT U3! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
102634 | 23S | Approved | P3 | 38 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 222.7 | 89.2 | 233 | 95.6 |  |  |  |  | 2 | P1_2-113_4LEBLANC!,4MORIL!+G_G3TECHE! ID 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
102635 | 23S | Approved | P3 | 38 | 335380 4MEAUX! 138 335386 4ABBEVILLE 138 1 | LN | 222 | 89.2 | 233 | 95.3 |  |  |  |  | 3 | P1_2-113_4LEBLANC!,4MORIL!+G_G1 ACAD! ID 1 | 335380 | 335386 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-113_4LEBLANC!,4MORIL! | G_G1 ACAD! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-010-HZ | 2020-06-01 | Meaux to Abbeville - Upgrade Meaux Line bay bus
102636 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.6 | 181 | 243 | 92.9 |  |  |  |  | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
102637 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.3 | 181 | 243 | 92.7 |  |  |  |  | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
102638 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334119 4TARKING! 138 1 | LN | 93.1 | 39.7 | 101 | 92.2 |  |  |  |  | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334084 | 334119 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
102639 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 221 | 181 | 243 | 91 |  |  |  |  | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
102640 | 23S | Approved | P3 | 38 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.8 | 331.9 | 360 | 92.7 |  |  |  |  | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 |  | No violation: below Rate A
102641 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334119 4TARKING! 138 1 | LN | 91.5 | 39.7 | 101 | 90.6 |  |  |  |  | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334084 | 334119 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 |  | No violation: below Rate A
102642 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334119 4TARKING! 138 1 | LN | 91.5 | 39.7 | 101 | 90.6 |  |  |  |  | 15 | P1_2-182_4PORTER%,4NEWCANY!+G_1G5SABIN! ID 1 | 334084 | 334119 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-182_4PORTER%,4NEWCANY! | G_1G5SABIN! ID 1 |  | No violation: below Rate A
102643 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.9 | 181 | 243 | 93 |  |  |  |  | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
102644 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.7 | 181 | 243 | 92.9 |  |  |  |  | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
102647 | 23S | Approved | P3 | 38 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | LN | 35.5 | 11.2 | 39 | 90.9 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334265 | 334266 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
102648 | 23S | Approved | P3 | 38 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 36 | 11.5 | 39 | 92.2 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
102649 | 23S | Approved | P3 | 38 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 36.2 | 11.6 | 39 | 92.9 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
102650 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 40.5 | 15.5 | 39 | 103.9 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
102651 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 43.4 | 18.3 | 39 | 111.2 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
102652 | 23S | Approved | P3 | 38 | 334271 2TEX-HIL 69.0 334560 2SO.BMT.! 69.0 1 | LN | 45.4 | 19.4 | 49 | 92.7 |  |  |  |  | 36 | P1_2-224_4MEMORIL!,4MID CO%+G_1G1LEWIS! ID 1 | 334271 | 334560 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
102654 | 23S | Approved | P3 | 38 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | LN | 35.4 | 11.2 | 39 | 90.7 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334265 | 334266 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
102655 | 23S | Approved | P3 | 38 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | LN | 35.9 | 11.5 | 39 | 92 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334266 | 334267 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
102656 | 23S | Approved | P3 | 38 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | LN | 36.1 | 11.6 | 39 | 92.7 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334267 | 334269 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
102657 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 40.4 | 15.5 | 39 | 103.5 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
102658 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 43.2 | 18.3 | 39 | 110.8 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
102659 | 23S | Approved | P3 | 38 | 334271 2TEX-HIL 69.0 334560 2SO.BMT.! 69.0 1 | LN | 45.3 | 19.4 | 49 | 92.4 |  |  |  |  | 37 | P1_2-224_4MEMORIL!,4MID CO%+G_1G2LEWIS! ID 1 | 334271 | 334560 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-224_4MEMORIL!,4MID CO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
102662 | 23S | Approved | P3 | 38 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 114.4 | 50 | 127 | 90 |  |  |  |  | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
102668 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 238 | 155.7 | 191 | 124.6 |  |  |  |  | 52 | P1_2-565_4MEAUX!,6MEAUX!+G_1ACADIA_S26! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102669 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 237.9 | 155.7 | 191 | 124.5 |  |  |  |  | 53 | P1_2-565_4MEAUX!,6MEAUX!+G_1ACADIA_C25! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102670 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 237.9 | 155.7 | 191 | 124.5 |  |  |  |  | 54 | P1_2-565_4MEAUX!,6MEAUX!+G_1ACADIA_C24! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102673 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 238 | 155.7 | 191 | 124.6 |  |  |  |  | 57 | P1_2-565_4MEAUX!,6MEAUX!+G_G3MADISN! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102674 | 23S | Approved | P3 | 38 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 234.7 | 105.9 | 241 | 97.4 |  |  |  |  | 58 | P1_2-565_4MEAUX!,6MEAUX!+G_G3TECHE! ID 1 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-565_4MEAUX!,6MEAUX! | G_G3TECHE! ID 1 |  | No violation: below Rate A
102682 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 237.9 | 155.7 | 191 | 124.6 |  |  |  |  | 64 | P1_2-566_6MEAUX!,SELLRD6%+G_1ACADIA_S26! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102683 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 237.9 | 155.7 | 191 | 124.5 |  |  |  |  | 65 | P1_2-566_6MEAUX!,SELLRD6%+G_1ACADIA_C25! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102684 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 237.9 | 155.7 | 191 | 124.5 |  |  |  |  | 66 | P1_2-566_6MEAUX!,SELLRD6%+G_1ACADIA_C24! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102687 | 23S | Approved | P3 | 38 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | LN | 238 | 155.7 | 191 | 124.6 |  |  |  |  | 69 | P1_2-566_6MEAUX!,SELLRD6%+G_G3MADISN! ID 1 | 335387 | 335388 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_G3MADISN! ID 1 | Project Proposed |  | 11-EGL-007-CP | 2016-06-01 | Upgrade Moril-Delcambre 138 kV station equipment
102688 | 23S | Approved | P3 | 38 | 303132 4JUDICE! 138 335379 4SCOTT_1! 138 1 | LN | 234.8 | 105.9 | 241 | 97.4 |  |  |  |  | 70 | P1_2-566_6MEAUX!,SELLRD6%+G_G3TECHE! ID 1 | 303132 | 335379 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-566_6MEAUX!,SELLRD6% | G_G3TECHE! ID 1 |  | No violation: below Rate A
102698 | 23S | Approved | P3 | 38 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 112 | 57.8 | 115 | 97.4 |  |  |  |  | 80 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1DOLHIL! ID 1 | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
102699 | 23S | Approved | P3 | 38 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 104.3 | 57.8 | 115 | 90.7 |  |  |  |  | 81 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_PIRKEY 1 ID 1 | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
102728 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 86.5 | 47.3 | 80 | 108.2 |  |  |  |  | 98 | P1_2-1214_3SWARTZ!,3STERLING%+G_G1DOLHIL! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1DOLHIL! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102729 | 23S | Approved | P3 | 38 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 243.4 | 190.8 | 262 | 92.9 |  |  |  |  | 99 | P1_2-1214_3SWARTZ!,3STERLING%+G_G1NESBIT! ID 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G1NESBIT! ID 1 | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
102731 | 23S | Approved | P3 | 38 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 244.5 | 190.8 | 262 | 93.3 |  |  |  |  | 100 | P1_2-1214_3SWARTZ!,3STERLING%+G_G2RODEMR! ID 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G2RODEMR! ID 1 | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
102732 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 86.4 | 47.3 | 80 | 108 |  |  |  |  | 100 | P1_2-1214_3SWARTZ!,3STERLING%+G_G2RODEMR! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G2RODEMR! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102733 | 23S | Approved | P3 | 38 | 337392 3WALNUT_GR_1 115 337415 3STERLING% 115 1 | LN | 245.9 | 190.8 | 262 | 93.9 |  |  |  |  | 101 | P1_2-1214_3SWARTZ!,3STERLING%+G_G3MADISN! ID 1 | 337392 | 337415 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G3MADISN! ID 1 | Project Horizon | No violation: below Rate A | 14-ELL-002-HZ | 2020-06-01 | Sterlington 115 kV Substaton: Upgrde jumpers on the Sterlington to Walnut Grove 115 kV line (line 1
102734 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 87 | 47.3 | 80 | 108.7 |  |  |  |  | 101 | P1_2-1214_3SWARTZ!,3STERLING%+G_G3MADISN! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1214_3SWARTZ!,3STERLING% | G_G3MADISN! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102759 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 106.7 | 47.3 | 80 | 133.4 |  |  |  |  | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102762 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 105.5 | 47.3 | 80 | 131.9 |  |  |  |  | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102763 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 105.6 | 47.3 | 80 | 132 |  |  |  |  | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102767 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 106 | 47.3 | 80 | 132.5 |  |  |  |  | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102768 | 23S | Approved | P3 | 38 | 337447 3TALLULAH! 115 337448 3DELHI_LA! 115 1 | LN | 105.6 | 47.3 | 80 | 132 |  |  |  |  | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337447 | 337448 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
102769 | 23S | Approved | P3 | 38 | 337619 3WOODWARD-S! 115 337621 3WATSON CHPL 115 1 | LN | 208.5 | 74.8 | 219 | 95.2 |  |  |  |  | 132 | P1_2-1293_3WOODWARD-N!,3MCCAMANT!+105 | 337619 | 337621 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1293_3WOODWARD-N!,3MCCAMANT! | G_1ANDRUS U1 ID 1 |  | No violation: below Rate A
102770 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.8 | 193.7 | 239 | 102.4 |  |  |  |  | 142 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+5 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1BCAJUN2_U1% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102772 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.9 | 193.7 | 239 | 102.5 |  |  |  |  | 143 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+6 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1BCAJUN2_U2% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102774 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.9 | 193.7 | 239 | 102.5 |  |  |  |  | 144 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+7 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1BCAJUN2_U3% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102776 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 145 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1FRNTR 1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1FRNTR 1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102778 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 146 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1FRNTR 2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1FRNTR 2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102780 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.5 | 193.7 | 239 | 102.7 |  |  |  |  | 147 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G1LEWIS! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G1LEWIS! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102782 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.4 | 193.7 | 239 | 102.7 |  |  |  |  | 148 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G2LEWIS! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G2LEWIS! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102784 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.7 | 193.7 | 239 | 102.4 |  |  |  |  | 149 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G1SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G1SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102786 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.7 | 193.7 | 239 | 102.4 |  |  |  |  | 150 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G2SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G2SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102788 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.2 | 193.7 | 239 | 103 |  |  |  |  | 151 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G3SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G3SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102791 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 247 | 193.7 | 239 | 103.4 |  |  |  |  | 152 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G4SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G4SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102793 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.4 | 193.7 | 239 | 103.1 |  |  |  |  | 153 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1G5SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1G5SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102795 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.4 | 193.7 | 239 | 102.3 |  |  |  |  | 154 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1RS_CGN_R5! ID 5 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1RS_CGN_R5! ID 5 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102797 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.4 | 193.7 | 239 | 103.1 |  |  |  |  | 155 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1NELSON_G4! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1NELSON_G4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102799 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.7 | 193.7 | 239 | 103.2 |  |  |  |  | 156 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1NELSON_G6! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1NELSON_G6! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102801 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.5 | 193.7 | 239 | 102.3 |  |  |  |  | 157 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+66 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1WILL_GL_G4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102803 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 247.5 | 193.7 | 239 | 103.6 |  |  |  |  | 158 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+71 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1RVR_BND_G1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102805 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.7 | 193.7 | 239 | 102.4 |  |  |  |  | 159 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1WAT U1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1WAT U1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102807 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.7 | 193.7 | 239 | 102.4 |  |  |  |  | 160 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1WAT U2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1WAT U2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102809 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 248.1 | 193.7 | 239 | 103.8 |  |  |  |  | 161 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1WAT U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1WAT U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102811 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.4 | 193.7 | 239 | 102.3 |  |  |  |  | 162 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1SOXY U1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1SOXY U1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102813 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.3 | 193.7 | 239 | 102.6 |  |  |  |  | 163 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1GYP U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1GYP U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102815 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.8 | 193.7 | 239 | 102.4 |  |  |  |  | 164 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1GYP U2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1GYP U2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102817 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246 | 193.7 | 239 | 102.9 |  |  |  |  | 165 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1NMIL U4! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1NMIL U4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102819 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.1 | 193.7 | 239 | 103 |  |  |  |  | 166 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1NMIL U5! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1NMIL U5! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102821 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.3 | 193.7 | 239 | 102.6 |  |  |  |  | 167 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1MICH U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1MICH U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102823 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 248 | 193.7 | 239 | 103.8 |  |  |  |  | 168 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1GGNS U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1GGNS U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102825 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.5 | 193.7 | 239 | 102.3 |  |  |  |  | 169 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1B.WLSN U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1B.WLSN U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102827 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 247.3 | 193.7 | 239 | 103.5 |  |  |  |  | 170 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1COUCH U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1COUCH U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102829 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 256.4 | 193.7 | 239 | 107.3 |  |  |  |  | 171 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1DEGRAY U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1DEGRAY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102831 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 253 | 193.7 | 239 | 105.8 |  |  |  |  | 172 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1DEGRAY U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1DEGRAY U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102834 | 23S | Approved | P3 | 38 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 179.7 | 99.2 | 159 | 113 |  |  |  |  | 173 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1BLAKELY U1 ID 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1BLAKELY U1 ID 1 | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
102836 | 23S | Approved | P3 | 38 | 337717 3HS.S 115 337718 3CARPENTER! 115 1 | LN | 179.7 | 99.2 | 159 | 113 |  |  |  |  | 174 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1BLAKELY U2 ID 1 | 337717 | 337718 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1BLAKELY U2 ID 1 | Project Approved | Model: Project 11-EAI-007-CP is not in the case | 11-EAI-007-CP | 2015-06-01 | Hot Springs Hamilton (Albright) - Carpenter Dam: Construct new 115 kV Line and convert Mountain Pine
102837 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 175 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1DUKE HS S1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1DUKE HS S1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102839 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.3 | 193.7 | 239 | 102.2 |  |  |  |  | 176 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1DUKE HS C1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1DUKE HS C1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102841 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.3 | 193.7 | 239 | 102.2 |  |  |  |  | 177 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_1DUKE HS C2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_1DUKE HS C2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102843 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 252.1 | 193.7 | 239 | 105.5 |  |  |  |  | 178 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G1DOLHIL! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G1DOLHIL! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102845 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.1 | 193.7 | 239 | 103 |  |  |  |  | 179 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G1NESBIT! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G1NESBIT! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102847 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 246.7 | 193.7 | 239 | 103.2 |  |  |  |  | 180 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G2RODEMR! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G2RODEMR! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102849 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 247.4 | 193.7 | 239 | 103.5 |  |  |  |  | 181 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G3MADISN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G3MADISN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102851 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 182 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G3TECHE! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G3TECHE! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102853 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.5 | 193.7 | 239 | 102.3 |  |  |  |  | 183 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_G1 ACAD! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_G1 ACAD! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102855 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 247.5 | 193.7 | 239 | 103.6 |  |  |  |  | 184 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_FULTONU1 1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_FULTONU1 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102857 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 253.8 | 193.7 | 239 | 106.2 |  |  |  |  | 185 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_PIRKEY 1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_PIRKEY 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102859 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 252.5 | 193.7 | 239 | 105.7 |  |  |  |  | 186 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_WELSH2-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_WELSH2-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102861 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 252.5 | 193.7 | 239 | 105.7 |  |  |  |  | 187 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_WELSH3-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_WELSH3-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102863 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 258.8 | 193.7 | 239 | 108.3 |  |  |  |  | 188 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_TURKCOAL ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_TURKCOAL ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102865 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 189 | P1_2-1332_3ARKLAHOMA%,3CHEETAH%+G_MUSKOG4G ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1332_3ARKLAHOMA%,3CHEETAH% | G_MUSKOG4G ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102867 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.8 | 193.7 | 239 | 115 |  |  |  |  | 190 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+5 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BCAJUN2_U1% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102871 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.9 | 193.7 | 239 | 115 |  |  |  |  | 191 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+6 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BCAJUN2_U2% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102875 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.9 | 193.7 | 239 | 115 |  |  |  |  | 192 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+7 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BCAJUN2_U3% ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102883 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.8 | 193.7 | 239 | 115 |  |  |  |  | 194 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1FRNTR 1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1FRNTR 1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102887 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.8 | 193.7 | 239 | 115 |  |  |  |  | 195 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1FRNTR 2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1FRNTR 2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102891 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 275.3 | 193.7 | 239 | 115.2 |  |  |  |  | 196 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G1LEWIS! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G1LEWIS! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102892 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 186.5 | 99.4 | 176 | 105.9 |  |  |  |  | 196 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G1LEWIS! ID 1 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
102895 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 275.3 | 193.7 | 239 | 115.2 |  |  |  |  | 197 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G2LEWIS! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G2LEWIS! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102896 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 186.5 | 99.4 | 176 | 106 |  |  |  |  | 197 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G2LEWIS! ID 1 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
102903 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.5 | 193.7 | 239 | 114.8 |  |  |  |  | 199 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G1SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G1SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102907 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.5 | 193.7 | 239 | 114.8 |  |  |  |  | 200 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G2SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G2SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102911 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.2 | 193.7 | 239 | 115.5 |  |  |  |  | 201 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G3SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G3SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102916 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 277.2 | 193.7 | 239 | 116 |  |  |  |  | 202 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G4SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G4SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102920 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.4 | 193.7 | 239 | 115.7 |  |  |  |  | 203 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1G5SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1G5SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102936 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.5 | 193.7 | 239 | 115.7 |  |  |  |  | 207 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+48 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1NELSON_G4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102940 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.8 | 193.7 | 239 | 115.8 |  |  |  |  | 208 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+49 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1NELSON_G6! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102956 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.4 | 193.7 | 239 | 114.8 |  |  |  |  | 212 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+66 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1WILL_GL_G4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102960 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 278.3 | 193.7 | 239 | 116.4 |  |  |  |  | 213 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+71 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1RVR_BND_G1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102964 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.6 | 193.7 | 239 | 114.9 |  |  |  |  | 214 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1WAT U1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1WAT U1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102968 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.6 | 193.7 | 239 | 114.9 |  |  |  |  | 215 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1WAT U2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1WAT U2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102972 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 279 | 193.7 | 239 | 116.7 |  |  |  |  | 216 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1WAT U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1WAT U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102976 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.4 | 193.7 | 239 | 114.8 |  |  |  |  | 217 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1SOXY U1! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1SOXY U1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102980 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 275.5 | 193.7 | 239 | 115.3 |  |  |  |  | 218 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1GYP U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1GYP U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102988 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.8 | 193.7 | 239 | 115 |  |  |  |  | 220 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1GYP U2! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1GYP U2! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102992 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.4 | 193.7 | 239 | 115.6 |  |  |  |  | 221 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1NMIL U4! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1NMIL U4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
102996 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.5 | 193.7 | 239 | 115.7 |  |  |  |  | 222 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1NMIL U5! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1NMIL U5! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103000 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 275.4 | 193.7 | 239 | 115.2 |  |  |  |  | 223 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1MICH U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1MICH U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103008 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 279.4 | 193.7 | 239 | 116.9 |  |  |  |  | 225 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1GGNS U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1GGNS U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103012 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.5 | 193.7 | 239 | 114.9 |  |  |  |  | 226 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+96 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1B.WLSN U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103017 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 188.7 | 99.4 | 176 | 107.2 |  |  |  |  | 227 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+105 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
103020 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 277.1 | 193.7 | 239 | 115.9 |  |  |  |  | 228 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_1COUCH U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1COUCH U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103024 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 286.7 | 193.7 | 239 | 120 |  |  |  |  | 229 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+135 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1DEGRAY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103028 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 283 | 193.7 | 239 | 118.4 |  |  |  |  | 230 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+136 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1DEGRAY U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103033 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 205.6 | 99.4 | 176 | 116.8 |  |  |  |  | 231 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+142 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
103034 | 23S | Approved | P3 | 38 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 190.6 | 86.8 | 176 | 108.3 |  |  |  |  | 231 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+142 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
103035 | 23S | Approved | P3 | 38 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 202.3 | 97.9 | 176 | 114.9 |  |  |  |  | 231 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+142 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U1 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
103037 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 205.6 | 99.4 | 176 | 116.8 |  |  |  |  | 232 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+143 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
103038 | 23S | Approved | P3 | 38 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 190.6 | 86.8 | 176 | 108.3 |  |  |  |  | 232 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+143 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
103039 | 23S | Approved | P3 | 38 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 202.3 | 97.9 | 176 | 114.9 |  |  |  |  | 232 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+143 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1BLAKELY U2 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
103040 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 278.1 | 193.7 | 239 | 116.4 |  |  |  |  | 233 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+144 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103041 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 207.5 | 99.4 | 176 | 117.9 |  |  |  |  | 233 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+144 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
103042 | 23S | Approved | P3 | 38 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 192.7 | 86.8 | 176 | 109.5 |  |  |  |  | 233 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+144 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
103043 | 23S | Approved | P3 | 38 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 204.4 | 97.9 | 176 | 116.1 |  |  |  |  | 233 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+144 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U1 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
103044 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 278.3 | 193.7 | 239 | 116.4 |  |  |  |  | 234 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+145 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103045 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337734 3HS IND 115 1 | LN | 208.3 | 99.4 | 176 | 118.3 |  |  |  |  | 234 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+145 | 337685 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-016-CP | 2015-06-01 | Upgrade HS EHV-HS Industrial 115 kV terminal equipment
103046 | 23S | Approved | P3 | 38 | 337731 3HS.E+ 115 337733 3HS UCARBIDE 115 1 | LN | 193.4 | 86.8 | 176 | 109.9 |  |  |  |  | 234 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+145 | 337731 | 337733 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-018-CP | 2015-06-01 | Upgrade HS Union Carbide-HS East 115 kV terminal equipment
103047 | 23S | Approved | P3 | 38 | 337733 3HS UCARBIDE 115 337734 3HS IND 115 1 | LN | 205.1 | 97.9 | 176 | 116.5 |  |  |  |  | 234 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+145 | 337733 | 337734 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1CARPENTR U2 ID 1 | Project Proposed |  | 12-EAI-017-CP | 2015-06-01 | Upgrade HS Industrial-HS Union Carbide 115 kV terminal equipment
103048 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.8 | 193.7 | 239 | 115 |  |  |  |  | 235 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+146 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_1DUKE HS S1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103064 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 282.2 | 193.7 | 239 | 118.1 |  |  |  |  | 239 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G1DOLHIL! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G1DOLHIL! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103068 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.1 | 193.7 | 239 | 115.5 |  |  |  |  | 240 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G1NESBIT! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G1NESBIT! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103072 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 276.7 | 193.7 | 239 | 115.8 |  |  |  |  | 241 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G2RODEMR! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G2RODEMR! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103076 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 277.6 | 193.7 | 239 | 116.2 |  |  |  |  | 242 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G3MADISN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G3MADISN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103080 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 275 | 193.7 | 239 | 115.1 |  |  |  |  | 243 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G3TECHE! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G3TECHE! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103084 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 274.3 | 193.7 | 239 | 114.8 |  |  |  |  | 244 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_G1 ACAD! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_G1 ACAD! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103088 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 277.2 | 193.7 | 239 | 116 |  |  |  |  | 245 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+206 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_FULTONU1 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103092 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 283.8 | 193.7 | 239 | 118.8 |  |  |  |  | 246 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_PIRKEY 1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_PIRKEY 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103096 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 282.4 | 193.7 | 239 | 118.2 |  |  |  |  | 247 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_WELSH2-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_WELSH2-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103100 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 282.5 | 193.7 | 239 | 118.2 |  |  |  |  | 248 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_WELSH3-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_WELSH3-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103104 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 288.9 | 193.7 | 239 | 120.9 |  |  |  |  | 249 | P1_2-1333_3ARKLAHOMA%,3CARPENTER!+G_TURKCOAL ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1333_3ARKLAHOMA%,3CARPENTER! | G_TURKCOAL ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103124 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242.3 | 193.7 | 239 | 101.4 |  |  |  |  | 257 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1G1LEWIS! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1G1LEWIS! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103132 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.1 | 193.7 | 239 | 101.7 |  |  |  |  | 261 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1G3SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1G3SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103135 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.9 | 193.7 | 239 | 102 |  |  |  |  | 262 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1G4SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1G4SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103137 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.3 | 193.7 | 239 | 101.8 |  |  |  |  | 263 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1G5SABIN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1G5SABIN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103141 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.2 | 193.7 | 239 | 101.8 |  |  |  |  | 265 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1NELSON_G4! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1NELSON_G4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103143 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.6 | 193.7 | 239 | 101.9 |  |  |  |  | 266 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1NELSON_G6! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1NELSON_G6! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103149 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.5 | 193.7 | 239 | 102.3 |  |  |  |  | 269 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+71 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1RVR_BND_G1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103155 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.1 | 193.7 | 239 | 102.6 |  |  |  |  | 272 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1WAT U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1WAT U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103159 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242.3 | 193.7 | 239 | 101.4 |  |  |  |  | 274 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1GYP U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1GYP U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103163 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243 | 193.7 | 239 | 101.7 |  |  |  |  | 276 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1NMIL U4! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1NMIL U4! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103165 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243 | 193.7 | 239 | 101.7 |  |  |  |  | 277 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1NMIL U5! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1NMIL U5! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103167 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242.3 | 193.7 | 239 | 101.4 |  |  |  |  | 278 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1MICH U3! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1MICH U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103169 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.2 | 193.7 | 239 | 102.6 |  |  |  |  | 279 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1GGNS U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1GGNS U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103173 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.2 | 193.7 | 239 | 102.2 |  |  |  |  | 281 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1COUCH U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1COUCH U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103175 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 253.2 | 193.7 | 239 | 105.9 |  |  |  |  | 282 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1DEGRAY U1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1DEGRAY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103177 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 249.7 | 193.7 | 239 | 104.5 |  |  |  |  | 283 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_1DEGRAY U2 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1DEGRAY U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103179 | 23S | Approved | P3 | 38 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 549.3 | 547.5 | 598 | 91.8 |  |  |  |  | 284 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+138 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1CATHRINE U3 ID 1 |  | No violation: below Rate A
103182 | 23S | Approved | P3 | 38 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 548.9 | 547.5 | 598 | 91.8 |  |  |  |  | 285 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+139 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1CATHRINE U1 ID 1 |  | No violation: below Rate A
103184 | 23S | Approved | P3 | 38 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | LN | 166.4 | 91.3 | 159 | 104.6 |  |  |  |  | 286 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+140 | 337799 | 337803 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_1CATHRINE U4 ID 1 | Project Horizon |  | 12-EAI-014-HZ | 2020-06-01 | Mabelvale-Bryant: Reconductor 115kV line
103199 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 248.7 | 193.7 | 239 | 104 |  |  |  |  | 294 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_G1DOLHIL! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_G1DOLHIL! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103201 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243 | 193.7 | 239 | 101.7 |  |  |  |  | 295 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_G1NESBIT! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_G1NESBIT! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103203 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 243.6 | 193.7 | 239 | 101.9 |  |  |  |  | 296 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_G2RODEMR! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_G2RODEMR! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103205 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.4 | 193.7 | 239 | 102.2 |  |  |  |  | 297 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_G3MADISN! ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_G3MADISN! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103211 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.2 | 193.7 | 239 | 102.2 |  |  |  |  | 300 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_FULTONU1 1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_FULTONU1 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103213 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 250.2 | 193.7 | 239 | 104.7 |  |  |  |  | 301 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_PIRKEY 1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_PIRKEY 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103215 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 249.1 | 193.7 | 239 | 104.2 |  |  |  |  | 302 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_WELSH2-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_WELSH2-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103217 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 249.1 | 193.7 | 239 | 104.2 |  |  |  |  | 303 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_WELSH3-1 ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_WELSH3-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103219 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 255.1 | 193.7 | 239 | 106.7 |  |  |  |  | 304 | P1_2-1346_3HS EHV-E!,3WOODLAWN%+G_TURKCOAL ID 1 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1346_3HS EHV-E!,3WOODLAWN% | G_TURKCOAL ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103223 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 106.8 | 48.6 | 106 | 100.8 |  |  |  |  | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103224 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 99.1 | 45.9 | 106 | 93.5 |  |  |  |  | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103225 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.3 | 48.6 | 106 | 103.1 |  |  |  |  | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103226 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.6 | 45.9 | 106 | 95.8 |  |  |  |  | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103227 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.7 | 42.3 | 106 | 90.2 |  |  |  |  | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103228 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.3 | 48.6 | 106 | 103.1 |  |  |  |  | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103229 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.6 | 45.9 | 106 | 95.8 |  |  |  |  | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103230 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.7 | 42.3 | 106 | 90.2 |  |  |  |  | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103231 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.3 | 48.6 | 106 | 103.1 |  |  |  |  | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103232 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.6 | 45.9 | 106 | 95.8 |  |  |  |  | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103233 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.7 | 42.3 | 106 | 90.2 |  |  |  |  | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103234 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.3 | 48.6 | 106 | 103.1 |  |  |  |  | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103235 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.6 | 45.9 | 106 | 95.8 |  |  |  |  | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103236 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.7 | 42.3 | 106 | 90.2 |  |  |  |  | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103237 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109 | 48.6 | 106 | 102.9 |  |  |  |  | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103238 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.3 | 45.9 | 106 | 95.5 |  |  |  |  | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103239 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.8 | 48.6 | 106 | 103.6 |  |  |  |  | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103240 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 102 | 45.9 | 106 | 96.2 |  |  |  |  | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103241 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 96 | 42.3 | 106 | 90.6 |  |  |  |  | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103242 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 107.5 | 48.6 | 106 | 101.4 |  |  |  |  | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103243 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 99.9 | 45.9 | 106 | 94.2 |  |  |  |  | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103244 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 111.6 | 48.6 | 106 | 105.3 |  |  |  |  | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103245 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 103.7 | 45.9 | 106 | 97.8 |  |  |  |  | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103246 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 97.7 | 42.3 | 106 | 92.2 |  |  |  |  | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103247 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.3 | 48.6 | 106 | 103.2 |  |  |  |  | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103248 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101.6 | 45.9 | 106 | 95.8 |  |  |  |  | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103249 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.7 | 42.3 | 106 | 90.2 |  |  |  |  | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103250 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 110.7 | 48.6 | 106 | 104.4 |  |  |  |  | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103251 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 102.8 | 45.9 | 106 | 97 |  |  |  |  | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103252 | 23S | Approved | P3 | 38 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 96.8 | 42.3 | 106 | 91.3 |  |  |  |  | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103253 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.8 | 48.6 | 106 | 102.6 |  |  |  |  | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103254 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101 | 45.9 | 106 | 95.3 |  |  |  |  | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103255 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.8 | 48.6 | 106 | 102.6 |  |  |  |  | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103256 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101 | 45.9 | 106 | 95.3 |  |  |  |  | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103257 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.8 | 48.6 | 106 | 102.6 |  |  |  |  | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103258 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101 | 45.9 | 106 | 95.3 |  |  |  |  | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103259 | 23S | Approved | P3 | 38 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 108.8 | 48.6 | 106 | 102.6 |  |  |  |  | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103260 | 23S | Approved | P3 | 38 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 101 | 45.9 | 106 | 95.3 |  |  |  |  | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103262 | 23S | Approved | P3 | 38 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 105.2 | 61.1 | 106 | 99.3 |  |  |  |  | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103263 | 23S | Approved | P3 | 38 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 105.3 | 61.1 | 106 | 99.3 |  |  |  |  | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103264 | 23S | Approved | P3 | 38 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 105.2 | 61.1 | 106 | 99.3 |  |  |  |  | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103265 | 23S | Approved | P3 | 38 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 105.3 | 61.1 | 106 | 99.3 |  |  |  |  | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103266 | 23S | Approved | P3 | 38 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 105.2 | 61.1 | 106 | 99.3 |  |  |  |  | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103267 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 241.2 | 105.1 | 226 | 106.7 |  |  |  |  | 327 | P1_2-1563_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1NM G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103268 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 246.8 | 105.1 | 226 | 109.2 |  |  |  |  | 328 | P1_2-1563_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1PLUM PT U1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103269 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 243.8 | 105.1 | 226 | 107.9 |  |  |  |  | 329 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103270 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 243.8 | 105.1 | 226 | 107.9 |  |  |  |  | 330 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103271 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 243.8 | 105.1 | 226 | 107.9 |  |  |  |  | 331 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103272 | 23S | Approved | P3 | 38 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 243.7 | 105.1 | 226 | 107.8 |  |  |  |  | 332 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103274 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.6 | 271.2 | 335 | 110.9 |  |  |  |  | 390 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility
103275 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.6 | 271.2 | 335 | 110.9 |  |  |  |  | 391 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility
103276 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.2 | 271.2 | 335 | 113.2 |  |  |  |  | 392 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility
103277 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.7 | 271.2 | 335 | 113.3 |  |  |  |  | 393 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility
103278 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.6 | 271.2 | 335 | 113.3 |  |  |  |  | 394 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility
103279 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.8 | 271.2 | 335 | 111 |  |  |  |  | 395 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility
103280 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.7 | 271.2 | 335 | 111 |  |  |  |  | 396 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility
103281 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.7 | 271.2 | 335 | 111 |  |  |  |  | 397 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility
103282 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.8 | 271.2 | 335 | 110.4 |  |  |  |  | 398 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility
103283 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.5 | 271.2 | 335 | 110.6 |  |  |  |  | 399 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility
103284 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.8 | 271.2 | 335 | 110.7 |  |  |  |  | 400 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility
103285 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 401 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility
103286 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 402 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility
103287 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.7 | 271.2 | 335 | 110.4 |  |  |  |  | 403 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility
103288 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.4 | 271.2 | 335 | 111.5 |  |  |  |  | 404 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility
103289 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.4 | 271.2 | 335 | 111.5 |  |  |  |  | 405 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility
103290 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.2 | 271.2 | 335 | 111.4 |  |  |  |  | 406 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_S1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_S1! ID 1 |  | No violation: CLECO facility
103291 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.3 | 271.2 | 335 | 111.4 |  |  |  |  | 407 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G1! ID 1 |  | No violation: CLECO facility
103292 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 375.3 | 271.2 | 335 | 112 |  |  |  |  | 408 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G2! ID 1 |  | No violation: CLECO facility
103293 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 377.7 | 271.2 | 335 | 112.7 |  |  |  |  | 409 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G4! ID 1 |  | No violation: CLECO facility
103294 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.9 | 271.2 | 335 | 110.4 |  |  |  |  | 410 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility
103295 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 411 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility
103296 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.3 | 271.2 | 335 | 110.2 |  |  |  |  | 412 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility
103297 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 401 | 271.2 | 335 | 119.7 |  |  |  |  | 413 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
103298 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379 | 271.2 | 335 | 113.1 |  |  |  |  | 414 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U1! ID 1 |  | No violation: CLECO facility
103299 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379 | 271.2 | 335 | 113.1 |  |  |  |  | 415 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U2! ID 1 |  | No violation: CLECO facility
103300 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 404.1 | 271.2 | 335 | 120.6 |  |  |  |  | 416 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility
103301 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 377.3 | 271.2 | 335 | 112.6 |  |  |  |  | 417 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1SOXY U1! ID 1 |  | No violation: CLECO facility
103302 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 418 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility
103303 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 419 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility
103304 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 383.6 | 271.2 | 335 | 114.5 |  |  |  |  | 420 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U3! ID 1 |  | No violation: CLECO facility
103305 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 375.6 | 271.2 | 335 | 112.1 |  |  |  |  | 421 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U1! ID 1 |  | No violation: CLECO facility
103306 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 380.4 | 271.2 | 335 | 113.5 |  |  |  |  | 422 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U2! ID 1 |  | No violation: CLECO facility
103307 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.3 | 271.2 | 335 | 111.4 |  |  |  |  | 423 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility
103308 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.3 | 271.2 | 335 | 111.4 |  |  |  |  | 424 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility
103309 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 374.2 | 271.2 | 335 | 111.7 |  |  |  |  | 425 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility
103310 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 388.6 | 271.2 | 335 | 116 |  |  |  |  | 426 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
103311 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 389.1 | 271.2 | 335 | 116.1 |  |  |  |  | 427 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
103312 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.1 | 271.2 | 335 | 110.8 |  |  |  |  | 428 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U3! ID 1 |  | No violation: CLECO facility
103313 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 374.6 | 271.2 | 335 | 111.8 |  |  |  |  | 429 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1MICH U2! ID 1 |  | No violation: CLECO facility
103314 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 382.8 | 271.2 | 335 | 114.3 |  |  |  |  | 430 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1MICH U3! ID 1 |  | No violation: CLECO facility
103315 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.2 | 271.2 | 335 | 110.2 |  |  |  |  | 431 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK1 ID 1 |  | No violation: CLECO facility
103316 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.2 | 271.2 | 335 | 110.2 |  |  |  |  | 432 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK2 ID 1 |  | No violation: CLECO facility
103317 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.2 | 271.2 | 335 | 110.2 |  |  |  |  | 433 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK3 ID 1 |  | No violation: CLECO facility
103318 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.3 | 271.2 | 335 | 110.5 |  |  |  |  | 434 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility
103319 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 383.7 | 271.2 | 335 | 114.5 |  |  |  |  | 435 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GGNS U1 ID 1 |  | No violation: CLECO facility
103320 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 371.4 | 271.2 | 335 | 110.9 |  |  |  |  | 436 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility
103321 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.8 | 271.2 | 335 | 110.4 |  |  |  |  | 437 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS G2 ID 1 |  | No violation: CLECO facility
103322 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.8 | 271.2 | 335 | 110.4 |  |  |  |  | 438 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS G1 ID 1 |  | No violation: CLECO facility
103323 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.4 | 271.2 | 335 | 110.3 |  |  |  |  | 439 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS S1 ID 1 |  | No violation: CLECO facility
103324 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.1 | 271.2 | 335 | 110.2 |  |  |  |  | 440 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1REX BRWN U4 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1REX BRWN U4 ID 1 |  | No violation: CLECO facility
103325 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.4 | 271.2 | 335 | 110.3 |  |  |  |  | 441 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility
103326 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.4 | 271.2 | 335 | 110.3 |  |  |  |  | 442 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility
103327 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.4 | 271.2 | 335 | 110.3 |  |  |  |  | 443 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility
103328 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370 | 271.2 | 335 | 110.5 |  |  |  |  | 444 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility
103329 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 386.9 | 271.2 | 335 | 115.5 |  |  |  |  | 445 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G3TECHE! ID 1 |  | No violation: CLECO facility
103330 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.9 | 271.2 | 335 | 110.4 |  |  |  |  | 446 | P1_2-1642_COCODR 6%,VILPLT 6!+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_TECHE_BS! ID 1 |  | No violation: CLECO facility
103331 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 374.7 | 271.2 | 335 | 111.8 |  |  |  |  | 447 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1 ACAD! ID 1 |  | No violation: CLECO facility
103332 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 372.6 | 271.2 | 335 | 111.2 |  |  |  |  | 448 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility
103333 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 372.6 | 271.2 | 335 | 111.2 |  |  |  |  | 449 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility
103334 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.6 | 271.2 | 335 | 110.3 |  |  |  |  | 450 | P1_2-1642_COCODR 6%,VILPLT 6!+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_LABBE2 ID 1 |  | No violation: CLECO facility
103335 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.8 | 271.2 | 335 | 110.7 |  |  |  |  | 451 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HARGIS1 ID 1 |  | No violation: CLECO facility
103336 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.8 | 271.2 | 335 | 110.7 |  |  |  |  | 452 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HARGIS2 ID 1 |  | No violation: CLECO facility
103337 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 372.3 | 271.2 | 335 | 111.1 |  |  |  |  | 453 | P1_2-1642_COCODR 6%,VILPLT 6!+G_BONIN2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_BONIN2 ID 1 |  | No violation: CLECO facility
103338 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.2 | 271.2 | 335 | 110.2 |  |  |  |  | 454 | P1_2-1642_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility
103339 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.1 | 271.2 | 335 | 110.5 |  |  |  |  | 455 | P1_2-1642_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility
103340 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.4 | 271.2 | 335 | 110.6 |  |  |  |  | 456 | P1_2-1642_COCODR 6%,VILPLT 6!+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility
103341 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.5 | 271.2 | 335 | 110.6 |  |  |  |  | 457 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HOUMA 3 ID 1 |  | No violation: CLECO facility
103343 | 23S | Approved | P3 | 38 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 202.7 | 16.7 | 225 | 90.1 |  |  |  |  | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
103344 | 23S | Approved | P3 | 38 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 208.3 | 16.7 | 225 | 92.6 |  |  |  |  | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
103345 | 23S | Approved | P3 | 38 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 205.8 | 16.7 | 225 | 91.5 |  |  |  |  | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
103346 | 23S | Approved | P3 | 38 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 208.8 | 157.6 | 225 | 92.8 |  |  |  |  | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon | No violation: below Rate A | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
103347 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.7 | 271.2 | 335 | 107.7 |  |  |  |  | 476 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility
103348 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.7 | 271.2 | 335 | 107.7 |  |  |  |  | 477 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility
103349 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.3 | 271.2 | 335 | 109.9 |  |  |  |  | 478 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility
103350 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.8 | 271.2 | 335 | 110.1 |  |  |  |  | 479 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility
103351 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.7 | 271.2 | 335 | 110 |  |  |  |  | 480 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility
103352 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361 | 271.2 | 335 | 107.8 |  |  |  |  | 481 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility
103353 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.9 | 271.2 | 335 | 107.7 |  |  |  |  | 482 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility
103354 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.9 | 271.2 | 335 | 107.7 |  |  |  |  | 483 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility
103355 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.9 | 271.2 | 335 | 107.1 |  |  |  |  | 484 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103356 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.7 | 271.2 | 335 | 107.4 |  |  |  |  | 485 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103357 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.9 | 271.2 | 335 | 107.4 |  |  |  |  | 486 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103358 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 271.2 | 335 | 107.4 |  |  |  |  | 487 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103359 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 271.2 | 335 | 107.4 |  |  |  |  | 488 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103360 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.9 | 271.2 | 335 | 107.1 |  |  |  |  | 489 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103361 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.5 | 271.2 | 335 | 108.2 |  |  |  |  | 490 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility
103362 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.5 | 271.2 | 335 | 108.2 |  |  |  |  | 491 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility
103363 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.4 | 271.2 | 335 | 108.2 |  |  |  |  | 492 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_S1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_S1! ID 1 |  | No violation: CLECO facility
103364 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.4 | 271.2 | 335 | 108.2 |  |  |  |  | 493 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G1! ID 1 |  | No violation: CLECO facility
103365 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.5 | 271.2 | 335 | 108.8 |  |  |  |  | 494 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G2! ID 1 |  | No violation: CLECO facility
103366 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 367 | 271.2 | 335 | 109.6 |  |  |  |  | 495 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G4! ID 1 |  | No violation: CLECO facility
103367 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 271.2 | 335 | 107.2 |  |  |  |  | 496 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103368 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 271.2 | 335 | 107.3 |  |  |  |  | 497 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103369 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.4 | 271.2 | 335 | 107 |  |  |  |  | 498 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103370 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 390.3 | 271.2 | 335 | 116.5 |  |  |  |  | 499 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
103371 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.1 | 271.2 | 335 | 109.9 |  |  |  |  | 500 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U1! ID 1 |  | No violation: CLECO facility
103372 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.1 | 271.2 | 335 | 109.9 |  |  |  |  | 501 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U2! ID 1 |  | No violation: CLECO facility
103373 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 393.2 | 271.2 | 335 | 117.4 |  |  |  |  | 502 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility
103374 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 366.4 | 271.2 | 335 | 109.4 |  |  |  |  | 503 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1SOXY U1! ID 1 |  | No violation: CLECO facility
103375 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 271.2 | 335 | 107.3 |  |  |  |  | 504 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103376 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 271.2 | 335 | 107.3 |  |  |  |  | 505 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103377 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373 | 271.2 | 335 | 111.3 |  |  |  |  | 506 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U3! ID 1 |  | No violation: CLECO facility
103378 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.7 | 271.2 | 335 | 108.9 |  |  |  |  | 507 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U1! ID 1 |  | No violation: CLECO facility
103379 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.5 | 271.2 | 335 | 110.3 |  |  |  |  | 508 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U2! ID 1 |  | No violation: CLECO facility
103380 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.4 | 271.2 | 335 | 108.2 |  |  |  |  | 509 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility
103381 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.4 | 271.2 | 335 | 108.2 |  |  |  |  | 510 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility
103382 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.3 | 271.2 | 335 | 108.4 |  |  |  |  | 511 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility
103383 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 378 | 271.2 | 335 | 112.8 |  |  |  |  | 512 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
103384 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 378.5 | 271.2 | 335 | 113 |  |  |  |  | 513 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
103385 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 271.2 | 335 | 107.5 |  |  |  |  | 514 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U3! ID 1 |  | No violation: CLECO facility
103386 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.7 | 271.2 | 335 | 108.6 |  |  |  |  | 515 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1MICH U2! ID 1 |  | No violation: CLECO facility
103387 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 372.3 | 271.2 | 335 | 111.1 |  |  |  |  | 516 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1MICH U3! ID 1 |  | No violation: CLECO facility
103388 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.3 | 271.2 | 335 | 107 |  |  |  |  | 517 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ISLVCRK1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ISLVCRK1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103389 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.3 | 271.2 | 335 | 107 |  |  |  |  | 518 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ISLVCRK2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ISLVCRK2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103390 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.3 | 271.2 | 335 | 107 |  |  |  |  | 519 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ISLVCRK3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ISLVCRK3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103391 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.4 | 271.2 | 335 | 107.3 |  |  |  |  | 520 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103392 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.1 | 271.2 | 335 | 111.4 |  |  |  |  | 521 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GGNS U1 ID 1 |  | No violation: CLECO facility
103393 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.5 | 271.2 | 335 | 107.6 |  |  |  |  | 522 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility
103394 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359 | 271.2 | 335 | 107.1 |  |  |  |  | 523 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103395 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359 | 271.2 | 335 | 107.1 |  |  |  |  | 524 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103396 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.5 | 271.2 | 335 | 107 |  |  |  |  | 525 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103397 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.6 | 271.2 | 335 | 107 |  |  |  |  | 526 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103398 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.6 | 271.2 | 335 | 107 |  |  |  |  | 527 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103399 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.5 | 271.2 | 335 | 107 |  |  |  |  | 528 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103400 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 271.2 | 335 | 107.2 |  |  |  |  | 529 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103401 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 375.9 | 271.2 | 335 | 112.2 |  |  |  |  | 530 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G3TECHE! ID 1 |  | No violation: CLECO facility
103402 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 271.2 | 335 | 107.2 |  |  |  |  | 531 | P1_2-1726_VILPLT 6!,WELLS 6%+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103403 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.6 | 271.2 | 335 | 108.5 |  |  |  |  | 532 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1 ACAD! ID 1 |  | No violation: CLECO facility
103404 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.6 | 271.2 | 335 | 107.9 |  |  |  |  | 533 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility
103405 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.6 | 271.2 | 335 | 107.9 |  |  |  |  | 534 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility
103406 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.6 | 271.2 | 335 | 107 |  |  |  |  | 535 | P1_2-1726_VILPLT 6!,WELLS 6%+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103407 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 271.2 | 335 | 107.6 |  |  |  |  | 536 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HARGIS1 ID 1 |  | No violation: CLECO facility
103408 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 271.2 | 335 | 107.6 |  |  |  |  | 537 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HARGIS2 ID 1 |  | No violation: CLECO facility
103409 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.3 | 271.2 | 335 | 107.9 |  |  |  |  | 538 | P1_2-1726_VILPLT 6!,WELLS 6%+G_BONIN2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_BONIN2 ID 1 |  | No violation: CLECO facility
103410 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.4 | 271.2 | 335 | 107 |  |  |  |  | 539 | P1_2-1726_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103411 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.2 | 271.2 | 335 | 107.2 |  |  |  |  | 540 | P1_2-1726_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103412 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 271.2 | 335 | 107.3 |  |  |  |  | 541 | P1_2-1726_VILPLT 6!,WELLS 6%+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103413 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.7 | 271.2 | 335 | 107.4 |  |  |  |  | 542 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HOUMA 3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103414 | 23S | Approved | P3 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.7 | 100.7 | 95 | 108.1 |  |  |  |  | 543 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+74 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
103415 | 23S | Approved | P3 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 103.1 | 100.7 | 95 | 108.5 |  |  |  |  | 544 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+190 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | Facility: Radial
103416 | 23S | Approved | P3 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 103.1 | 100.7 | 95 | 108.5 |  |  |  |  | 545 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+196 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | Facility: Radial
103417 | 23S | Approved | P3 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 103.1 | 100.7 | 95 | 108.5 |  |  |  |  | 546 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+197 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 |  | Facility: Radial
103418 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.1 | 65 | 115 | 101.8 |  |  |  |  | 547 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+198 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103419 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.1 | 65 | 115 | 101.8 |  |  |  |  | 548 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+199 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103420 | 23S | Approved | P3 | 38 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.9 | 100.7 | 95 | 108.3 |  |  |  |  | 549 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+200 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
103421 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565 | 331.2 | 561 | 100.7 |  |  |  |  | 552 | G_1NM G1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1NM G1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103422 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.3 | 123.8 | 159 | 100.8 |  |  |  |  | 553 | G_1NM G1 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1NM G1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103423 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.3 | 123.8 | 159 | 100.8 |  |  |  |  | 554 | G_1NM G1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1NM G1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103424 | 23S | Approved | P3 | 38 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 150.7 | 85.8 | 148 | 101.9 |  |  |  |  | 555 | G_1NM G1 ID 1+P1_2-1496_5NEWPORT!,5JONESBORO! | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496_5NEWPORT!,5JONESBORO! | G_1NM G1 ID 1 | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
103425 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 135.6 | 108.5 | 148 | 91.6 |  |  |  |  | 556 | G_1NM G1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1NM G1 ID 1 |  | No violation: below Rate A
103426 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 144.3 | 115.6 | 160 | 90.2 |  |  |  |  | 556 | G_1NM G1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1NM G1 ID 1 |  | No violation: below Rate A
103427 | 23S | Approved | P3 | 38 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 151.4 | 85.8 | 148 | 102.3 |  |  |  |  | 558 | G_1STFRG1 ID 1+P1_2-1496_5NEWPORT!,5JONESBORO! | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496_5NEWPORT!,5JONESBORO! | G_1STFRG1 ID 1 | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
103428 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.4 | 108.5 | 148 | 92.2 |  |  |  |  | 559 | G_1STFRG1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1STFRG1 ID 1 |  | No violation: below Rate A
103429 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145.2 | 115.6 | 160 | 90.7 |  |  |  |  | 559 | G_1STFRG1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1STFRG1 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103430 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.1 | 331.2 | 561 | 100.7 |  |  |  |  | 564 | G_1BCAJUN2_U1% ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103431 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 566 | G_1BCAJUN2_U2% ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1BCAJUN2_U2% ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103432 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.3 | 331.2 | 561 | 100.8 |  |  |  |  | 568 | G_1BCAJUN2_U3% ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103434 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 216.3 | 126.2 | 206 | 105 |  |  |  |  | 574 | G_1FRNTR 1! ID 1+P1_2-144_7GRIMES%,CROCKET7% | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-144_7GRIMES%,CROCKET7% | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103435 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 207.5 | 126.2 | 206 | 100.7 |  |  |  |  | 575 | G_1FRNTR 1! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103436 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 201.2 | 126.2 | 206 | 97.7 |  |  |  |  | 576 | G_1FRNTR 1! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 1! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103437 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 224.8 | 181 | 243 | 92.5 |  |  |  |  | 577 | G_1FRNTR 1! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1FRNTR 1! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103438 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 206.5 | 91.6 | 206 | 100.2 |  |  |  |  | 577 | G_1FRNTR 1! ID 1+P1_2-184_4PORTER%,6PORTER% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1FRNTR 1! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103440 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 211 | 126.2 | 206 | 102.4 |  |  |  |  | 579 | G_1FRNTR 1! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1863_LEBROCK7!,TENRUSK7! | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103442 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 210.8 | 126.2 | 206 | 102.3 |  |  |  |  | 580 | G_1FRNTR 1! ID 1+P1_2-1865_TENRUSK7!,CROCKET7% | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1865_TENRUSK7!,CROCKET7% | G_1FRNTR 1! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103444 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 216.3 | 126.2 | 206 | 105 |  |  |  |  | 581 | G_1FRNTR 2! ID 1+P1_2-144_7GRIMES%,CROCKET7% | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-144_7GRIMES%,CROCKET7% | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103445 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 207.5 | 126.2 | 206 | 100.7 |  |  |  |  | 582 | G_1FRNTR 2! ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103446 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 201.2 | 126.2 | 206 | 97.7 |  |  |  |  | 583 | G_1FRNTR 2! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 2! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103447 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 224.8 | 181 | 243 | 92.5 |  |  |  |  | 584 | G_1FRNTR 2! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1FRNTR 2! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103448 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 206.5 | 91.6 | 206 | 100.2 |  |  |  |  | 584 | G_1FRNTR 2! ID 1+P1_2-184_4PORTER%,6PORTER% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1FRNTR 2! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103450 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 211 | 126.2 | 206 | 102.4 |  |  |  |  | 586 | G_1FRNTR 2! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1863_LEBROCK7!,TENRUSK7! | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103452 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 210.8 | 126.2 | 206 | 102.3 |  |  |  |  | 587 | G_1FRNTR 2! ID 1+P1_2-1865_TENRUSK7!,CROCKET7% | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1865_TENRUSK7!,CROCKET7% | G_1FRNTR 2! ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103457 | 23S | Approved | P3 | 38 | 334120 4NU LJON! 138 334211 4BDAYTON! 138 1 | LN | 97.6 | 4.7 | 99 | 98.6 |  |  |  |  | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334120 | 334211 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103460 | 23S | Approved | P3 | 38 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 260.3 | 80.1 | 243 | 107.1 |  |  |  |  | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
103462 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 234.2 | 181 | 243 | 96.4 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103463 | 23S | Approved | P3 | 38 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 185.8 | 64.1 | 206 | 90.2 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103464 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 215.2 | 91.6 | 206 | 104.5 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103465 | 23S | Approved | P3 | 38 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 686.9 | 326.5 | 753 | 91.2 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103466 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 682.5 | 310.8 | 749 | 91.1 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103467 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 682.5 | 310.8 | 753 | 90.6 |  |  |  |  | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103469 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 233.9 | 181 | 243 | 96.3 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103470 | 23S | Approved | P3 | 38 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 186.2 | 64.1 | 206 | 90.4 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103471 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 215.3 | 91.6 | 206 | 104.5 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103472 | 23S | Approved | P3 | 38 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 686.1 | 326.5 | 753 | 91.1 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103473 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 683.6 | 310.8 | 749 | 91.3 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103474 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 683.6 | 310.8 | 753 | 90.8 |  |  |  |  | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103475 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 220.8 | 181 | 243 | 90.9 |  |  |  |  | 601 | G_1G1LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-216_4RAYWOOD!,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103477 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.4 | 15.5 | 39 | 96 |  |  |  |  | 602 | G_1G1LEWIS! ID 1+P1_2-220_4STOWELL!,4BIGHILL! | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! | G_1G1LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
103478 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.2 | 18.3 | 39 | 103.1 |  |  |  |  | 602 | G_1G1LEWIS! ID 1+P1_2-220_4STOWELL!,4BIGHILL! | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
103480 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.9 | 15.5 | 39 | 97.1 |  |  |  |  | 603 | G_1G1LEWIS! ID 1+P1_2-223_4BIGHILL!,4MEMORIL! | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G1LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
103481 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.6 | 18.3 | 39 | 104.1 |  |  |  |  | 603 | G_1G1LEWIS! ID 1+P1_2-223_4BIGHILL!,4MEMORIL! | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
103482 | 23S | Approved | P3 | 38 | 334193 4HONEY! 138 334319 4CYPRESS% 138 1 | LN | 217.9 | 155.8 | 239 | 91.2 |  |  |  |  | 604 | G_1G1LEWIS! ID 1+P1_2-264_6CYPRESS%,6AMELIA! | 334193 | 334319 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-264_6CYPRESS%,6AMELIA! | G_1G1LEWIS! ID 1 |  | No violation: below Rate A
103484 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 563.6 | 331.2 | 561 | 100.5 |  |  |  |  | 607 | G_1G1LEWIS! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103490 | 23S | Approved | P3 | 38 | 334120 4NU LJON! 138 334211 4BDAYTON! 138 1 | LN | 97.4 | 4.7 | 99 | 98.4 |  |  |  |  | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334120 | 334211 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103493 | 23S | Approved | P3 | 38 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 259.5 | 80.1 | 243 | 106.8 |  |  |  |  | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
103495 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 233.9 | 181 | 243 | 96.3 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103496 | 23S | Approved | P3 | 38 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 185.4 | 64.1 | 206 | 90 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103497 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 214.9 | 91.6 | 206 | 104.3 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103498 | 23S | Approved | P3 | 38 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 684.9 | 326.5 | 753 | 91 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103499 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 680.5 | 310.8 | 749 | 90.9 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103500 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 680.5 | 310.8 | 753 | 90.4 |  |  |  |  | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103502 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 233.6 | 181 | 243 | 96.1 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103503 | 23S | Approved | P3 | 38 | 334117 4APOLLO 138 334118 4SPLENDR! 138 1 | LN | 185.9 | 64.1 | 206 | 90.2 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334117 | 334118 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103504 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 215 | 91.6 | 206 | 104.4 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103505 | 23S | Approved | P3 | 38 | 334204 6CHINA% 230 334240 6BATISTE% 230 1 | LN | 684.2 | 326.5 | 753 | 90.9 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334204 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103506 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334206 6JACINTO% 230 1 | LN | 681.6 | 310.8 | 749 | 91 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334205 | 334206 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103507 | 23S | Approved | P3 | 38 | 334205 6CHJC_SER 230 334240 6BATISTE% 230 1 | LN | 681.6 | 310.8 | 753 | 90.5 |  |  |  |  | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334205 | 334240 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103508 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 220.4 | 181 | 243 | 90.7 |  |  |  |  | 622 | G_1G2LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-216_4RAYWOOD!,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103509 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.4 | 15.5 | 39 | 95.9 |  |  |  |  | 623 | G_1G2LEWIS! ID 1+P1_2-220_4STOWELL!,4BIGHILL! | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! | G_1G2LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
103510 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.1 | 18.3 | 39 | 102.9 |  |  |  |  | 623 | G_1G2LEWIS! ID 1+P1_2-220_4STOWELL!,4BIGHILL! | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-220_4STOWELL!,4BIGHILL! | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
103511 | 23S | Approved | P3 | 38 | 334269 2PANSY! 69.0 334270 2LOVELSL 69.0 1 | LN | 37.8 | 15.5 | 39 | 97 |  |  |  |  | 624 | G_1G2LEWIS! ID 1+P1_2-223_4BIGHILL!,4MEMORIL! | 334269 | 334270 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G2LEWIS! ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-010-01-CP | 2013-12-01 | Upgrade Lovells Lake-Pansy 69 kV to 100 deg design
103512 | 23S | Approved | P3 | 38 | 334270 2LOVELSL 69.0 334271 2TEX-HIL 69.0 1 | LN | 40.6 | 18.3 | 39 | 104 |  |  |  |  | 624 | G_1G2LEWIS! ID 1+P1_2-223_4BIGHILL!,4MEMORIL! | 334270 | 334271 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-010-02-CP | 2013-12-01 | Upgrade Lovells Lake-Texas Hillebrandt 69 kV to 100 deg design
103513 | 23S | Approved | P3 | 38 | 334193 4HONEY! 138 334319 4CYPRESS% 138 1 | LN | 217.5 | 155.8 | 239 | 91 |  |  |  |  | 625 | G_1G2LEWIS! ID 1+P1_2-264_6CYPRESS%,6AMELIA! | 334193 | 334319 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-264_6CYPRESS%,6AMELIA! | G_1G2LEWIS! ID 1 |  | No violation: below Rate A
103515 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 563.5 | 331.2 | 561 | 100.4 |  |  |  |  | 628 | G_1G2LEWIS! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103518 | 23S | Approved | P3 | 38 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 260 | 90.8 | 220 | 118.2 |  |  |  |  | 642 | G_1EXXONGT1! ID 1+P1_2-291_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-291_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
103519 | 23S | Approved | P3 | 38 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 265.4 | 107.2 | 220 | 120.6 |  |  |  |  | 643 | G_1EXXONGT1! ID 1+P1_2-292_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-292_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
103520 | 23S | Approved | P3 | 38 | 334396 47NECHES! 138 334398 4HAMPTON 138 1 | LN | 263.2 | 155.2 | 287 | 91.7 |  |  |  |  | 644 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334396 | 334398 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
103521 | 23S | Approved | P3 | 38 | 334398 4HAMPTON 138 334430 4SABINE! 138 1 | LN | 275.3 | 160.5 | 287 | 95.9 |  |  |  |  | 644 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334398 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
103522 | 23S | Approved | P3 | 38 | 334396 47NECHES! 138 334397 4OILLA 138 1 | LN | 265.8 | 154.3 | 282 | 94.3 |  |  |  |  | 645 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334396 | 334397 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
103523 | 23S | Approved | P3 | 38 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 273.9 | 159.2 | 282 | 97.1 |  |  |  |  | 645 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
103524 | 23S | Approved | P3 | 38 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 198.5 | 107.2 | 220 | 90.2 |  |  |  |  | 647 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 | Project Horizon | No violation: below Rate A | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
103525 | 23S | Approved | P3 | 38 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 205.3 | 107.2 | 220 | 93.3 |  |  |  |  | 648 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 | Project Horizon | No violation: below Rate A | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
103527 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 567 | 331.2 | 561 | 101.1 |  |  |  |  | 654 | G_1G3SABIN! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1G3SABIN! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103532 | 23S | Approved | P3 | 38 | 334326 6CYPRESS% 230 334328 6BEVIL 230 1 | LN | 687.9 | 393.8 | 685 | 100.4 |  |  |  |  | 659 | G_1G4SABIN! ID 1+P1_2-261_8HARTBRG%,6HARTBRG! | 334326 | 334328 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-261_8HARTBRG%,6HARTBRG! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
103533 | 23S | Approved | P3 | 38 | 334327 6AMELIA! 230 334328 6BEVIL 230 1 | LN | 651.5 | 367.6 | 685 | 95.1 |  |  |  |  | 659 | G_1G4SABIN! ID 1+P1_2-261_8HARTBRG%,6HARTBRG! | 334327 | 334328 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-261_8HARTBRG%,6HARTBRG! | G_1G4SABIN! ID 1 | Project Proposed | No violation: below Rate A | 11-ETI-023-CP | 2017-06-01 | Construct new Chisholm Road 230 kV substation; Construct new line from Hartburg to Chisholm Road; In
103536 | 23S | Approved | P3 | 38 | 334413 4PNEC BK! 138 334430 4SABINE! 138 1 | LN | 295.4 | 180.5 | 287 | 102.9 |  |  |  |  | 661 | G_1G4SABIN! ID 1+P1_2-303_4PNEC BK!,4SABINE! | 334413 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-303_4PNEC BK!,4SABINE! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-002-CP | 2017-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (Line 515)
103538 | 23S | Approved | P3 | 38 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 302.2 | 172.3 | 288 | 104.9 |  |  |  |  | 662 | G_1G4SABIN! ID 1+P1_2-304_4PNEC BK!,4SABINE! | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-304_4PNEC BK!,4SABINE! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
103542 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 569.5 | 331.2 | 561 | 101.5 |  |  |  |  | 665 | G_1G4SABIN! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1G4SABIN! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103543 | 23S | Approved | P3 | 38 | 334414 4LINDE 138 334430 4SABINE! 138 1 | LN | 292.7 | 172.3 | 288 | 101.6 |  |  |  |  | 666 | G_1G5SABIN! ID 1+P1_2-304_4PNEC BK!,4SABINE! | 334414 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-304_4PNEC BK!,4SABINE! | G_1G5SABIN! ID 1 | Project Proposed |  | 11-ETI-038-CP | 2018-06-01 | Reconductor Sabine-Port Neches Bulk 138 kV (via Linde Line 516)
103544 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 567.7 | 331.2 | 561 | 101.2 |  |  |  |  | 669 | G_1G5SABIN! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1G5SABIN! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103545 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.4 | 331.2 | 561 | 101.3 |  |  |  |  | 686 | G_1NELSON_G4! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1NELSON_G4! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103546 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 569.5 | 331.2 | 561 | 101.5 |  |  |  |  | 689 | G_1NELSON_G6! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1NELSON_G6! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103547 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 693 | G_6DOW_COGEN% ID 2+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 2 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103548 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.7 | 48 | 100 | 99.7 |  |  |  |  | 693 | G_6DOW_COGEN% ID 2+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 2 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103549 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.1 | 48.6 | 100 | 101.1 |  |  |  |  | 694 | G_6DOW_COGEN% ID 3+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 3 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103550 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.8 | 48 | 100 | 99.8 |  |  |  |  | 694 | G_6DOW_COGEN% ID 3+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 3 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103551 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 695 | G_6DOW_COGEN% ID 4+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103552 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.7 | 48 | 100 | 99.7 |  |  |  |  | 695 | G_6DOW_COGEN% ID 4+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 4 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103553 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 696 | G_6DOW_COGEN% ID 5+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103554 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.7 | 48 | 100 | 99.7 |  |  |  |  | 696 | G_6DOW_COGEN% ID 5+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_6DOW_COGEN% ID 5 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103555 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.5 | 48.6 | 100 | 101.5 |  |  |  |  | 698 | G_1CARVLE_C1! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_C1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103556 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.2 | 48 | 100 | 100.2 |  |  |  |  | 698 | G_1CARVLE_C1! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_C1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103557 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.5 | 48.6 | 100 | 101.5 |  |  |  |  | 700 | G_1CARVLE_C2! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103558 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.2 | 48 | 100 | 100.2 |  |  |  |  | 700 | G_1CARVLE_C2! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103559 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.5 | 48.6 | 100 | 101.5 |  |  |  |  | 702 | G_1CARVLE_S1! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_S1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103560 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.1 | 48 | 100 | 100.1 |  |  |  |  | 702 | G_1CARVLE_S1! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1CARVLE_S1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103561 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190.1 | 165.4 | 200 | 95.1 |  |  |  |  | 706 | G_1WILL_GL_G1! ID 1+P1_2-768_4PORT_HUD!,6PORT_HUD% | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-768_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103562 | 23S | Approved | P3 | 38 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 302.9 | 170.4 | 300 | 101 |  |  |  |  | 706 | G_1WILL_GL_G1! ID 1+P1_2-768_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-768_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103563 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 189.7 | 165.4 | 200 | 94.8 |  |  |  |  | 707 | G_1WILL_GL_G1! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103564 | 23S | Approved | P3 | 38 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 303.8 | 172.1 | 300 | 101.3 |  |  |  |  | 707 | G_1WILL_GL_G1! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103565 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 191 | 165.4 | 200 | 95.5 |  |  |  |  | 710 | G_1WILL_GL_G2! ID 1+P1_2-768_4PORT_HUD!,6PORT_HUD% | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-768_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G2! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103566 | 23S | Approved | P3 | 38 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 2 | TR | 306.8 | 170.4 | 300 | 102.3 |  |  |  |  | 710 | G_1WILL_GL_G2! ID 1+P1_2-768_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 2 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-768_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103567 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 190.6 | 165.4 | 200 | 95.3 |  |  |  |  | 711 | G_1WILL_GL_G2! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G2! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103568 | 23S | Approved | P3 | 38 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 307.7 | 172.1 | 300 | 102.6 |  |  |  |  | 711 | G_1WILL_GL_G2! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103569 | 23S | Approved | P3 | 38 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 595.6 | 341.2 | 593 | 100.4 |  |  |  |  | 712 | G_1WILL_GL_G2! ID 1+P1_2-772_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-772_6PORT_HUD%,6FANCY_PT% | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
103570 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 185.8 | 128 | 200 | 92.9 |  |  |  |  | 714 | G_1WILL_GL_G4! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1WILL_GL_G4! ID 1 |  | Model: does not represent split configuration
103571 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 203.7 | 140.4 | 200 | 101.8 |  |  |  |  | 714 | G_1WILL_GL_G4! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1WILL_GL_G4! ID 1 |  | Model: does not represent split configuration
103572 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 102.6 | 48.6 | 100 | 102.6 |  |  |  |  | 715 | G_1WILL_GL_G4! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103573 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 101.2 | 48 | 100 | 101.2 |  |  |  |  | 715 | G_1WILL_GL_G4! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103574 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 563.6 | 331.2 | 561 | 100.5 |  |  |  |  | 716 | G_1WILL_GL_G4! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103575 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.2 | 48.6 | 100 | 101.2 |  |  |  |  | 718 | G_1ENCO_G1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1ENCO_G1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103576 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.9 | 48 | 100 | 99.9 |  |  |  |  | 718 | G_1ENCO_G1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1ENCO_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103577 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.4 | 48.6 | 100 | 101.4 |  |  |  |  | 720 | G_1LA_STA_U5A! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103578 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.1 | 48 | 100 | 100.1 |  |  |  |  | 720 | G_1LA_STA_U5A! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103579 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 722 | G_1LA_STA_U4A! ID 1+1008 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103580 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.6 | 48 | 100 | 99.6 |  |  |  |  | 722 | G_1LA_STA_U4A! ID 1+1008 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1LA_STA_U4A! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103581 | 23S | Approved | P3 | 38 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1131.6 | 294.8 | 1069 | 105.9 |  |  |  |  | 724 | G_1RVR_BND_G1! ID 1+P1_2-591_8WEBRE%,8BYULABUTTE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-591_8WEBRE%,8BYULABUTTE% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
103582 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 184.1 | 128 | 200 | 92 |  |  |  |  | 725 | G_1RVR_BND_G1! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1RVR_BND_G1! ID 1 |  | Model: does not represent split configuration
103583 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 201.4 | 140.4 | 200 | 100.7 |  |  |  |  | 725 | G_1RVR_BND_G1! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1RVR_BND_G1! ID 1 |  | Model: does not represent split configuration
103584 | 23S | Approved | P3 | 38 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1255.4 | 294.8 | 1069 | 117.4 |  |  |  |  | 726 | G_1RVR_BND_G1! ID 1+P1_2-751_6COLY%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-751_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
103585 | 23S | Approved | P3 | 38 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1323.1 | 857.2 | 1186 | 111.6 |  |  |  |  | 727 | G_1RVR_BND_G1! ID 1+P1_2-774_6FANCY_PT%,8FANCY_PT% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
103586 | 23S | Approved | P3 | 38 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 305.1 | 271.2 | 335 | 91.1 |  |  |  |  | 727 | G_1RVR_BND_G1! ID 1+P1_2-774_6FANCY_PT%,8FANCY_PT% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-774_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103587 | 23S | Approved | P3 | 38 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1290 | 294.8 | 1069 | 120.7 |  |  |  |  | 728 | G_1RVR_BND_G1! ID 1+P1_2-776_8MCKNIGHT%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-776_8MCKNIGHT%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
103588 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 577.6 | 331.2 | 561 | 103 |  |  |  |  | 731 | G_1RVR_BND_G1! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103589 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 240.9 | 193.7 | 239 | 100.8 |  |  |  |  | 732 | G_1RVR_BND_G1! ID 1+1545 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_1RVR_BND_G1! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103590 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.5 | 48.6 | 100 | 101.5 |  |  |  |  | 734 | G_1WAT U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103591 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.2 | 48 | 100 | 100.2 |  |  |  |  | 734 | G_1WAT U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103592 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 564.6 | 331.2 | 561 | 100.6 |  |  |  |  | 735 | G_1WAT U1! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WAT U1! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103593 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.5 | 48.6 | 100 | 101.5 |  |  |  |  | 737 | G_1WAT U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103594 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.2 | 48 | 100 | 100.2 |  |  |  |  | 737 | G_1WAT U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103595 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 564.6 | 331.2 | 561 | 100.6 |  |  |  |  | 738 | G_1WAT U2! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WAT U2! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103596 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 2 | TR | 185.3 | 128 | 200 | 92.6 |  |  |  |  | 740 | G_1WAT U3! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 2 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1WAT U3! ID 1 |  | Model: does not represent split configuration
103597 | 23S | Approved | P3 | 38 | 335713 2COLY! 69.0 335771 6COLY% 230 3 | TR | 202.8 | 140.4 | 200 | 101.4 |  |  |  |  | 740 | G_1WAT U3! ID 1+P1_2-727_2COLY!,6COLY% | 335713 | 335771 | 3 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-727_2COLY!,6COLY% | G_1WAT U3! ID 1 |  | Model: does not represent split configuration
103598 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 103.7 | 48.6 | 100 | 103.7 |  |  |  |  | 741 | G_1WAT U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103599 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 102.3 | 48 | 100 | 102.3 |  |  |  |  | 741 | G_1WAT U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103600 | 23S | Approved | P3 | 38 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 2 | LN | 599.7 | 334.1 | 593 | 101.1 |  |  |  |  | 742 | G_1WAT U3! ID 1+P1_2-771_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 2 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-771_6PORT_HUD%,6FANCY_PT% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
103601 | 23S | Approved | P3 | 38 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 603.3 | 341.2 | 593 | 101.7 |  |  |  |  | 743 | G_1WAT U3! ID 1+P1_2-772_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-772_6PORT_HUD%,6FANCY_PT% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
103602 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 580.5 | 331.2 | 561 | 103.5 |  |  |  |  | 745 | G_1WAT U3! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103603 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 241.7 | 193.7 | 239 | 101.1 |  |  |  |  | 746 | G_1WAT U3! ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_1WAT U3! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103604 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.4 | 48.6 | 100 | 101.4 |  |  |  |  | 748 | G_1SOXY U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103605 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100 | 48 | 100 | 100 |  |  |  |  | 748 | G_1SOXY U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103606 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 102 | 48.6 | 100 | 102 |  |  |  |  | 754 | G_1GYP U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103607 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.6 | 48 | 100 | 100.6 |  |  |  |  | 754 | G_1GYP U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103608 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 567.7 | 331.2 | 561 | 101.2 |  |  |  |  | 756 | G_1GYP U3! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103609 | 23S | Approved | P3 | 38 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 107.3 | 80.2 | 115 | 93.3 |  |  |  |  | 757 | G_1GYP U3! ID 1+P1_2-1175_3PLANTATION! | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175_3PLANTATION! | G_1GYP U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103610 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.2 | 48.6 | 100 | 101.2 |  |  |  |  | 759 | G_1GYP U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U1! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103611 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.9 | 48 | 100 | 99.9 |  |  |  |  | 759 | G_1GYP U1! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103612 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.6 | 48.6 | 100 | 101.6 |  |  |  |  | 761 | G_1GYP U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103613 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.3 | 48 | 100 | 100.3 |  |  |  |  | 761 | G_1GYP U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103614 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 763 | G_1GYP U2! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1GYP U2! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103615 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 765 | G_1NMIL6 CT1 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103616 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.7 | 48 | 100 | 99.7 |  |  |  |  | 765 | G_1NMIL6 CT1 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 CT1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103617 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101 | 48.6 | 100 | 101 |  |  |  |  | 767 | G_1NMIL6 CT2 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103618 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.7 | 48 | 100 | 99.7 |  |  |  |  | 767 | G_1NMIL6 CT2 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 CT2 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103619 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.1 | 48.6 | 100 | 101.1 |  |  |  |  | 769 | G_1NMIL6 ST1 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103620 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.8 | 48 | 100 | 99.8 |  |  |  |  | 769 | G_1NMIL6 ST1 ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL6 ST1 ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103621 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 102.3 | 48.6 | 100 | 102.3 |  |  |  |  | 771 | G_1NMIL U4! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103622 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 101 | 48 | 100 | 101 |  |  |  |  | 771 | G_1NMIL U4! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103623 | 23S | Approved | P3 | 38 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 596.1 | 341.2 | 593 | 100.5 |  |  |  |  | 772 | G_1NMIL U4! ID 1+P1_2-772_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-772_6PORT_HUD%,6FANCY_PT% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
103624 | 23S | Approved | P3 | 38 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 116.1 | 78 | 115 | 100.9 |  |  |  |  | 773 | G_1NMIL U4! ID 1+P1_2-836_3BARATA!,39MILE% | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-836_3BARATA!,39MILE% | G_1NMIL U4! ID 1 | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
103625 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 571.1 | 331.2 | 561 | 101.8 |  |  |  |  | 775 | G_1NMIL U4! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103626 | 23S | Approved | P3 | 38 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 108.5 | 80.2 | 115 | 94.4 |  |  |  |  | 776 | G_1NMIL U4! ID 1+P1_2-1175_3PLANTATION! | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175_3PLANTATION! | G_1NMIL U4! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103627 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 102.3 | 48.6 | 100 | 102.3 |  |  |  |  | 778 | G_1NMIL U5! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103628 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 101 | 48 | 100 | 101 |  |  |  |  | 778 | G_1NMIL U5! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103629 | 23S | Approved | P3 | 38 | 335815 6PORT_HUD% 230 335825 6FANCY_PT% 230 1 | LN | 596.4 | 341.2 | 593 | 100.6 |  |  |  |  | 779 | G_1NMIL U5! ID 1+P1_2-772_6PORT_HUD%,6FANCY_PT% | 335815 | 335825 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-772_6PORT_HUD%,6FANCY_PT% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EGL-017-CP | 2017-06-02 | Construct Crown Zellerbach Tap 230-138 kV SS on Fancy Point-Waterloo 230 kV and CZ-Starhill 138 kV
103630 | 23S | Approved | P3 | 38 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 116.3 | 78 | 115 | 101.1 |  |  |  |  | 780 | G_1NMIL U5! ID 1+P1_2-836_3BARATA!,39MILE% | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-836_3BARATA!,39MILE% | G_1NMIL U5! ID 1 | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
103631 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 571.4 | 331.2 | 561 | 101.8 |  |  |  |  | 782 | G_1NMIL U5! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103632 | 23S | Approved | P3 | 38 | 336788 3PORTGIBSON! 115 336790 3S.VICKSBURG 115 1 | LN | 146 | 103.7 | 161 | 90.7 |  |  |  |  | 783 | G_1NMIL U5! ID 1+P1_2-1175_3PLANTATION! | 336788 | 336790 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1175_3PLANTATION! | G_1NMIL U5! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103633 | 23S | Approved | P3 | 38 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 108 | 80.2 | 115 | 93.9 |  |  |  |  | 783 | G_1NMIL U5! ID 1+P1_2-1175_3PLANTATION! | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175_3PLANTATION! | G_1NMIL U5! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103634 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.1 | 48.6 | 100 | 101.1 |  |  |  |  | 786 | G_1MICH U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1MICH U2! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103635 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 99.8 | 48 | 100 | 99.8 |  |  |  |  | 786 | G_1MICH U2! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1MICH U2! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103636 | 23S | Approved | P3 | 38 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 233.2 | 140.4 | 229 | 101.8 |  |  |  |  | 787 | G_1MICH U2! ID 1+P1_2-951_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! | G_1MICH U2! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
103637 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.8 | 48.6 | 100 | 101.8 |  |  |  |  | 789 | G_1MICH U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1MICH U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103638 | 23S | Approved | P3 | 38 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.4 | 48 | 100 | 100.4 |  |  |  |  | 789 | G_1MICH U3! ID 1+P1_2-760_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1MICH U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103639 | 23S | Approved | P3 | 38 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | LN | 115.6 | 78 | 115 | 100.5 |  |  |  |  | 791 | G_1MICH U3! ID 1+P1_2-836_3BARATA!,39MILE% | 336037 | 336080 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-836_3BARATA!,39MILE% | G_1MICH U3! ID 1 | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
103640 | 23S | Approved | P3 | 38 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 240.7 | 140.4 | 229 | 105.1 |  |  |  |  | 792 | G_1MICH U3! ID 1+P1_2-951_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! | G_1MICH U3! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
103641 | 23S | Approved | P3 | 38 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 234.6 | 165.8 | 229 | 102.4 |  |  |  |  | 793 | G_1MICH U3! ID 1+P1_2-952_39MILE%,3GRETNA! | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-952_39MILE%,3GRETNA! | G_1MICH U3! ID 1 | Project Horizon |  | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
103642 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 567.6 | 331.2 | 561 | 101.2 |  |  |  |  | 795 | G_1MICH U3! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103643 | 23S | Approved | P3 | 38 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 107.4 | 80.2 | 115 | 93.4 |  |  |  |  | 796 | G_1MICH U3! ID 1+P1_2-1175_3PLANTATION! | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175_3PLANTATION! | G_1MICH U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103644 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.3 | 331.2 | 561 | 101.3 |  |  |  |  | 801 | G_1B.WLSN U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1B.WLSN U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103645 | 23S | Approved | P3 | 38 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 630 | 343.6 | 600 | 105 |  |  |  |  | 804 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
103646 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 590.5 | 331.2 | 561 | 105.3 |  |  |  |  | 805 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103647 | 23S | Approved | P3 | 38 | 337016 3PICKENS! 115 337018 3MIDWAY MS+ 115 1 | LN | 109.6 | 45.5 | 108 | 101.5 |  |  |  |  | 805 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337016 | 337018 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
103648 | 23S | Approved | P3 | 38 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 109 | 57.3 | 108 | 100.9 |  |  |  |  | 805 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
103649 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 590.9 | 331.2 | 561 | 105.3 |  |  |  |  | 806 | G_1GGNS U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103650 | 23S | Approved | P3 | 38 | 337162 6FREEPORT% 230 337163 6TWINKLTOWN! 230 1 | LN | 479.7 | 175.7 | 462 | 103.8 |  |  |  |  | 807 | G_1GGNS U1 ID 1+P1_2-1159_6FREEPORT%,6HORN LAKE% | 337162 | 337163 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1159_6FREEPORT%,6HORN LAKE% | G_1GGNS U1 ID 1
103651 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 242.4 | 193.7 | 239 | 101.4 |  |  |  |  | 809 | G_1GGNS U1 ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_1GGNS U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103652 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.8 | 331.2 | 561 | 101.4 |  |  |  |  | 813 | G_1B.WLSN U2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1B.WLSN U2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103653 | 23S | Approved | P3 | 38 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 104.5 | 80.2 | 115 | 90.9 |  |  |  |  | 814 | G_1B.WLSN U2 ID 1+P1_2-1175_3PLANTATION! | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1175_3PLANTATION! | G_1B.WLSN U2 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
103654 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 578.5 | 331.2 | 561 | 103.1 |  |  |  |  | 816 | G_1HINDS G2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1HINDS G2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103655 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 578.5 | 331.2 | 561 | 103.1 |  |  |  |  | 818 | G_1HINDS G1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1HINDS G1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103656 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 572.7 | 331.2 | 561 | 102.1 |  |  |  |  | 820 | G_1HINDS S1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1HINDS S1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103657 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 564 | 331.2 | 561 | 100.5 |  |  |  |  | 822 | G_1REX BRWN U4 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1REX BRWN U4 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103658 | 23S | Approved | P3 | 38 | 336800 3BXTRWILSON% 115 336960 3SE.VICKSBRG 115 1 | LN | 165.1 | 86.5 | 161 | 102.5 |  |  |  |  | 831 | G_1ANDRUS U1 ID 1+1279 | 336800 | 336960 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1031_3VICKSBURG!,3N.VICKSBRG! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EMI-002-CP | 2015-06-01 | Upgrade Baxter Wilson-S.E. Vicksburg 115 kV
103659 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 648.8 | 331.2 | 561 | 115.6 |  |  |  |  | 832 | G_1ANDRUS U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103660 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 1 | TR | 632.4 | 298.9 | 615 | 102.8 |  |  |  |  | 833 | G_1ANDRUS U1 ID 1+P1_2-1098_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 1 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1098_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103661 | 23S | Approved | P3 | 38 | 337162 6FREEPORT% 230 337163 6TWINKLTOWN! 230 1 | LN | 471.8 | 175.7 | 462 | 102.1 |  |  |  |  | 834 | G_1ANDRUS U1 ID 1+P1_2-1159_6FREEPORT%,6HORN LAKE% | 337162 | 337163 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1159_6FREEPORT%,6HORN LAKE% | G_1ANDRUS U1 ID 1
103662 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 583 | 331.2 | 561 | 103.9 |  |  |  |  | 836 | G_3GREENWOOD! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_3GREENWOOD! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103663 | 23S | Approved | P3 | 38 | 337023 3GREENWOOD+ 115 337054 3GREENWOOD! 115 1 | LN | 72.3 | 38.3 | 70 | 103.2 |  |  |  |  | 837 | G_3GREENWOOD! ID 1+P1_2-1100_6MCADAMS%,3ATTALA! | 337023 | 337054 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1100_6MCADAMS%,3ATTALA! | G_3GREENWOOD! ID 1
103664 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 563.3 | 331.2 | 561 | 100.4 |  |  |  |  | 839 | G_3CLRKD MUNI! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_3CLRKD MUNI! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103665 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 841 | G_1CROSSRDS G1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103666 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 843 | G_1CROSSRDS G2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103667 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 845 | G_1CROSSRDS G3 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103668 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.4 | 331.2 | 561 | 100.8 |  |  |  |  | 847 | G_1CROSSRDS G4 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103669 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 569.3 | 331.2 | 561 | 101.5 |  |  |  |  | 849 | G_1SLSBAU3 ID 5+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1SLSBAU3 ID 5 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103670 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 578.4 | 331.2 | 561 | 103.1 |  |  |  |  | 851 | G_1CLSBAU3 ID 6+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CLSBAU3 ID 6 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103671 | 23S | Approved | P3 | 38 | 337162 6FREEPORT% 230 337163 6TWINKLTOWN! 230 1 | LN | 469 | 175.7 | 462 | 101.5 |  |  |  |  | 852 | G_1CLSBAU3 ID 6+P1_2-1159_6FREEPORT%,6HORN LAKE% | 337162 | 337163 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1159_6FREEPORT%,6HORN LAKE% | G_1CLSBAU3 ID 6
103672 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 578.5 | 331.2 | 561 | 103.1 |  |  |  |  | 873 | G_1WHT BLUF U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WHT BLUF U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103673 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 166.8 | 123.8 | 159 | 104.9 |  |  |  |  | 874 | G_1WHT BLUF U1 ID 1+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1WHT BLUF U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103674 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 166.8 | 123.8 | 159 | 104.9 |  |  |  |  | 875 | G_1WHT BLUF U1 ID 1+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1WHT BLUF U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103675 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 579.3 | 331.2 | 561 | 103.3 |  |  |  |  | 878 | G_1WHT BLUF U2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1WHT BLUF U2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103676 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 167.1 | 123.8 | 159 | 105.1 |  |  |  |  | 879 | G_1WHT BLUF U2 ID 1+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1WHT BLUF U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103677 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 167.1 | 123.8 | 159 | 105.1 |  |  |  |  | 880 | G_1WHT BLUF U2 ID 1+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1WHT BLUF U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103678 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 248.6 | 193.7 | 239 | 104 |  |  |  |  | 882 | G_1DEGRAY U1 ID 1+1545 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_1DEGRAY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103679 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 241.3 | 193.7 | 239 | 100.9 |  |  |  |  | 883 | G_1DEGRAY U1 ID 1+P1_2-1326_3HS EHV-W!,8HS EHV% | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326_3HS EHV-W!,8HS EHV% | G_1DEGRAY U1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103680 | 23S | Approved | P3 | 38 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.4 | 547.5 | 598 | 91.4 |  |  |  |  | 883 | G_1DEGRAY U1 ID 1+P1_2-1326_3HS EHV-W!,8HS EHV% | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326_3HS EHV-W!,8HS EHV% | G_1DEGRAY U1 ID 1 |  | Facility: Radial
103681 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245 | 193.7 | 239 | 102.5 |  |  |  |  | 885 | G_1DEGRAY U2 ID 1+1545 | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_1DEGRAY U2 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103682 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 572.3 | 331.2 | 561 | 102 |  |  |  |  | 891 | G_1CATHRINE U4 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CATHRINE U4 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103683 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.5 | 331.2 | 561 | 100.8 |  |  |  |  | 897 | G_1DUKE HS S1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1DUKE HS S1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103684 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 578.9 | 331.2 | 561 | 103.2 |  |  |  |  | 902 | G_1ANO U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANO U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103685 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 170.6 | 123.8 | 159 | 107.3 |  |  |  |  | 903 | G_1ANO U1 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ANO U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103686 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 170.6 | 123.8 | 159 | 107.3 |  |  |  |  | 904 | G_1ANO U1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ANO U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103687 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 582.9 | 331.2 | 561 | 103.9 |  |  |  |  | 908 | G_1ANO U2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANO U2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103688 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 172.9 | 123.8 | 159 | 108.8 |  |  |  |  | 909 | G_1ANO U2 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ANO U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103689 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 172.9 | 123.8 | 159 | 108.8 |  |  |  |  | 910 | G_1ANO U2 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ANO U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103690 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.9 | 123.8 | 159 | 101.2 |  |  |  |  | 914 | G_1LYNCH U3 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1LYNCH U3 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103691 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.9 | 123.8 | 159 | 101.2 |  |  |  |  | 915 | G_1LYNCH U3 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1LYNCH U3 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103692 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 575.7 | 331.2 | 561 | 102.6 |  |  |  |  | 918 | G_1ISES U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ISES U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103693 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 164.4 | 123.8 | 159 | 103.4 |  |  |  |  | 919 | G_1ISES U1 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ISES U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103694 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 164.4 | 123.8 | 159 | 103.4 |  |  |  |  | 920 | G_1ISES U1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ISES U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103695 | 23S | Approved | P3 | 38 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 342.1 | 202.2 | 266 | 128.6 |  |  |  |  | 921 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
103696 | 23S | Approved | P3 | 38 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 299.9 | 162.4 | 266 | 112.7 |  |  |  |  | 921 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
103697 | 23S | Approved | P3 | 38 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 487.6 | 276.8 | 450 | 108.3 |  |  |  |  | 921 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Horizon |  | 14-EAI-010-HZ | 2020-06-01 | West Memphis - Add 2nd 500-161 kV auto
103698 | 23S | Approved | P3 | 38 | 338161 5W.MEMPHIS! 161 338412 5WM LEHI-W 161 1 | LN | 205.6 | 117.6 | 223 | 92.2 |  |  |  |  | 921 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338412 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 |  | No violation: below Rate A
103699 | 23S | Approved | P3 | 38 | 338229 3T.E.P/S-8 115 338230 3JIM HILL! 115 1 | LN | 63.3 | 47.9 | 70 | 90.5 |  |  |  |  | 921 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338229 | 338230 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Horizon | No violation: below Rate A | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
103700 | 23S | Approved | P3 | 38 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 266.8 | 202.2 | 266 | 100.3 |  |  |  |  | 922 | G_1ISES U1 ID 1+P1_2-1487_5ISES-1!,5RUTHERFORD! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1487_5ISES-1!,5RUTHERFORD! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
103701 | 23S | Approved | P3 | 38 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 245.6 | 118.8 | 223 | 110.1 |  |  |  |  | 923 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1
103702 | 23S | Approved | P3 | 38 | 338413 5WM LEHI-E 161 338414 5WM POLK AVE 161 1 | LN | 208 | 81.6 | 223 | 93.3 |  |  |  |  | 923 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338413 | 338414 | 1 |  | 161 | 161 | 334 | WMU | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1 |  | No violation: below Rate A
103703 | 23S | Approved | P3 | 38 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 248.1 | 202.2 | 266 | 93.3 |  |  |  |  | 924 | G_1ISES U1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
103704 | 23S | Approved | P3 | 38 | 338142 5ISES-1! 161 338144 8ISES-XF 500 1 | TR | 410.8 | 108.5 | 425 | 96.7 |  |  |  |  | 924 | G_1ISES U1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338142 | 338144 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1ISES U1 ID 1 |  | No violation: below Rate A
103705 | 23S | Approved | P3 | 38 | 338144 8ISES-XF 500 338145 8ISES% 500 1 | LN | 826.6 | 217.6 | 850 | 97.2 |  |  |  |  | 924 | G_1ISES U1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338144 | 338145 | 1 |  | 500 | 500 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1ISES U1 ID 1 |  | No violation: below Rate A
103706 | 23S | Approved | P3 | 38 | 338144 8ISES-XF 500 338152 5ISES-2! 161 2 | TR | 415.7 | 109.8 | 425 | 97.8 |  |  |  |  | 924 | G_1ISES U1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338144 | 338152 | 2 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1ISES U1 ID 1 |  | No violation: below Rate A
103707 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 575 | 331.2 | 561 | 102.5 |  |  |  |  | 929 | G_1ISES U2 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ISES U2 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103708 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 165.1 | 123.8 | 159 | 103.8 |  |  |  |  | 930 | G_1ISES U2 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ISES U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103709 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 165 | 123.8 | 159 | 103.8 |  |  |  |  | 931 | G_1ISES U2 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ISES U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103710 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.2 | 331.2 | 561 | 101.3 |  |  |  |  | 935 | G_1PLUM PT U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103711 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 161.1 | 123.8 | 159 | 101.3 |  |  |  |  | 936 | G_1PLUM PT U1 ID 1+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1PLUM PT U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103712 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 161.1 | 123.8 | 159 | 101.3 |  |  |  |  | 937 | G_1PLUM PT U1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1PLUM PT U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103713 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 135.5 | 108.5 | 148 | 91.6 |  |  |  |  | 938 | G_1PLUM PT U1 ID 1+1748 | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1PLUM PT U1 ID 1 |  | No violation: below Rate A
103714 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 144.2 | 115.6 | 160 | 90.1 |  |  |  |  | 938 | G_1PLUM PT U1 ID 1+1748 | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1PLUM PT U1 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103715 | 23S | Approved | P3 | 38 | 337530 3CAMDEN MAG! 115 337536 3SMACKOVER 115 1 | LN | 105.6 | 20.4 | 98 | 107.7 |  |  |  |  | 943 | G_1MCCLELAN U1 ID 1+1514 | 337530 | 337536 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1266_3MCNEIL!,3CAMDEN MAG! | G_1MCCLELAN U1 ID 1
103716 | 23S | Approved | P3 | 38 | 337516 3MCNEIL! 115 337518 3STEPHENS 115 1 | LN | 152 | 35.8 | 159 | 95.6 |  |  |  |  | 944 | G_1MCCLELAN U1 ID 1+1523 | 337516 | 337518 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 |  | No violation: below Rate A
103717 | 23S | Approved | P3 | 38 | 337516 3MCNEIL! 115 337519 3MAGNOLIA.W 115 1 | LN | 160 | 85.7 | 177 | 90.4 |  |  |  |  | 944 | G_1MCCLELAN U1 ID 1+1523 | 337516 | 337519 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 |  | No violation: below Rate A
103718 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568.5 | 331.2 | 561 | 101.3 |  |  |  |  | 964 | G_1CAL G1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1CAL G1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103719 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159.9 | 123.8 | 159 | 100.6 |  |  |  |  | 965 | G_1CAL G1 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1CAL G1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103720 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159.9 | 123.8 | 159 | 100.5 |  |  |  |  | 966 | G_1CAL G1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1CAL G1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103721 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 971 | G_1CUMBRL F1HL ID 1+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1CUMBRL F1HL ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103722 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 972 | G_1CUMBRL F1HL ID 1+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1CUMBRL F1HL ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103723 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 976 | G_1CUMBRL F1HL ID 2+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1CUMBRL F1HL ID 2 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103724 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 977 | G_1CUMBRL F1HL ID 2+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1CUMBRL F1HL ID 2 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103725 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 981 | G_1CUMBRL F2HL ID 1+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1CUMBRL F2HL ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103726 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 982 | G_1CUMBRL F2HL ID 1+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1CUMBRL F2HL ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103727 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 986 | G_1CUMBRL F2HL ID 2+1559 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1CUMBRL F2HL ID 2 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103728 | 23S | Approved | P3 | 38 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 159 | 123.8 | 159 | 100 |  |  |  |  | 987 | G_1CUMBRL F2HL ID 2+1596 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1CUMBRL F2HL ID 2 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
103729 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 572.4 | 331.2 | 561 | 102 |  |  |  |  | 993 | G_G1DOLHIL! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103730 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.2 | 193.7 | 239 | 102.2 |  |  |  |  | 994 | G_G1DOLHIL! ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_G1DOLHIL! ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103731 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 566.3 | 331.2 | 561 | 100.9 |  |  |  |  | 996 | G_G1NESBIT! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_G1NESBIT! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103732 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 568 | 331.2 | 561 | 101.3 |  |  |  |  | 998 | G_G2RODEMR! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_G2RODEMR! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103733 | 23S | Approved | P3 | 38 | 335782 2PORT_HUD_A!69.0 335815 6PORT_HUD% 230 1 | TR | 188.8 | 165.4 | 200 | 94.4 |  |  |  |  | 999 | G_G3MADISN! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335782 | 335815 | 1 |  | 230 | 69 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_G3MADISN! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103734 | 23S | Approved | P3 | 38 | 335805 4PORT_HUD! 138 335815 6PORT_HUD% 230 1 | TR | 301.2 | 172.1 | 300 | 100.4 |  |  |  |  | 999 | G_G3MADISN! ID 1+P1_2-769_4PORT_HUD!,6PORT_HUD% | 335805 | 335815 | 1 |  | 230 | 138 | 351 | EES | 351 | EES | P1_2-769_4PORT_HUD!,6PORT_HUD% | G_G3MADISN! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
103735 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 570.3 | 331.2 | 561 | 101.7 |  |  |  |  | 1001 | G_G3MADISN! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_G3MADISN! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103736 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 564.8 | 331.2 | 561 | 100.7 |  |  |  |  | 1004 | G_G3TECHE! ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_G3TECHE! ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103737 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.3 | 65 | 115 | 97.7 |  |  |  |  | 1005 | G_G3TECHE! ID 1+2143 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103738 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 132.9 | 65 | 115 | 115.6 |  |  |  |  | 1016 | G_HARGIS1 ID 1+2143 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103739 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 90.3 | 56.8 | 95 | 95.1 |  |  |  |  | 1016 | G_HARGIS1 ID 1+2143 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: below Rate A
103740 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 132.9 | 65 | 115 | 115.6 |  |  |  |  | 1018 | G_HARGIS2 ID 1+2143 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103741 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 90.3 | 56.8 | 95 | 95.1 |  |  |  |  | 1018 | G_HARGIS2 ID 1+2143 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: below Rate A
103742 | 23S | Approved | P3 | 38 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.4 | 65 | 115 | 97.7 |  |  |  |  | 1020 | G_BONIN2 ID 1+2143 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
103743 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.6 | 108.5 | 148 | 92.3 |  |  |  |  | 1025 | G_JBOGA&B1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 1 |  | No violation: below Rate A
103744 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145.4 | 115.6 | 160 | 90.9 |  |  |  |  | 1025 | G_JBOGA&B1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103745 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.6 | 108.5 | 148 | 92.3 |  |  |  |  | 1026 | G_JBOGA&B1 ID 2+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 2 |  | No violation: below Rate A
103746 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145.4 | 115.6 | 160 | 90.9 |  |  |  |  | 1026 | G_JBOGA&B1 ID 2+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 2 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103747 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.9 | 108.5 | 148 | 92.5 |  |  |  |  | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 |  | No violation: below Rate A
103748 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145.8 | 115.6 | 160 | 91.1 |  |  |  |  | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103749 | 23S | Approved | P3 | 38 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 149.7 | 85.8 | 148 | 101.2 |  |  |  |  | 1030 | G_JBOGENC1 ID C+P1_2-1496_5NEWPORT!,5JONESBORO! | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496_5NEWPORT!,5JONESBORO! | G_JBOGENC1 ID C | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
103750 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 137.4 | 108.5 | 148 | 92.8 |  |  |  |  | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C |  | No violation: below Rate A
103751 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 146.2 | 115.6 | 160 | 91.4 |  |  |  |  | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103752 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.3 | 108.5 | 148 | 92.1 |  |  |  |  | 1033 | G_GF #1 1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_GF #1 1 ID 1 |  | No violation: below Rate A
103753 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145 | 115.6 | 160 | 90.6 |  |  |  |  | 1033 | G_GF #1 1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_GF #1 1 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103754 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 136.3 | 108.5 | 148 | 92.1 |  |  |  |  | 1035 | G_GF #2 2 ID 2+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_GF #2 2 ID 2 |  | No violation: below Rate A
103755 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 145 | 115.6 | 160 | 90.6 |  |  |  |  | 1035 | G_GF #2 2 ID 2+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_GF #2 2 ID 2 | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103756 | 23S | Approved | P3 | 38 | 338169 5TRUMANN 161 338707 5TRUMANN.W# 161 1 | LN | 150.2 | 85.8 | 148 | 101.5 |  |  |  |  | 1038 | G_JBOGENE1 ID E+P1_2-1496_5NEWPORT!,5JONESBORO! | 338169 | 338707 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1496_5NEWPORT!,5JONESBORO! | G_JBOGENE1 ID E | Project Horizon |  | 11-EAI-021-HZ | 2021-06-01 | Trumann-Trumann West- Upgrade 161 kV Line
103757 | 23S | Approved | P3 | 38 | 338022 5MOSES% 161 338044 5MCCRORY 161 1 | LN | 137.8 | 108.5 | 148 | 93.1 |  |  |  |  | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338022 | 338044 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E |  | No violation: below Rate A
103758 | 23S | Approved | P3 | 38 | 338044 5MCCRORY 161 338879 5BAILEY#! 161 1 | LN | 146.7 | 115.6 | 160 | 91.7 |  |  |  |  | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338044 | 338879 | 1 |  | 161 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Approved | No violation: below Rate A | 14-EAI-002-CP | 2014-12-01 | Hot Springs Transmission Service: McCrory-Bailey: Upgrade line to 100C
103759 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.8 | 331.2 | 561 | 100.9 |  |  |  |  | 1067 | G_FLINTCR1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103760 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 207.2 | 126.2 | 206 | 100.6 |  |  |  |  | 1069 | G_PIRKEY 1 ID 1+P1_2-159_4LEWIS%,4CANEYCREEK! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-159_4LEWIS%,4CANEYCREEK! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103761 | 23S | Approved | P3 | 38 | 334099 4CONROE2! 138 334103 4PLANTAT 138 1 | LN | 246.3 | 80.1 | 243 | 101.4 |  |  |  |  | 1070 | G_PIRKEY 1 ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334099 | 334103 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-175_4OAKRIDG!,4PORTER% | G_PIRKEY 1 ID 1 | Project Complete | Model: Line rating should be updated to 478 MVA after approved project 11-ETI-036-CP | 11-ETI-036-CP | 2013-04-01 | Plantation to Conroe 138 kV line: Reconductor Line
103762 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.7 | 181 | 243 | 92.9 |  |  |  |  | 1071 | G_PIRKEY 1 ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_PIRKEY 1 ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103763 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 207.3 | 91.6 | 206 | 100.6 |  |  |  |  | 1071 | G_PIRKEY 1 ID 1+P1_2-184_4PORTER%,6PORTER% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_PIRKEY 1 ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103764 | 23S | Approved | P3 | 38 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 225.4 | 181 | 243 | 92.8 |  |  |  |  | 1072 | G_PIRKEY 1 ID 1+P1_2-203_6PORTER%,6CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_PIRKEY 1 ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
103765 | 23S | Approved | P3 | 38 | 334118 4SPLENDR! 138 334208 4JACINTO% 138 1 | LN | 207 | 91.6 | 206 | 100.5 |  |  |  |  | 1072 | G_PIRKEY 1 ID 1+P1_2-203_6PORTER%,6CHINA% | 334118 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_PIRKEY 1 ID 1 | Project Proposed |  | 11-ETI-039-CP | 2015-06-01 | Upgrade Jacinto-Splendora 138 kV
103766 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 572 | 331.2 | 561 | 102 |  |  |  |  | 1075 | G_PIRKEY 1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103767 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 245.7 | 193.7 | 239 | 102.8 |  |  |  |  | 1076 | G_PIRKEY 1 ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_PIRKEY 1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103768 | 23S | Approved | P3 | 38 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.7 | 156.4 | 700 | 93.2 |  |  |  |  | 1077 | G_PIRKEY 1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
103769 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 230 | 71.8 | 204 | 112.8 |  |  |  |  | 1077 | G_PIRKEY 1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
103770 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 211.4 | 48.4 | 188 | 112.4 |  |  |  |  | 1077 | G_PIRKEY 1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
103771 | 23S | Approved | P3 | 38 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | LN | 186.6 | 126.2 | 206 | 90.6 |  |  |  |  | 1078 | G_PIRKEY 1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 334072 | 334073 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1863_LEBROCK7!,TENRUSK7! | G_PIRKEY 1 ID 1 | Project Proposed | No violation: below Rate A | 13-ETI-011-CP | 2014-06-01 | Reconductor Lewis Creek-Egypt 138 kV
103772 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 569.1 | 331.2 | 561 | 101.4 |  |  |  |  | 1081 | G_WELSH2-1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_WELSH2-1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103773 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.3 | 193.7 | 239 | 102.2 |  |  |  |  | 1082 | G_WELSH2-1 ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_WELSH2-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103774 | 23S | Approved | P3 | 38 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.1 | 156.4 | 700 | 93.2 |  |  |  |  | 1083 | G_WELSH2-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
103775 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 221.3 | 71.8 | 204 | 108.5 |  |  |  |  | 1083 | G_WELSH2-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
103776 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 202.1 | 48.4 | 188 | 107.5 |  |  |  |  | 1083 | G_WELSH2-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
103777 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 569.1 | 331.2 | 561 | 101.4 |  |  |  |  | 1087 | G_WELSH3-1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_WELSH3-1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103778 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 244.3 | 193.7 | 239 | 102.2 |  |  |  |  | 1088 | G_WELSH3-1 ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_WELSH3-1 ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103779 | 23S | Approved | P3 | 38 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.1 | 156.4 | 700 | 93.2 |  |  |  |  | 1089 | G_WELSH3-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
103780 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 221.3 | 71.8 | 204 | 108.5 |  |  |  |  | 1089 | G_WELSH3-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
103781 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 202.1 | 48.4 | 188 | 107.5 |  |  |  |  | 1089 | G_WELSH3-1 ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
103782 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 570.7 | 331.2 | 561 | 101.7 |  |  |  |  | 1093 | G_TURKCOAL ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_TURKCOAL ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103783 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 250.3 | 193.7 | 239 | 104.7 |  |  |  |  | 1094 | G_TURKCOAL ID 1+P1_2-1297_3WOODWARD-N!,3HS EHV-E! | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1297_3WOODWARD-N!,3HS EHV-E! | G_TURKCOAL ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103784 | 23S | Approved | P3 | 38 | 337685 3HS EHV-W! 115 337686 3ARKLAHOMA% 115 1 | LN | 241.8 | 193.7 | 239 | 101.2 |  |  |  |  | 1095 | G_TURKCOAL ID 1+P1_2-1326_3HS EHV-W!,8HS EHV% | 337685 | 337686 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326_3HS EHV-W!,8HS EHV% | G_TURKCOAL ID 1 | Project Approved; then close bus tie breakers at Hot Springs EHV |  | 13-EAI-008-CP | 2013-06-01 | Hot Springs EHV Substation: Replace two 115 kV autotransformer breakers
103785 | 23S | Approved | P3 | 38 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.4 | 547.5 | 598 | 91.4 |  |  |  |  | 1095 | G_TURKCOAL ID 1+P1_2-1326_3HS EHV-W!,8HS EHV% | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1326_3HS EHV-W!,8HS EHV% | G_TURKCOAL ID 1 |  | Facility: Radial
103786 | 23S | Approved | P3 | 38 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652 | 156.4 | 700 | 93.1 |  |  |  |  | 1096 | G_TURKCOAL ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
103787 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 219.4 | 71.8 | 204 | 107.6 |  |  |  |  | 1096 | G_TURKCOAL ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
103788 | 23S | Approved | P3 | 38 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.2 | 48.4 | 188 | 106.5 |  |  |  |  | 1096 | G_TURKCOAL ID 1+P1_2-1661_DOLHILL7%,SW SHV 7 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
103789 | 23S | Approved | P3 | 38 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 565.8 | 331.2 | 561 | 100.9 |  |  |  |  | 1100 | G_MUSKOG4G ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
103790 | 15S | Proposed | P0 | 39 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332 | 332 | 360 | 92.2 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
103791 | 15S | Proposed | P0 | 39 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.2 | 35.2 | 39 | 90.1 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
103792 | 15S | Proposed | P0 | 39 | 335781 2ZACHARY_REA69.0 335782 2PORT_HUD_A!69.0 1 | LN | 87.4 | 87.4 | 93 | 94 | [5 empty] | ** Base Case ** | 335781 | 335782 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  | Project Proposed | No violation: below Rate A | 14-EGL-016-CP | 2017-06-01 | Reconductor Port Hudson-Zachary REA 69 kV
103793 | 15S | Proposed | P0 | 39 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 35.2 | 35.2 | 39 | 90.2 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
103794 | 15S | Proposed | P0 | 39 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100.7 | 100.7 | 95 | 106 | [5 empty] | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case **
103795 | 15S | Proposed | P3 | 39 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 117 | 18.3 | 115 | 101.7 |  |  |  |  | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
103796 | 15S | Proposed | P3 | 39 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 117 | 18.3 | 115 | 101.7 |  |  |  |  | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
103819 | 15S | Proposed | P3 | 39 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 95.5 | 27.8 | 106 | 90.1 |  |  |  |  | 34 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 |  | No violation: below Rate A
103820 | 15S | Proposed | P3 | 39 | 337620 3WOODWARD-N! 115 337962 3ALTHEIMER+ 115 1 | LN | 109.9 | 32.5 | 106 | 103.6 |  |  |  |  | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337620 | 337962 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103821 | 15S | Proposed | P3 | 39 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | LN | 102.2 | 30.2 | 106 | 96.4 |  |  |  |  | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337962 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103822 | 15S | Proposed | P3 | 39 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | LN | 96.7 | 27.8 | 106 | 91.2 |  |  |  |  | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337964 | 338738 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 |  | No violation: below Rate A
103885 | 15S | Proposed | P3 | 39 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | LN | 101.2 | 62.9 | 106 | 95.5 |  |  |  |  | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337967 | 337972 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed | No violation: below Rate A | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
103931 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.9 | 123.8 | 226 | 111.5 |  |  |  |  | 134 | P1_2-1558_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1NM G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103932 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 258.2 | 123.8 | 226 | 114.2 |  |  |  |  | 135 | P1_2-1558_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1PLUM PT U1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103933 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 247.3 | 123.8 | 226 | 109.4 |  |  |  |  | 136 | P1_2-1558_8FREEPORTTN%+G_1CAL G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CAL G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103934 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 254.4 | 123.8 | 226 | 112.6 |  |  |  |  | 137 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F1HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103935 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 254.4 | 123.8 | 226 | 112.6 |  |  |  |  | 138 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F1HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103936 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 254.4 | 123.8 | 226 | 112.6 |  |  |  |  | 139 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F2HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103937 | 15S | Proposed | P3 | 39 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 254.4 | 123.8 | 226 | 112.6 |  |  |  |  | 140 | P1_2-1558_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1558_8FREEPORTTN% | G_1CUMBRL F2HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
103938 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.5 | 249.9 | 335 | 103.4 |  |  |  |  | 228 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103939 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.5 | 249.9 | 335 | 103.4 |  |  |  |  | 229 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103940 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.2 | 249.9 | 335 | 105.4 |  |  |  |  | 230 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103941 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.8 | 249.9 | 335 | 105.9 |  |  |  |  | 231 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103942 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.6 | 249.9 | 335 | 105.9 |  |  |  |  | 232 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103943 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.7 | 249.9 | 335 | 103.5 |  |  |  |  | 233 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103944 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.6 | 249.9 | 335 | 103.5 |  |  |  |  | 234 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103945 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.6 | 249.9 | 335 | 103.5 |  |  |  |  | 235 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103946 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.6 | 249.9 | 335 | 103.2 |  |  |  |  | 236 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1DOW_AEP_1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1DOW_AEP_1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103947 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.7 | 249.9 | 335 | 102.9 |  |  |  |  | 237 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103948 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.5 | 249.9 | 335 | 103.1 |  |  |  |  | 238 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103949 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.8 | 249.9 | 335 | 103.2 |  |  |  |  | 239 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103950 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.4 | 249.9 | 335 | 103.1 |  |  |  |  | 240 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103951 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.4 | 249.9 | 335 | 103.1 |  |  |  |  | 241 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103952 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.7 | 249.9 | 335 | 102.9 |  |  |  |  | 242 | P1_2-1637_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103953 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.4 | 249.9 | 335 | 104 |  |  |  |  | 243 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103954 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.5 | 249.9 | 335 | 104 |  |  |  |  | 244 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103955 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.9 | 249.9 | 335 | 103 |  |  |  |  | 245 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103956 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.4 | 249.9 | 335 | 103.1 |  |  |  |  | 246 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103957 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.2 | 249.9 | 335 | 102.8 |  |  |  |  | 247 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103958 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 376.4 | 249.9 | 335 | 112.4 |  |  |  |  | 248 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
103959 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.2 | 249.9 | 335 | 103.3 |  |  |  |  | 249 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103960 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.2 | 249.9 | 335 | 103.3 |  |  |  |  | 250 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103961 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.7 | 249.9 | 335 | 113.3 |  |  |  |  | 251 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility
103962 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.1 | 249.9 | 335 | 103.9 |  |  |  |  | 252 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103963 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.1 | 249.9 | 335 | 103.9 |  |  |  |  | 253 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103964 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.1 | 249.9 | 335 | 103.9 |  |  |  |  | 254 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GOXY U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GOXY U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103965 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.2 | 249.9 | 335 | 105.1 |  |  |  |  | 255 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1SOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103966 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.4 | 249.9 | 335 | 103.1 |  |  |  |  | 256 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103967 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.4 | 249.9 | 335 | 103.1 |  |  |  |  | 257 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103968 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.5 | 249.9 | 335 | 107 |  |  |  |  | 258 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103969 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.2 | 249.9 | 335 | 104.5 |  |  |  |  | 259 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103970 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.9 | 249.9 | 335 | 105.9 |  |  |  |  | 260 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GYP U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103971 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.2 | 249.9 | 335 | 103.9 |  |  |  |  | 261 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103972 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.2 | 249.9 | 335 | 103.9 |  |  |  |  | 262 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103973 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.1 | 249.9 | 335 | 104.2 |  |  |  |  | 263 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103974 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.5 | 249.9 | 335 | 108.5 |  |  |  |  | 264 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
103975 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364 | 249.9 | 335 | 108.7 |  |  |  |  | 265 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
103976 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346 | 249.9 | 335 | 103.3 |  |  |  |  | 266 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1NMIL U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103977 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 249.9 | 335 | 104.3 |  |  |  |  | 267 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1MICH U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103978 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 357.8 | 249.9 | 335 | 106.8 |  |  |  |  | 268 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1MICH U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103979 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.5 | 249.9 | 335 | 103.4 |  |  |  |  | 269 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103980 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.6 | 249.9 | 335 | 107 |  |  |  |  | 270 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1GGNS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103981 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.2 | 249.9 | 335 | 103.9 |  |  |  |  | 271 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103982 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344 | 249.9 | 335 | 102.7 |  |  |  |  | 272 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1HINDS G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103983 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.1 | 249.9 | 335 | 103 |  |  |  |  | 273 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1REX BRWN U4 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1REX BRWN U4 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103984 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.3 | 249.9 | 335 | 102.8 |  |  |  |  | 274 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103985 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.3 | 249.9 | 335 | 102.8 |  |  |  |  | 275 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103986 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.3 | 249.9 | 335 | 102.8 |  |  |  |  | 276 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103987 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.9 | 249.9 | 335 | 103.3 |  |  |  |  | 277 | P1_2-1637_COCODR 6%,VILPLT 6!+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103988 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.4 | 249.9 | 335 | 107.9 |  |  |  |  | 278 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G3TECHE! ID 1 |  | No violation: CLECO facility
103989 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.9 | 249.9 | 335 | 102.9 |  |  |  |  | 279 | P1_2-1637_COCODR 6%,VILPLT 6!+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103990 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.8 | 249.9 | 335 | 104.4 |  |  |  |  | 280 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1 ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103991 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.8 | 249.9 | 335 | 103.8 |  |  |  |  | 281 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103992 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.8 | 249.9 | 335 | 103.8 |  |  |  |  | 282 | P1_2-1637_COCODR 6%,VILPLT 6!+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103993 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.3 | 249.9 | 335 | 102.8 |  |  |  |  | 283 | P1_2-1637_COCODR 6%,VILPLT 6!+G_LABBE1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_LABBE1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103994 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345 | 249.9 | 335 | 103 |  |  |  |  | 284 | P1_2-1637_COCODR 6%,VILPLT 6!+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103995 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346 | 249.9 | 335 | 103.3 |  |  |  |  | 285 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HARGIS1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103996 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346 | 249.9 | 335 | 103.3 |  |  |  |  | 286 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HARGIS2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103997 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.1 | 249.9 | 335 | 102.7 |  |  |  |  | 287 | P1_2-1637_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103998 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345 | 249.9 | 335 | 103 |  |  |  |  | 288 | P1_2-1637_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
103999 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 344.1 | 249.9 | 335 | 102.7 |  |  |  |  | 289 | P1_2-1637_COCODR 6%,VILPLT 6!+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104000 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 345.9 | 249.9 | 335 | 103.2 |  |  |  |  | 290 | P1_2-1637_COCODR 6%,VILPLT 6!+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1637_COCODR 6%,VILPLT 6! | G_HOUMA 3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104003 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.7 | 94.9 | 700 | 93 |  |  |  |  | 306 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104004 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 221 | 88 | 204 | 108.3 |  |  |  |  | 306 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230
104005 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.9 | 64.5 | 188 | 106.8 |  |  |  |  | 306 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230
104006 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.7 | 94.9 | 700 | 93 |  |  |  |  | 307 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104007 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 221 | 88 | 204 | 108.3 |  |  |  |  | 307 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230
104008 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.9 | 64.5 | 188 | 106.8 |  |  |  |  | 307 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230
104009 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.8 | 94.9 | 700 | 93 |  |  |  |  | 308 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104010 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 220.4 | 88 | 204 | 108 |  |  |  |  | 308 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230
104011 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.3 | 64.5 | 188 | 106.6 |  |  |  |  | 308 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230
104012 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.9 | 94.9 | 700 | 93 |  |  |  |  | 309 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104013 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 220.8 | 88 | 204 | 108.2 |  |  |  |  | 309 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230
104014 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.8 | 64.5 | 188 | 106.8 |  |  |  |  | 309 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230
104015 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.9 | 94.9 | 700 | 93 |  |  |  |  | 310 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104016 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 222.5 | 88 | 204 | 109.1 |  |  |  |  | 310 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230
104017 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 202.5 | 64.5 | 188 | 107.7 |  |  |  |  | 310 | P1_2-1656_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230
104018 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.9 | 94.9 | 700 | 93 |  |  |  |  | 311 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104019 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 223.3 | 88 | 204 | 109.4 |  |  |  |  | 311 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230
104020 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 203.3 | 64.5 | 188 | 108.1 |  |  |  |  | 311 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230
104021 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.7 | 94.9 | 700 | 93 |  |  |  |  | 312 | P1_2-1656_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104022 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 219.9 | 88 | 204 | 107.8 |  |  |  |  | 312 | P1_2-1656_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230
104023 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 199.7 | 64.5 | 188 | 106.2 |  |  |  |  | 312 | P1_2-1656_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230
104024 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.9 | 94.9 | 700 | 93 |  |  |  |  | 313 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104025 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 223.3 | 88 | 204 | 109.5 |  |  |  |  | 313 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230
104026 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 203.3 | 64.5 | 188 | 108.2 |  |  |  |  | 313 | P1_2-1656_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230
104027 | 15S | Proposed | P3 | 39 | 334334 4LEACH! 138 700411 SIXMILE4 138 1 | LN | 153.1 | 90.4 | 166 | 92.2 |  |  |  |  | 314 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 334334 | 700411 | 1 |  | 138 | 138 | 351 | EES | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104028 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.8 | 94.9 | 700 | 93.3 |  |  |  |  | 314 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104029 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 248.8 | 88 | 204 | 121.9 |  |  |  |  | 314 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104030 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 230.3 | 64.5 | 188 | 122.5 |  |  |  |  | 314 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104031 | 15S | Proposed | P3 | 39 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 240.8 | 109.4 | 264 | 91.2 |  |  |  |  | 314 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104032 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.3 | 94.9 | 700 | 93.2 |  |  |  |  | 315 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104033 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 241.8 | 88 | 204 | 118.5 |  |  |  |  | 315 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104034 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 222.9 | 64.5 | 188 | 118.6 |  |  |  |  | 315 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104035 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.3 | 94.9 | 700 | 93.2 |  |  |  |  | 316 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104036 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 241.8 | 88 | 204 | 118.5 |  |  |  |  | 316 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104037 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 222.9 | 64.5 | 188 | 118.6 |  |  |  |  | 316 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104038 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.4 | 94.9 | 700 | 93.2 |  |  |  |  | 317 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104039 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 242.3 | 88 | 204 | 118.8 |  |  |  |  | 317 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104040 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 223.5 | 64.5 | 188 | 118.9 |  |  |  |  | 317 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104041 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651 | 94.9 | 700 | 93 |  |  |  |  | 318 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
104042 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 224.1 | 88 | 204 | 109.9 |  |  |  |  | 318 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230
104043 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 204.2 | 64.5 | 188 | 108.6 |  |  |  |  | 318 | P1_2-1656_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230
104044 | 15S | Proposed | P3 | 39 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.7 | 94.9 | 700 | 93 |  |  |  |  | 319 | P1_2-1656_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: below Rate A | Messick 500/230
104045 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 220.4 | 88 | 204 | 108 |  |  |  |  | 319 | P1_2-1656_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1656_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230
104046 | 15S | Proposed | P3 | 39 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 200.2 | 64.5 | 188 | 106.5 |  |  |  |  | 319 | P1_2-1656_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1656_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230
104047 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 150.5 | 91.1 | 150 | 100.3 |  |  |  |  | 320 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1
104048 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 154.1 | 93.3 | 150 | 102.7 |  |  |  |  | 320 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1
104049 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 175.9 | 91.1 | 150 | 117.3 |  |  |  |  | 321 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
104050 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 180.1 | 93.3 | 150 | 120 |  |  |  |  | 321 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
104051 | 15S | Proposed | P3 | 39 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.4 | 49.7 | 115 | 102.1 |  |  |  |  | 321 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104052 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 175.9 | 91.1 | 150 | 117.3 |  |  |  |  | 322 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
104053 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 180.1 | 93.3 | 150 | 120 |  |  |  |  | 322 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
104054 | 15S | Proposed | P3 | 39 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117.4 | 49.7 | 115 | 102.1 |  |  |  |  | 322 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104055 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 136.1 | 93.3 | 150 | 90.7 |  |  |  |  | 323 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+173 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: below Rate A
104056 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 158.2 | 91.1 | 150 | 105.5 |  |  |  |  | 324 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
104057 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 161.9 | 93.3 | 150 | 108 |  |  |  |  | 324 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
104058 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 158.2 | 91.1 | 150 | 105.5 |  |  |  |  | 325 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
104059 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 161.9 | 93.3 | 150 | 108 |  |  |  |  | 325 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
104060 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 342.2 | 249.9 | 335 | 102.2 |  |  |  |  | 326 | G_1BCAJUN2_U1% ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104061 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343.8 | 249.9 | 335 | 102.6 |  |  |  |  | 327 | G_1BCAJUN2_U2% ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104062 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343.6 | 249.9 | 335 | 102.6 |  |  |  |  | 328 | G_1BCAJUN2_U3% ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104063 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 484.7 | 330 | 470 | 103.1 |  |  |  |  | 331 | G_1G1LEWIS! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G1LEWIS! ID 1 | Reduce PPG Plant
104064 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 387.7 | 254.6 | 386 | 100.4 |  |  |  |  | 332 | G_1G1LEWIS! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G1LEWIS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104065 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 304.9 | 180.3 | 336 | 90.7 |  |  |  |  | 332 | G_1G1LEWIS! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G1LEWIS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104066 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 484.4 | 330 | 470 | 103.1 |  |  |  |  | 335 | G_1G2LEWIS! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G2LEWIS! ID 1 | Reduce PPG Plant
104067 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 387.6 | 254.6 | 386 | 100.4 |  |  |  |  | 336 | G_1G2LEWIS! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G2LEWIS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104068 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 304.8 | 180.3 | 336 | 90.7 |  |  |  |  | 336 | G_1G2LEWIS! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G2LEWIS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104069 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 395.2 | 254.6 | 386 | 102.4 |  |  |  |  | 338 | G_4TOLEDO% ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_4TOLEDO% ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104070 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 309.7 | 180.3 | 336 | 92.2 |  |  |  |  | 338 | G_4TOLEDO% ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_4TOLEDO% ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104071 | 15S | Proposed | P3 | 39 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 246.3 | 84.5 | 220 | 112 |  |  |  |  | 339 | G_1EXXONGT1! ID 1+P1_2-285_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-285_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
104072 | 15S | Proposed | P3 | 39 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 251.4 | 99.7 | 220 | 114.3 |  |  |  |  | 340 | G_1EXXONGT1! ID 1+P1_2-286_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-286_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
104073 | 15S | Proposed | P3 | 39 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 255.2 | 148 | 282 | 90.5 |  |  |  |  | 342 | G_1EXXONGT1! ID 1+P1_2-288_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-288_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104074 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 487.2 | 330 | 470 | 103.7 |  |  |  |  | 344 | G_1G1SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G1SABIN! ID 1 | Reduce PPG Plant
104075 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 487.2 | 330 | 470 | 103.7 |  |  |  |  | 345 | G_1G2SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G2SABIN! ID 1 | Reduce PPG Plant
104076 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 519.2 | 330 | 470 | 110.5 |  |  |  |  | 346 | G_1G3SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G3SABIN! ID 1 | Reduce PPG Plant
104077 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 390.7 | 254.6 | 386 | 101.2 |  |  |  |  | 347 | G_1G3SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G3SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104078 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 307.9 | 180.3 | 336 | 91.6 |  |  |  |  | 347 | G_1G3SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G3SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104079 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 494.6 | 330 | 470 | 105.2 |  |  |  |  | 348 | G_1G4SABIN! ID 1+P1_2-106_6MOSS_BLUFF!,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-106_6MOSS_BLUFF!,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
104080 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 496.1 | 330 | 470 | 105.6 |  |  |  |  | 349 | G_1G4SABIN! ID 1+P1_2-253_8CYPRESS%,8HARTBRG% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-253_8CYPRESS%,8HARTBRG% | G_1G4SABIN! ID 1 | Reduce PPG Plant
104081 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 566.1 | 330 | 470 | 120.5 |  |  |  |  | 350 | G_1G4SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
104082 | 15S | Proposed | P3 | 39 | 335135 6VERDINE% 230 335136 6PPG! 230 1 | LN | 444.1 | 224.4 | 470 | 94.5 |  |  |  |  | 350 | G_1G4SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335135 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 |  | No violation: below Rate A
104083 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 391.8 | 254.6 | 386 | 101.5 |  |  |  |  | 351 | G_1G4SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G4SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104084 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 308.9 | 180.3 | 336 | 91.9 |  |  |  |  | 351 | G_1G4SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G4SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104085 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 476.6 | 330 | 470 | 101.4 |  |  |  |  | 352 | G_1G5SABIN! ID 1+P1_2-253_8CYPRESS%,8HARTBRG% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-253_8CYPRESS%,8HARTBRG% | G_1G5SABIN! ID 1 | Reduce PPG Plant
104086 | 15S | Proposed | P3 | 39 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 540.2 | 330 | 470 | 114.9 |  |  |  |  | 353 | G_1G5SABIN! ID 1+P1_2-452_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-452_6CARLYSS%,6NELSON% | G_1G5SABIN! ID 1 | Reduce PPG Plant
104087 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 390.4 | 254.6 | 386 | 101.1 |  |  |  |  | 354 | G_1G5SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G5SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104088 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 307.6 | 180.3 | 336 | 91.5 |  |  |  |  | 354 | G_1G5SABIN! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1G5SABIN! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104089 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 392.9 | 254.6 | 386 | 101.8 |  |  |  |  | 355 | G_1NELSON_G4! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1NELSON_G4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104090 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 310 | 180.3 | 336 | 92.3 |  |  |  |  | 355 | G_1NELSON_G4! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1NELSON_G4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104091 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 394.2 | 254.6 | 386 | 102.1 |  |  |  |  | 356 | G_1NELSON_G6! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1NELSON_G6! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104092 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 310.9 | 180.3 | 336 | 92.5 |  |  |  |  | 356 | G_1NELSON_G6! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1NELSON_G6! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104093 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.5 | 249.9 | 335 | 100.7 |  |  |  |  | 357 | G_1CARVLE_C1! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104094 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 677.1 | 479.8 | 672 | 100.8 |  |  |  |  | 358 | G_1CARVLE_C2! ID 1+P1_2-775_6IBERVIL%,6BYULABUTTE! | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104095 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 677.1 | 479.8 | 672 | 100.8 |  |  |  |  | 359 | G_1CARVLE_C2! ID 1+1017 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104096 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.5 | 249.9 | 335 | 100.8 |  |  |  |  | 361 | G_1CARVLE_C2! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104097 | 15S | Proposed | P3 | 39 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1183.4 | 300.9 | 1069 | 110.7 |  |  |  |  | 363 | G_1RVR_BND_G1! ID 1+P1_2-585_8WEBRE%,8BYULABUTTE% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-585_8WEBRE%,8BYULABUTTE% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104098 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 676.5 | 479.8 | 672 | 100.7 |  |  |  |  | 364 | G_1RVR_BND_G1! ID 1+P1_2-746_6COLY%,8COLY% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-746_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104099 | 15S | Proposed | P3 | 39 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1248 | 300.9 | 1069 | 116.7 |  |  |  |  | 364 | G_1RVR_BND_G1! ID 1+P1_2-746_6COLY%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-746_6COLY%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104100 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 666 | 479.8 | 672 | 99.1 |  |  |  |  | 365 | G_1RVR_BND_G1! ID 1+P1_2-769_6FANCY_PT%,8FANCY_PT% | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-769_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104101 | 15S | Proposed | P3 | 39 | 335771 6COLY% 230 335837 8COLY% 500 1 | TR | 1283.1 | 814 | 1186 | 108.2 |  |  |  |  | 365 | G_1RVR_BND_G1! ID 1+P1_2-769_6FANCY_PT%,8FANCY_PT% | 335771 | 335837 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-769_6FANCY_PT%,8FANCY_PT% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104102 | 15S | Proposed | P3 | 39 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1303.2 | 300.9 | 1069 | 121.9 |  |  |  |  | 366 | G_1RVR_BND_G1! ID 1+P1_2-771_8MCKNIGHT%,8COLY% | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-771_8MCKNIGHT%,8COLY% | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104103 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 687 | 479.8 | 672 | 102.2 |  |  |  |  | 367 | G_1RVR_BND_G1! ID 1+1007 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104104 | 15S | Proposed | P3 | 39 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1025.5 | 300.9 | 1069 | 95.9 |  |  |  |  | 367 | G_1RVR_BND_G1! ID 1+1007 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-775_6IBERVIL%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104105 | 15S | Proposed | P3 | 39 | 335568 6WILLOW_GL% 230 335618 8WILLOW_GL% 500 1 | TR | 687 | 479.8 | 672 | 102.2 |  |  |  |  | 368 | G_1RVR_BND_G1! ID 1+1017 | 335568 | 335618 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EGL-003-CP | 2016-06-01 | Replace Willow Glenn 500-230 kV single phase transformer bank with 1200 MVA units
104106 | 15S | Proposed | P3 | 39 | 335825 6FANCY_PT% 230 335835 8FANCY_PT% 500 1 | TR | 1025.5 | 300.9 | 1069 | 95.9 |  |  |  |  | 368 | G_1RVR_BND_G1! ID 1+1017 | 335825 | 335835 | 1 |  | 500 | 230 | 351 | EES | 351 | EES | P1_2-785_8BYULABUTTE%,6BYULABUTTE! | G_1RVR_BND_G1! ID 1 | Project Proposed | No violation: below Rate A | 14-EGL-004-CP | 2017-06-01 | Install Fancy Point 2nd 500-230 kV, 1200 MVA transformer
104107 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 365.4 | 249.9 | 335 | 109.1 |  |  |  |  | 369 | G_1RVR_BND_G1! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
104108 | 15S | Proposed | P3 | 39 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 183.8 | 120.7 | 199 | 92.4 |  |  |  |  | 370 | G_1WAT U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104109 | 15S | Proposed | P3 | 39 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 206.5 | 141.8 | 199 | 103.8 |  |  |  |  | 370 | G_1WAT U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104110 | 15S | Proposed | P3 | 39 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 106.3 | 77.2 | 115 | 92.4 |  |  |  |  | 371 | G_1WAT U3! ID 1+1249 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1017_3PORTGIBSON!,3BXTRWILSON% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
104111 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.7 | 249.9 | 335 | 110.1 |  |  |  |  | 372 | G_1WAT U3! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility
104112 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.2 | 249.9 | 335 | 100.6 |  |  |  |  | 373 | G_1GOXY U1! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104113 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.2 | 249.9 | 335 | 100.6 |  |  |  |  | 374 | G_1GOXY U2! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104114 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.2 | 249.9 | 335 | 100.6 |  |  |  |  | 375 | G_1GOXY U3! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GOXY U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104115 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 341.3 | 249.9 | 335 | 101.9 |  |  |  |  | 376 | G_1SOXY U1! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1SOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104116 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.6 | 249.9 | 335 | 103.8 |  |  |  |  | 377 | G_1GYP U3! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104117 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.3 | 249.9 | 335 | 101.3 |  |  |  |  | 378 | G_1GYP U1! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104118 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 343.9 | 249.9 | 335 | 102.7 |  |  |  |  | 379 | G_1GYP U2! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GYP U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104119 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.3 | 249.9 | 335 | 100.7 |  |  |  |  | 380 | G_1NMIL6 CT1 ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104120 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.3 | 249.9 | 335 | 100.7 |  |  |  |  | 381 | G_1NMIL6 CT2 ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104121 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.1 | 249.9 | 335 | 100.9 |  |  |  |  | 382 | G_1NMIL6 ST1 ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104122 | 15S | Proposed | P3 | 39 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 179.9 | 120.7 | 199 | 90.4 |  |  |  |  | 383 | G_1NMIL U4! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104123 | 15S | Proposed | P3 | 39 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 202.5 | 141.8 | 199 | 101.7 |  |  |  |  | 383 | G_1NMIL U4! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104124 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.4 | 249.9 | 335 | 105.2 |  |  |  |  | 384 | G_1NMIL U4! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL U4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104125 | 15S | Proposed | P3 | 39 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 180.2 | 120.7 | 199 | 90.6 |  |  |  |  | 385 | G_1NMIL U5! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104126 | 15S | Proposed | P3 | 39 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 202.8 | 141.8 | 199 | 101.9 |  |  |  |  | 385 | G_1NMIL U5! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104127 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353 | 249.9 | 335 | 105.4 |  |  |  |  | 386 | G_1NMIL U5! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1NMIL U5! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104128 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.4 | 249.9 | 335 | 101 |  |  |  |  | 387 | G_1MICH U2! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1MICH U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104129 | 15S | Proposed | P3 | 39 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 200.9 | 141.8 | 199 | 100.9 |  |  |  |  | 388 | G_1MICH U3! ID 1+P1_2-860_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-860_6ADMSCRK%,8FRANKLIN% | G_1MICH U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104130 | 15S | Proposed | P3 | 39 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 232.4 | 135.2 | 229 | 101.5 |  |  |  |  | 389 | G_1MICH U3! ID 1+P1_2-946_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-946_39MILE%,3WSTWGO! | G_1MICH U3! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
104131 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.8 | 249.9 | 335 | 103.5 |  |  |  |  | 390 | G_1MICH U3! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1MICH U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104132 | 15S | Proposed | P3 | 39 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | LN | 416.2 | 179.6 | 462 | 90.1 |  |  |  |  | 391 | G_1GGNS U1 ID 1+P1_2-1083_8LAKEOVER%,8MCADAMS% | 336866 | 337015 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1083_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
104133 | 15S | Proposed | P3 | 39 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 517.5 | 278.8 | 561 | 92.3 |  |  |  |  | 391 | G_1GGNS U1 ID 1+P1_2-1083_8LAKEOVER%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1083_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A
104134 | 15S | Proposed | P3 | 39 | 337028 3CONEHOMA 115 337031 3CARTHAGE MS 115 1 | LN | 100.3 | 51 | 108 | 92.9 |  |  |  |  | 391 | G_1GGNS U1 ID 1+P1_2-1083_8LAKEOVER%,8MCADAMS% | 337028 | 337031 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1083_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
104135 | 15S | Proposed | P3 | 39 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 112.1 | 63.2 | 108 | 103.8 |  |  |  |  | 391 | G_1GGNS U1 ID 1+P1_2-1083_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1083_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104136 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.6 | 249.9 | 335 | 103.8 |  |  |  |  | 392 | G_1GGNS U1 ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1GGNS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104137 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 337.3 | 249.9 | 335 | 100.7 |  |  |  |  | 393 | G_1B.WLSN U2 ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104138 | 15S | Proposed | P3 | 39 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 616.3 | 278.8 | 561 | 109.9 |  |  |  |  | 394 | G_1ANDRUS U1 ID 1+P1_2-1092_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1092_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed
104139 | 15S | Proposed | P3 | 39 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 105.7 | 77.2 | 115 | 91.9 |  |  |  |  | 395 | G_1MURRY_U1&2 ID 1+1249 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1017_3PORTGIBSON!,3BXTRWILSON% | G_1MURRY_U1&2 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
104140 | 15S | Proposed | P3 | 39 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 105.7 | 77.2 | 115 | 91.9 |  |  |  |  | 396 | G_1MURRY_U3&4 ID 1+1249 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1017_3PORTGIBSON!,3BXTRWILSON% | G_1MURRY_U3&4 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
104141 | 15S | Proposed | P3 | 39 | 337331 3ALTO_LA 115 337390 3SWARTZ! 115 1 | LN | 105.7 | 77.2 | 115 | 91.9 |  |  |  |  | 397 | G_1MURRY_U5&6 ID 1+1249 | 337331 | 337390 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1017_3PORTGIBSON!,3BXTRWILSON% | G_1MURRY_U5&6 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
104142 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 387.7 | 254.6 | 386 | 100.4 |  |  |  |  | 398 | G_1ANO U1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1ANO U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104143 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 304.7 | 180.3 | 336 | 90.7 |  |  |  |  | 398 | G_1ANO U1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1ANO U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104144 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 388.6 | 254.6 | 386 | 100.7 |  |  |  |  | 399 | G_1ANO U2 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1ANO U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104145 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 305.5 | 180.3 | 336 | 90.9 |  |  |  |  | 399 | G_1ANO U2 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_1ANO U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104146 | 15S | Proposed | P3 | 39 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 288.7 | 160.1 | 266 | 108.5 |  |  |  |  | 400 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
104147 | 15S | Proposed | P3 | 39 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 252.3 | 123.1 | 266 | 94.9 |  |  |  |  | 400 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
104148 | 15S | Proposed | P3 | 39 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 424.8 | 237.1 | 450 | 94.4 |  |  |  |  | 400 | G_1ISES U1 ID 1+P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1481_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Generation redispatch: Turn on Ritchie unit 500 MW | No violation: below Rate A
104149 | 15S | Proposed | P3 | 39 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 69.6 | 39.1 | 77 | 90.4 |  |  |  |  | 401 | G_G1WKRAFT! ID 3+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1WKRAFT! ID 3 | Project External | No violation: below Rate A | Messick 500/230
104150 | 15S | Proposed | P3 | 39 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 102.6 | 52.9 | 98 | 104.7 |  |  |  |  | 403 | G_G1DOLHIL! ID 1+P1_2-241_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104151 | 15S | Proposed | P3 | 39 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 89 | 37.7 | 77 | 115.6 |  |  |  |  | 404 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104152 | 15S | Proposed | P3 | 39 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 92.5 | 39.1 | 77 | 120.1 |  |  |  |  | 404 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104153 | 15S | Proposed | P3 | 39 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 85.4 | 38.4 | 77 | 110.9 |  |  |  |  | 404 | G_G1DOLHIL! ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104154 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 405.5 | 254.6 | 386 | 105.1 |  |  |  |  | 405 | G_G1DOLHIL! ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104155 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 320.1 | 180.3 | 336 | 95.3 |  |  |  |  | 405 | G_G1DOLHIL! ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104156 | 15S | Proposed | P3 | 39 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 102.9 | 51.4 | 111 | 92.7 |  |  |  |  | 406 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104157 | 15S | Proposed | P3 | 39 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 119.6 | 65.3 | 115 | 104 |  |  |  |  | 406 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104158 | 15S | Proposed | P3 | 39 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 392.2 | 234.4 | 414 | 94.7 |  |  |  |  | 406 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104159 | 15S | Proposed | P3 | 39 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 75.2 | 38.4 | 77 | 97.6 |  |  |  |  | 406 | G_G1DOLHIL! ID 1+P1_2-1199_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1199_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104160 | 15S | Proposed | P3 | 39 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 80.6 | 37.7 | 77 | 104.7 |  |  |  |  | 408 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104161 | 15S | Proposed | P3 | 39 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 83.4 | 39.1 | 77 | 108.4 |  |  |  |  | 408 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104162 | 15S | Proposed | P3 | 39 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 78.4 | 38.4 | 77 | 101.8 |  |  |  |  | 408 | G_G1DOLHIL! ID 1+P1_2-1626_CARROLL6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1626_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104163 | 15S | Proposed | P3 | 39 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 81.2 | 37.7 | 77 | 105.5 |  |  |  |  | 409 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104164 | 15S | Proposed | P3 | 39 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 84.1 | 39.1 | 77 | 109.2 |  |  |  |  | 409 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104165 | 15S | Proposed | P3 | 39 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 79 | 38.4 | 77 | 102.6 |  |  |  |  | 409 | G_G1DOLHIL! ID 1+P1_2-1631_CLARN 6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104166 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 415.4 | 254.6 | 386 | 107.6 |  |  |  |  | 410 | G_G1DOLHIL! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104167 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 328.4 | 180.3 | 336 | 97.7 |  |  |  |  | 410 | G_G1DOLHIL! ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104168 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.4 | 249.9 | 335 | 104.6 |  |  |  |  | 412 | G_G3TECHE! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G3TECHE! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104169 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.8 | 249.9 | 335 | 101.1 |  |  |  |  | 413 | G_G1 ACAD! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1 ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104170 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 336.8 | 249.9 | 335 | 100.5 |  |  |  |  | 414 | G_G1-1ACAD! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104171 | 15S | Proposed | P3 | 39 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 336.8 | 249.9 | 335 | 100.5 |  |  |  |  | 415 | G_G1-2ACAD! ID 1+P1_2-1721_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1721_VILPLT 6!,WELLS 6% | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104172 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 147.2 | 91.1 | 150 | 98.2 |  |  |  |  | 416 | G_HARGIS1 ID 1+2122 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS1 ID 1 |  | No violation: below Rate A
104173 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 150.7 | 93.3 | 150 | 100.5 |  |  |  |  | 416 | G_HARGIS1 ID 1+2122 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS1 ID 1
104174 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 1 | TR | 147.2 | 91.1 | 150 | 98.2 |  |  |  |  | 417 | G_HARGIS2 ID 1+2122 | 502404 | 502405 | 1 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS2 ID 1 |  | No violation: below Rate A
104175 | 15S | Proposed | P3 | 39 | 502404 BONIN 4 138 502405 BONIN 2 69.0 2 | TR | 150.7 | 93.3 | 150 | 100.5 |  |  |  |  | 417 | G_HARGIS2 ID 1+2122 | 502404 | 502405 | 2 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS2 ID 1
104176 | 15S | Proposed | P3 | 39 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 104.7 | 52.9 | 98 | 106.9 |  |  |  |  | 420 | G_PIRKEY 1 ID 1+P1_2-241_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241_4BUNA!,4EVADALE! | G_PIRKEY 1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104177 | 15S | Proposed | P3 | 39 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 76.4 | 37.7 | 77 | 99.2 |  |  |  |  | 421 | G_PIRKEY 1 ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104178 | 15S | Proposed | P3 | 39 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 79 | 39.1 | 77 | 102.6 |  |  |  |  | 421 | G_PIRKEY 1 ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104179 | 15S | Proposed | P3 | 39 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 74 | 38.4 | 77 | 96.1 |  |  |  |  | 421 | G_PIRKEY 1 ID 1+P1_2-1166_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104180 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 394.3 | 254.6 | 386 | 102.1 |  |  |  |  | 422 | G_PIRKEY 1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104181 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 310.4 | 180.3 | 336 | 92.4 |  |  |  |  | 422 | G_PIRKEY 1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104182 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 404 | 254.6 | 386 | 104.7 |  |  |  |  | 423 | G_PIRKEY 1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104183 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 319.3 | 180.3 | 336 | 95 |  |  |  |  | 423 | G_PIRKEY 1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104184 | 15S | Proposed | P3 | 39 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 101.3 | 52.9 | 98 | 103.4 |  |  |  |  | 424 | G_WELSH2-1 ID 1+P1_2-241_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241_4BUNA!,4EVADALE! | G_WELSH2-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104185 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 388.9 | 254.6 | 386 | 100.7 |  |  |  |  | 425 | G_WELSH2-1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_WELSH2-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104186 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 305.6 | 180.3 | 336 | 90.9 |  |  |  |  | 425 | G_WELSH2-1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_WELSH2-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104187 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 398.5 | 254.6 | 386 | 103.2 |  |  |  |  | 426 | G_WELSH2-1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_WELSH2-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104188 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 314.4 | 180.3 | 336 | 93.6 |  |  |  |  | 426 | G_WELSH2-1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_WELSH2-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104189 | 15S | Proposed | P3 | 39 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 101.3 | 52.9 | 98 | 103.4 |  |  |  |  | 427 | G_WELSH3-1 ID 1+P1_2-241_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241_4BUNA!,4EVADALE! | G_WELSH3-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104190 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 388.9 | 254.6 | 386 | 100.7 |  |  |  |  | 428 | G_WELSH3-1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_WELSH3-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104191 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 305.6 | 180.3 | 336 | 90.9 |  |  |  |  | 428 | G_WELSH3-1 ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_WELSH3-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104192 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 398.5 | 254.6 | 386 | 103.2 |  |  |  |  | 429 | G_WELSH3-1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_WELSH3-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104193 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 314.4 | 180.3 | 336 | 93.6 |  |  |  |  | 429 | G_WELSH3-1 ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_WELSH3-1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104194 | 15S | Proposed | P3 | 39 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 101.5 | 52.9 | 98 | 103.6 |  |  |  |  | 430 | G_TURKCOAL ID 1+P1_2-241_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-241_4BUNA!,4EVADALE! | G_TURKCOAL ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104195 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 389.5 | 254.6 | 386 | 100.9 |  |  |  |  | 431 | G_TURKCOAL ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_TURKCOAL ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104196 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 306.1 | 180.3 | 336 | 91.1 |  |  |  |  | 431 | G_TURKCOAL ID 1+P1_2-1167_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1167_6MONTGOMERY!,COLFAX 6! | G_TURKCOAL ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104197 | 15S | Proposed | P3 | 39 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 399.2 | 254.6 | 386 | 103.4 |  |  |  |  | 432 | G_TURKCOAL ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_TURKCOAL ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104198 | 15S | Proposed | P3 | 39 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 315 | 180.3 | 336 | 93.8 |  |  |  |  | 432 | G_TURKCOAL ID 1+P1_2-1641_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1641_COLFAX 6!,RODEMR 6% | G_TURKCOAL ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104199 | 18L | Proposed | P0 | 40 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 331.8 | 331.8 | 360 | 92.2 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
104200 | 18L | Proposed | P0 | 40 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.2 | 35.2 | 39 | 90.3 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104201 | 18L | Proposed | P0 | 40 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | LN | 1075.9 | 1075.9 | 1194 | 90.1 | [5 empty] | ** Base Case ** | 335825 | 335830 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104202 | 18L | Proposed | P0 | 40 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.2 | 36.2 | 39 | 92.9 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
104203 | 18L | Proposed | P0 | 40 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101.3 | 101.3 | 112 | 90.4 | [5 empty] | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
104204 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 310.9 | 217.2 | 278 | 111.8 |  |  |  |  | 83 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+97 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1SLSBAU3 ID 5 | SPS: Clarksdale
104205 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 311.3 | 217.2 | 278 | 112 |  |  |  |  | 84 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+108 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1WHT BLUF U1 ID 1 | SPS: Clarksdale
104206 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 311.3 | 217.2 | 278 | 112 |  |  |  |  | 85 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+109 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1WHT BLUF U2 ID 1 | SPS: Clarksdale
104207 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 310.5 | 217.2 | 278 | 111.7 |  |  |  |  | 86 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+112 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1ISES U1 ID 1 | SPS: Clarksdale
104208 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 310.8 | 217.2 | 278 | 111.8 |  |  |  |  | 87 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+113 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1ISES U2 ID 1 | SPS: Clarksdale
104209 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 311 | 217.2 | 278 | 111.9 |  |  |  |  | 88 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+115 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1LSPWRU1 ID 1 | SPS: Clarksdale
104210 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 305.9 | 217.2 | 278 | 110 |  |  |  |  | 89 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+97 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1SLSBAU3 ID 5 | SPS: Clarksdale
104211 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 306.4 | 217.2 | 278 | 110.2 |  |  |  |  | 90 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+108 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1WHT BLUF U1 ID 1 | SPS: Clarksdale
104212 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 306.3 | 217.2 | 278 | 110.2 |  |  |  |  | 91 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+109 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1WHT BLUF U2 ID 1 | SPS: Clarksdale
104213 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 305.5 | 217.2 | 278 | 109.9 |  |  |  |  | 92 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+112 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1ISES U1 ID 1 | SPS: Clarksdale
104214 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 305.9 | 217.2 | 278 | 110 |  |  |  |  | 93 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+113 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1ISES U2 ID 1 | SPS: Clarksdale
104215 | 18L | Proposed | P3 | 40 | 337100 6CROSSROADS! 230 337107 6MOONLAKE% 230 1 | LN | 306.1 | 217.2 | 278 | 110.1 |  |  |  |  | 94 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+115 | 337100 | 337107 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1LSPWRU1 ID 1 | SPS: Clarksdale
104216 | 18L | Proposed | P3 | 40 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | LN | 1074.8 | 1075.9 | 1194 | 90 |  |  |  |  | 211 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1CARVLE_C1! ID 1 | 335825 | 335830 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1CARVLE_C1! ID 1 |  | No violation: below Rate A
104217 | 18L | Proposed | P3 | 40 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | LN | 1074.6 | 1075.9 | 1194 | 90 |  |  |  |  | 224 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1GYP U3! ID 1 | 335825 | 335830 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1GYP U3! ID 1 |  | No violation: below Rate A
104218 | 18L | Proposed | P3 | 40 | 335825 6FANCY_PT% 230 335830 6RIVER_BEND 230 1 | LN | 1074.8 | 1075.9 | 1194 | 90 |  |  |  |  | 231 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NMIL U5! ID 1 | 335825 | 335830 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1NMIL U5! ID 1 |  | No violation: below Rate A
104221 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.4 | 60.1 | 700 | 92.3 |  |  |  |  | 257 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1FRNTR 1! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104225 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.4 | 60.1 | 700 | 92.3 |  |  |  |  | 258 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1FRNTR 2! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104227 | 18L | Proposed | P3 | 40 | 337351 3SAILES! 115 337352 3RINGGOLD_LA 115 1 | LN | 109.7 | 34.4 | 115 | 95.4 |  |  |  |  | 259 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U1 ID 1 | 337351 | 337352 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104228 | 18L | Proposed | P3 | 40 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 119.6 | 43.5 | 125 | 95.7 |  |  |  |  | 259 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U1 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104229 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.4 | 60.1 | 700 | 92.3 |  |  |  |  | 259 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104231 | 18L | Proposed | P3 | 40 | 337351 3SAILES! 115 337352 3RINGGOLD_LA 115 1 | LN | 110.2 | 34.4 | 115 | 95.8 |  |  |  |  | 260 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U2 ID 1 | 337351 | 337352 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104232 | 18L | Proposed | P3 | 40 | 337352 3RINGGOLD_LA 115 337353 4RINGGOLD_LA 138 1 | TR | 120.1 | 43.5 | 125 | 96.1 |  |  |  |  | 260 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U2 ID 1 | 337352 | 337353 | 1 |  | 138 | 115 | 351 | EES | 351 | EES | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104233 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.5 | 60.1 | 700 | 92.4 |  |  |  |  | 260 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1ANO U2 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104237 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.5 | 60.1 | 700 | 92.4 |  |  |  |  | 261 | P1_2-1664_DOLHILL7%, SW SHV 7+G_1CAL G1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104241 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.4 | 60.1 | 700 | 92.3 |  |  |  |  | 262 | P1_2-1664_DOLHILL7%, SW SHV 7+G_BVR #1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104245 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.5 | 60.1 | 700 | 92.4 |  |  |  |  | 263 | P1_2-1664_DOLHILL7%, SW SHV 7+G_FLINTCR1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104249 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647 | 60.1 | 700 | 92.4 |  |  |  |  | 264 | P1_2-1664_DOLHILL7%, SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104250 | 18L | Proposed | P3 | 40 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 229.1 | 80.9 | 204 | 112.3 |  |  |  |  | 264 | P1_2-1664_DOLHILL7%, SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104253 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.8 | 60.1 | 700 | 92.4 |  |  |  |  | 265 | P1_2-1664_DOLHILL7%, SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104254 | 18L | Proposed | P3 | 40 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.5 | 80.9 | 204 | 113.5 |  |  |  |  | 265 | P1_2-1664_DOLHILL7%, SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104255 | 18L | Proposed | P3 | 40 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.2 | 57.7 | 233 | 91.1 |  |  |  |  | 265 | P1_2-1664_DOLHILL7%, SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%, SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104258 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.5 | 60.1 | 700 | 92.4 |  |  |  |  | 266 | P1_2-1664_DOLHILL7%, SW SHV 7+G_MUSKOG4G ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
104262 | 18L | Proposed | P3 | 40 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 646.4 | 60.1 | 700 | 92.3 |  |  |  |  | 267 | P1_2-1664_DOLHILL7%, SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%, SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: below Rate A | Messick 500/230
104264 | 18W | Proposed | P0 | 41 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.7 | 332.7 | 360 | 92.4 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
104265 | 18W | Proposed | P0 | 41 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.2 | 35.2 | 39 | 90.3 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104266 | 18W | Proposed | P0 | 41 | 360613 8MAGNOL CC1 500 990238 1.00 1 | TR | 333 | 333 | 360 | 92.5 | [5 empty] | ** Base Case ** | 360613 | 990238 | 1 |  | 500 | 18 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
104267 | 18W | Proposed | P0 | 41 | 360614 8MAGNOL CC2 500 990036 1.00 2 | TR | 333.2 | 333.2 | 360 | 92.5 | [5 empty] | ** Base Case ** | 360614 | 990036 | 2 |  | 500 | 18 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
104268 | 18W | Proposed | P0 | 41 | 360614 8MAGNOL CC2 500 990062 1.00 3 | TR | 333.2 | 333.2 | 360 | 92.5 | [5 empty] | ** Base Case ** | 360614 | 990062 | 3 |  | 500 | 18 | 347 | TVA | 347 | TVA | ** Base Case ** |  |  | No violation: below Rate A
104269 | 18W | Proposed | P0 | 41 | 500120 B.BRID 2 69.0 500620 NICKTAP2 69.0 1 | LN | 25.4 | 25.4 | 28 | 90.5 | [5 empty] | ** Base Case ** | 500120 | 500620 | 1 |  | 69 | 69 | 502 | CLEC | 502 | CLEC | ** Base Case ** |  |  | No violation: below Rate A
104270 | 18W | Proposed | P0 | 41 | 500620 NICKTAP2 69.0 502413 ELKS 2 69.0 1 | LN | 25.9 | 25.9 | 28 | 92.6 | [5 empty] | ** Base Case ** | 500620 | 502413 | 1 |  | 69 | 69 | 502 | CLEC | 503 | LAFA | ** Base Case ** |  |  | No violation: below Rate A
104271 | 18W | Proposed | P3 | 41 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 110.6 | 63.7 | 120 | 92.2 |  |  |  |  | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104272 | 18W | Proposed | P3 | 41 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 118.3 | 71.2 | 127 | 93.1 |  |  |  |  | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104273 | 18W | Proposed | P3 | 41 | 334307 4BUNA! 138 334308 4JNE EVA 138 1 | LN | 108.7 | 63.7 | 120 | 90.6 |  |  |  |  | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334307 | 334308 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104274 | 18W | Proposed | P3 | 41 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | LN | 116.4 | 71.2 | 127 | 91.6 |  |  |  |  | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334308 | 334309 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104275 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 111.9 | 61.8 | 98 | 114.2 |  |  |  |  | 91 | P1_2-247_4BUNA!,4EVADALE!+G_1FRNTR 1! ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1FRNTR 1! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104276 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 111.9 | 61.8 | 98 | 114.2 |  |  |  |  | 92 | P1_2-247_4BUNA!,4EVADALE!+G_1FRNTR 2! ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1FRNTR 2! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104277 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 102.1 | 61.8 | 98 | 104.1 |  |  |  |  | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104278 | 18W | Proposed | P3 | 41 | 334314 4URLAND! 138 334315 4WOODVILLE 138 1 | LN | 133 | 104 | 145 | 91.7 |  |  |  |  | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334314 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
104279 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.1 | 61.8 | 98 | 116.5 |  |  |  |  | 94 | P1_2-247_4BUNA!,4EVADALE!+G_1CAL G1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_1CAL G1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104280 | 18W | Proposed | P3 | 41 | 334280 4DOUCETT! 138 334315 4WOODVILLE 138 1 | LN | 132.5 | 100.8 | 145 | 91.4 |  |  |  |  | 95 | P1_2-247_4BUNA!,4EVADALE!+G_G1DOLHIL! ID 1 | 334280 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104281 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 121.1 | 61.8 | 98 | 123.6 |  |  |  |  | 95 | P1_2-247_4BUNA!,4EVADALE!+G_G1DOLHIL! ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104282 | 18W | Proposed | P3 | 41 | 334314 4URLAND! 138 334315 4WOODVILLE 138 1 | LN | 135.7 | 104 | 145 | 93.6 |  |  |  |  | 95 | P1_2-247_4BUNA!,4EVADALE!+G_G1DOLHIL! ID 1 | 334314 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104283 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.3 | 61.8 | 98 | 116.6 |  |  |  |  | 96 | P1_2-247_4BUNA!,4EVADALE!+G_FULTONU1 1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_FULTONU1 1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104284 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.4 | 61.8 | 98 | 116.7 |  |  |  |  | 97 | P1_2-247_4BUNA!,4EVADALE!+G_FLINTCR1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_FLINTCR1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104285 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 121.3 | 61.8 | 98 | 123.8 |  |  |  |  | 98 | P1_2-247_4BUNA!,4EVADALE!+G_PIRKEY 1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_PIRKEY 1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104286 | 18W | Proposed | P3 | 41 | 334314 4URLAND! 138 334315 4WOODVILLE 138 1 | LN | 132.2 | 104 | 145 | 91.2 |  |  |  |  | 98 | P1_2-247_4BUNA!,4EVADALE!+G_PIRKEY 1 ID 1 | 334314 | 334315 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104287 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 118.4 | 61.8 | 98 | 120.8 |  |  |  |  | 99 | P1_2-247_4BUNA!,4EVADALE!+G_WELSH2-1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_WELSH2-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104288 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 118.4 | 61.8 | 98 | 120.8 |  |  |  |  | 100 | P1_2-247_4BUNA!,4EVADALE!+G_WELSH3-1 ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_WELSH3-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104289 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 117.4 | 61.8 | 98 | 119.8 |  |  |  |  | 101 | P1_2-247_4BUNA!,4EVADALE!+G_TURKCOAL ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_TURKCOAL ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104290 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 114.8 | 61.8 | 98 | 117.2 |  |  |  |  | 102 | P1_2-247_4BUNA!,4EVADALE!+G_MUSKOG4G ID 1 | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_MUSKOG4G ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104292 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 89.2 | 700 | 92.4 |  |  |  |  | 227 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104294 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 89.2 | 700 | 92.4 |  |  |  |  | 228 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104296 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647 | 89.2 | 700 | 92.4 |  |  |  |  | 229 | P1_2-1664_DOLHILL7%,SW SHV 7+G_4RAYBURN% ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_4RAYBURN% ID 1 | Project External | No violation: below Rate A | Messick 500/230
104298 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.2 | 89.2 | 700 | 92.5 |  |  |  |  | 230 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104300 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.2 | 89.2 | 700 | 92.5 |  |  |  |  | 231 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104302 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.3 | 89.2 | 700 | 92.5 |  |  |  |  | 232 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104304 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.3 | 89.2 | 700 | 92.5 |  |  |  |  | 233 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104306 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 89.2 | 700 | 92.4 |  |  |  |  | 234 | P1_2-1664_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104308 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.3 | 89.2 | 700 | 92.5 |  |  |  |  | 235 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104310 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648.6 | 89.2 | 700 | 92.7 |  |  |  |  | 236 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104311 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 245.5 | 90.2 | 204 | 120.3 |  |  |  |  | 236 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104312 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 225.7 | 66.4 | 233 | 96.9 |  |  |  |  | 236 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104313 | 18W | Proposed | P3 | 41 | 500530 MANSFLD4 138 500762 REDRVRTAP4 138 1 | LN | 238.6 | 111.4 | 264 | 90.4 |  |  |  |  | 236 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500530 | 500762 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104314 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648.2 | 89.2 | 700 | 92.6 |  |  |  |  | 237 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104315 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239.3 | 90.2 | 204 | 117.3 |  |  |  |  | 237 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104316 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 219.2 | 66.4 | 233 | 94.1 |  |  |  |  | 237 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104317 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 648.2 | 89.2 | 700 | 92.6 |  |  |  |  | 238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104318 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 239.3 | 90.2 | 204 | 117.3 |  |  |  |  | 238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104319 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 219.2 | 66.4 | 233 | 94.1 |  |  |  |  | 238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104320 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.9 | 89.2 | 700 | 92.6 |  |  |  |  | 239 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104321 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 236.1 | 90.2 | 204 | 115.7 |  |  |  |  | 239 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104322 | 18W | Proposed | P3 | 41 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 215.8 | 66.4 | 233 | 92.6 |  |  |  |  | 239 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104323 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.4 | 89.2 | 700 | 92.5 |  |  |  |  | 240 | P1_2-1664_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
104325 | 18W | Proposed | P3 | 41 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 647.1 | 89.2 | 700 | 92.4 |  |  |  |  | 241 | P1_2-1664_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1664_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: below Rate A | Messick 500/230
104327 | 18W | Proposed | P3 | 41 | 502404 BONIN 4 138 502405 BONIN 2 69.0 3 | TR | 141.7 | 113.9 | 150 | 94.5 |  |  |  |  | 242 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+169 | 502404 | 502405 | 3 |  | 138 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: below Rate A
104328 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 70.2 | 45.2 | 77 | 91.2 |  |  |  |  | 249 | G_4RAYBURN% ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_4RAYBURN% ID 1 | Project External | No violation: below Rate A | Messick 500/230
104329 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 72.2 | 46.5 | 77 | 93.8 |  |  |  |  | 249 | G_4RAYBURN% ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_4RAYBURN% ID 1 | Project External | No violation: below Rate A | Messick 500/230
104330 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 358.5 | 250.5 | 386 | 92.9 |  |  |  |  | 250 | G_4RAYBURN% ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_4RAYBURN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104331 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 368.9 | 250.5 | 386 | 95.6 |  |  |  |  | 253 | G_4RAYBURN% ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1649_COLFAX 6!,RODEMR 6% | G_4RAYBURN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104333 | 18W | Proposed | P3 | 41 | 335072 6ROSE_BLUFF% 230 335136 6PPG! 230 1 | LN | 488.2 | 301.4 | 470 | 103.9 |  |  |  |  | 258 | G_1G4SABIN! ID 1+P1_2-458_6CARLYSS%,6NELSON% | 335072 | 335136 | 1 |  | 230 | 230 | 351 | EES | 351 | EES | P1_2-458_6CARLYSS%,6NELSON% | G_1G4SABIN! ID 1 | Reduce PPG Plant
104334 | 18W | Proposed | P3 | 41 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 347.8 | 232.6 | 335 | 103.8 |  |  |  |  | 260 | G_1RVR_BND_G1! ID 1+P1_2-1645_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1645_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104335 | 18W | Proposed | P3 | 41 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 336 | 232.6 | 335 | 100.3 |  |  |  |  | 261 | G_1RVR_BND_G1! ID 1+P1_2-1729_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1729_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104336 | 18W | Proposed | P3 | 41 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 101.7 | 52.6 | 100 | 101.7 |  |  |  |  | 262 | G_1WAT U3! ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104337 | 18W | Proposed | P3 | 41 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 100.4 | 51.9 | 100 | 100.4 |  |  |  |  | 262 | G_1WAT U3! ID 1+P1_2-761_2PORT_HUD_A!,6PORT_HUD% | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-761_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104338 | 18W | Proposed | P3 | 41 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.3 | 232.6 | 335 | 104.6 |  |  |  |  | 264 | G_1WAT U3! ID 1+P1_2-1645_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1645_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104339 | 18W | Proposed | P3 | 41 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 338.5 | 232.6 | 335 | 101.1 |  |  |  |  | 265 | G_1WAT U3! ID 1+P1_2-1729_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1729_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104340 | 18W | Proposed | P3 | 41 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 599.6 | 302.7 | 600 | 99.9 |  |  |  |  | 268 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104341 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 100.5 | 61.8 | 98 | 102.6 |  |  |  |  | 308 | G_G1DOLHIL! ID 1+P1_2-246_4CALL!,4BUNA! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-246_4CALL!,4BUNA! | G_G1DOLHIL! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104342 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 94.5 | 45.2 | 77 | 122.7 |  |  |  |  | 310 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104343 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 97.9 | 46.5 | 77 | 127.1 |  |  |  |  | 310 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104344 | 18W | Proposed | P3 | 41 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 83.9 | 40.1 | 77 | 108.9 |  |  |  |  | 310 | G_G1DOLHIL! ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104345 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 384.8 | 250.5 | 386 | 99.7 |  |  |  |  | 311 | G_G1DOLHIL! ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104346 | 18W | Proposed | P3 | 41 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 305.5 | 181.2 | 336 | 90.9 |  |  |  |  | 311 | G_G1DOLHIL! ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104347 | 18W | Proposed | P3 | 41 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 101.3 | 50.2 | 111 | 91.3 |  |  |  |  | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104348 | 18W | Proposed | P3 | 41 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 117.6 | 62.8 | 115 | 102.2 |  |  |  |  | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104349 | 18W | Proposed | P3 | 41 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 376.4 | 217.7 | 414 | 90.9 |  |  |  |  | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104350 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 69.5 | 46.5 | 77 | 90.3 |  |  |  |  | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104351 | 18W | Proposed | P3 | 41 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 75.9 | 40.1 | 77 | 98.6 |  |  |  |  | 312 | G_G1DOLHIL! ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1207_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104352 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 71.2 | 45.2 | 77 | 92.4 |  |  |  |  | 313 | G_G1DOLHIL! ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1208_7SAREPTA%,LONGWD 7 | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104353 | 18W | Proposed | P3 | 41 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 387.1 | 217.7 | 414 | 93.5 |  |  |  |  | 313 | G_G1DOLHIL! ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1208_7SAREPTA%,LONGWD 7 | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104354 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 73.3 | 46.5 | 77 | 95.2 |  |  |  |  | 313 | G_G1DOLHIL! ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1208_7SAREPTA%,LONGWD 7 | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104355 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 87.7 | 45.2 | 77 | 113.9 |  |  |  |  | 314 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104356 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 90.6 | 46.5 | 77 | 117.7 |  |  |  |  | 314 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104357 | 18W | Proposed | P3 | 41 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 78.2 | 40.1 | 77 | 101.6 |  |  |  |  | 314 | G_G1DOLHIL! ID 1+P1_2-1634_CARROLL6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1634_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104358 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 88.4 | 45.2 | 77 | 114.8 |  |  |  |  | 315 | G_G1DOLHIL! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104359 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 91.3 | 46.5 | 77 | 118.6 |  |  |  |  | 315 | G_G1DOLHIL! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104360 | 18W | Proposed | P3 | 41 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 78.8 | 40.1 | 77 | 102.3 |  |  |  |  | 315 | G_G1DOLHIL! ID 1+P1_2-1639_CLARN 6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1639_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104361 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 395.3 | 250.5 | 386 | 102.4 |  |  |  |  | 316 | G_G1DOLHIL! ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1649_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104362 | 18W | Proposed | P3 | 41 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 315 | 181.2 | 336 | 93.8 |  |  |  |  | 316 | G_G1DOLHIL! ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1649_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104363 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 71.5 | 45.2 | 77 | 92.9 |  |  |  |  | 317 | G_G1DOLHIL! ID 1+P1_2-1669_ELEESV 6!,RODEMR 6% | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1669_ELEESV 6!,RODEMR 6% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104364 | 18W | Proposed | P3 | 41 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 381.7 | 217.7 | 414 | 92.2 |  |  |  |  | 317 | G_G1DOLHIL! ID 1+P1_2-1669_ELEESV 6!,RODEMR 6% | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1669_ELEESV 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104365 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 73.5 | 46.5 | 77 | 95.5 |  |  |  |  | 317 | G_G1DOLHIL! ID 1+P1_2-1669_ELEESV 6!,RODEMR 6% | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1669_ELEESV 6!,RODEMR 6% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104366 | 18W | Proposed | P3 | 41 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 100.8 | 61.8 | 98 | 102.8 |  |  |  |  | 326 | G_PIRKEY 1 ID 1+P1_2-246_4CALL!,4BUNA! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-246_4CALL!,4BUNA! | G_PIRKEY 1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104367 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 79.3 | 45.2 | 77 | 103 |  |  |  |  | 328 | G_PIRKEY 1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104368 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 81.7 | 46.5 | 77 | 106.1 |  |  |  |  | 328 | G_PIRKEY 1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104369 | 18W | Proposed | P3 | 41 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 70.1 | 40.1 | 77 | 91 |  |  |  |  | 328 | G_PIRKEY 1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104370 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 370.1 | 250.5 | 386 | 95.9 |  |  |  |  | 329 | G_PIRKEY 1 ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104371 | 18W | Proposed | P3 | 41 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 380.5 | 250.5 | 386 | 98.6 |  |  |  |  | 331 | G_PIRKEY 1 ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1649_COLFAX 6!,RODEMR 6% | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104372 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 76.7 | 45.2 | 77 | 99.6 |  |  |  |  | 335 | G_WELSH2-1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104373 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 79 | 46.5 | 77 | 102.5 |  |  |  |  | 335 | G_WELSH2-1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104374 | 18W | Proposed | P3 | 41 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 76.7 | 45.2 | 77 | 99.6 |  |  |  |  | 337 | G_WELSH3-1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104375 | 18W | Proposed | P3 | 41 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 79 | 46.5 | 77 | 102.5 |  |  |  |  | 337 | G_WELSH3-1 ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104376 | 23S | Proposed | P0 | 42 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 333.3 | 333.3 | 360 | 92.6 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
104377 | 23S | Proposed | P0 | 42 | 303131 2KAPLAN 69.0 335336 2HUNTER 69.0 1 | LN | 18.1 | 18.1 | 19 | 95.2 | [5 empty] | ** Base Case ** | 303131 | 335336 | 1 |  | 69 | 69 | 332 | LAGN | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104378 | 23S | Proposed | P0 | 42 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.3 | 35.3 | 39 | 90.5 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104379 | 23S | Proposed | P0 | 42 | 335336 2HUNTER 69.0 335337 2MEAUX! 69.0 1 | LN | 53.7 | 53.7 | 56 | 96 | [5 empty] | ** Base Case ** | 335336 | 335337 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104380 | 23S | Proposed | P0 | 42 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179.7 | 179.7 | 193 | 93.1 | [5 empty] | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | No violation: below Rate A
104381 | 23S | Proposed | P0 | 42 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 38 | 38 | 39 | 97.4 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
104382 | 23S | Proposed | P0 | 42 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 106.5 | 106.5 | 112 | 95.1 | [5 empty] | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
104383 | 23S | Proposed | P0 | 42 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 548.8 | 548.8 | 598 | 91.8 | [5 empty] | ** Base Case ** | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
104384 | 23S | Proposed | P0 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100.7 | 100.7 | 95 | 106 | [5 empty] | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case **
104385 | 23S | Proposed | P3 | 42 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.6 | 548.8 | 598 | 91.4 |  |  |  |  | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Facility: Radial
104386 | 23S | Proposed | P3 | 42 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 125.5 | 17.2 | 115 | 109.1 |  |  |  |  | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
104387 | 23S | Proposed | P3 | 42 | 337715 3MILTON 115 337721 3ALBRIGHT 115 1 | LN | 167 | 21 | 176 | 94.9 |  |  |  |  | 3 | P1_2-1341_3BLAKELY!,3CARPENTER!+144 | 337715 | 337721 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | No violation: below Rate A
104388 | 23S | Proposed | P3 | 42 | 337686 3ARKLAHOMA% 115 337690 3CATHRINE U4 115 1 | LN | 546.6 | 548.8 | 598 | 91.4 |  |  |  |  | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337686 | 337690 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Facility: Radial
104389 | 23S | Proposed | P3 | 42 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 125.5 | 17.2 | 115 | 109.1 |  |  |  |  | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
104390 | 23S | Proposed | P3 | 42 | 337715 3MILTON 115 337721 3ALBRIGHT 115 1 | LN | 167 | 21 | 176 | 94.9 |  |  |  |  | 4 | P1_2-1341_3BLAKELY!,3CARPENTER!+145 | 337715 | 337721 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | No violation: below Rate A
104391 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 248.9 | 113.1 | 226 | 110.1 |  |  |  |  | 5 | P1_2-1563_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1NM G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104392 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 254.7 | 113.1 | 226 | 112.7 |  |  |  |  | 6 | P1_2-1563_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1PLUM PT U1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104393 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.5 | 113.1 | 226 | 111.3 |  |  |  |  | 7 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104394 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.5 | 113.1 | 226 | 111.3 |  |  |  |  | 8 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104395 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.5 | 113.1 | 226 | 111.3 |  |  |  |  | 9 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104396 | 23S | Proposed | P3 | 42 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.5 | 113.1 | 226 | 111.3 |  |  |  |  | 10 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104401 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.3 | 262.9 | 335 | 107.9 |  |  |  |  | 134 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility
104402 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.3 | 262.9 | 335 | 107.9 |  |  |  |  | 135 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility
104403 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.2 | 262.9 | 335 | 110.2 |  |  |  |  | 136 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility
104404 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.6 | 262.9 | 335 | 110.3 |  |  |  |  | 137 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility
104405 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 369.5 | 262.9 | 335 | 110.3 |  |  |  |  | 138 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility
104406 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.8 | 262.9 | 335 | 108 |  |  |  |  | 139 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility
104407 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.7 | 262.9 | 335 | 108 |  |  |  |  | 140 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility
104408 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.7 | 262.9 | 335 | 108 |  |  |  |  | 141 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility
104409 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 262.9 | 335 | 107.3 |  |  |  |  | 142 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104410 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 262.9 | 335 | 107.5 |  |  |  |  | 143 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility
104411 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.5 | 262.9 | 335 | 107.6 |  |  |  |  | 144 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility
104412 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.2 | 262.9 | 335 | 107.5 |  |  |  |  | 145 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility
104413 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.2 | 262.9 | 335 | 107.5 |  |  |  |  | 146 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility
104414 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 262.9 | 335 | 107.3 |  |  |  |  | 147 | P1_2-1642_COCODR 6%,VILPLT 6!+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104415 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.1 | 262.9 | 335 | 108.4 |  |  |  |  | 148 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility
104416 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.1 | 262.9 | 335 | 108.4 |  |  |  |  | 149 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility
104417 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.9 | 262.9 | 335 | 108.3 |  |  |  |  | 150 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1CARVLE_S1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1CARVLE_S1! ID 1 |  | No violation: CLECO facility
104418 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363 | 262.9 | 335 | 108.4 |  |  |  |  | 151 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G1! ID 1 |  | No violation: CLECO facility
104419 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.9 | 262.9 | 335 | 108.9 |  |  |  |  | 152 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G2! ID 1 |  | No violation: CLECO facility
104420 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 367.7 | 262.9 | 335 | 109.7 |  |  |  |  | 153 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WILL_GL_G4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WILL_GL_G4! ID 1 |  | No violation: CLECO facility
104421 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.7 | 262.9 | 335 | 107.4 |  |  |  |  | 154 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104422 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.1 | 262.9 | 335 | 107.5 |  |  |  |  | 155 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility
104423 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359 | 262.9 | 335 | 107.2 |  |  |  |  | 156 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104424 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 390.3 | 262.9 | 335 | 116.5 |  |  |  |  | 157 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
104425 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.7 | 262.9 | 335 | 110.1 |  |  |  |  | 158 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U1! ID 1 |  | No violation: CLECO facility
104426 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.7 | 262.9 | 335 | 110.1 |  |  |  |  | 159 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U2! ID 1 |  | No violation: CLECO facility
104427 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 394.3 | 262.9 | 335 | 117.7 |  |  |  |  | 160 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility
104428 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 367.1 | 262.9 | 335 | 109.6 |  |  |  |  | 161 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1SOXY U1! ID 1 |  | No violation: CLECO facility
104429 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.2 | 262.9 | 335 | 107.5 |  |  |  |  | 162 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility
104430 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.2 | 262.9 | 335 | 107.5 |  |  |  |  | 163 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility
104431 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373.7 | 262.9 | 335 | 111.5 |  |  |  |  | 164 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U3! ID 1 |  | No violation: CLECO facility
104432 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 365.3 | 262.9 | 335 | 109 |  |  |  |  | 165 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U1! ID 1 |  | No violation: CLECO facility
104433 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 370.2 | 262.9 | 335 | 110.5 |  |  |  |  | 166 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GYP U2! ID 1 |  | No violation: CLECO facility
104434 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363 | 262.9 | 335 | 108.4 |  |  |  |  | 167 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility
104435 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363 | 262.9 | 335 | 108.4 |  |  |  |  | 168 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility
104436 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363.9 | 262.9 | 335 | 108.6 |  |  |  |  | 169 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility
104437 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 378.8 | 262.9 | 335 | 113.1 |  |  |  |  | 170 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
104438 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.2 | 262.9 | 335 | 113.2 |  |  |  |  | 171 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
104439 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.9 | 262.9 | 335 | 107.7 |  |  |  |  | 172 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U3! ID 1 |  | No violation: CLECO facility
104440 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.3 | 262.9 | 335 | 108.8 |  |  |  |  | 173 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1MICH U2! ID 1 |  | No violation: CLECO facility
104441 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 373 | 262.9 | 335 | 111.3 |  |  |  |  | 174 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1MICH U3! ID 1 |  | No violation: CLECO facility
104442 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.9 | 262.9 | 335 | 107.1 |  |  |  |  | 175 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104443 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.9 | 262.9 | 335 | 107.1 |  |  |  |  | 176 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104444 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.9 | 262.9 | 335 | 107.1 |  |  |  |  | 177 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ISLVCRK3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ISLVCRK3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104445 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360 | 262.9 | 335 | 107.4 |  |  |  |  | 178 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility
104446 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 374 | 262.9 | 335 | 111.6 |  |  |  |  | 179 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1GGNS U1 ID 1 |  | No violation: CLECO facility
104447 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 361.2 | 262.9 | 335 | 107.8 |  |  |  |  | 180 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility
104448 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 262.9 | 335 | 107.3 |  |  |  |  | 181 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104449 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 262.9 | 335 | 107.3 |  |  |  |  | 182 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104450 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 262.9 | 335 | 107.2 |  |  |  |  | 183 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1HINDS S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1HINDS S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104451 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 262.9 | 335 | 107.2 |  |  |  |  | 184 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104452 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 262.9 | 335 | 107.2 |  |  |  |  | 185 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104453 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.1 | 262.9 | 335 | 107.2 |  |  |  |  | 186 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104454 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.6 | 262.9 | 335 | 107.3 |  |  |  |  | 187 | P1_2-1642_COCODR 6%,VILPLT 6!+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104455 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 376.6 | 262.9 | 335 | 112.4 |  |  |  |  | 188 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G3TECHE! ID 1 |  | No violation: CLECO facility
104456 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.7 | 262.9 | 335 | 107.4 |  |  |  |  | 189 | P1_2-1642_COCODR 6%,VILPLT 6!+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104457 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 364.8 | 262.9 | 335 | 108.9 |  |  |  |  | 190 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1 ACAD! ID 1 |  | No violation: CLECO facility
104458 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.7 | 262.9 | 335 | 108.3 |  |  |  |  | 191 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility
104459 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.6 | 262.9 | 335 | 108.2 |  |  |  |  | 192 | P1_2-1642_COCODR 6%,VILPLT 6!+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility
104460 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.2 | 262.9 | 335 | 107.2 |  |  |  |  | 193 | P1_2-1642_COCODR 6%,VILPLT 6!+G_LABBE1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_LABBE1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104461 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.5 | 262.9 | 335 | 107.3 |  |  |  |  | 194 | P1_2-1642_COCODR 6%,VILPLT 6!+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104462 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.9 | 262.9 | 335 | 107.7 |  |  |  |  | 195 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HARGIS1 ID 1 |  | No violation: CLECO facility
104463 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.9 | 262.9 | 335 | 107.7 |  |  |  |  | 196 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HARGIS2 ID 1 |  | No violation: CLECO facility
104464 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.3 | 262.9 | 335 | 108.1 |  |  |  |  | 197 | P1_2-1642_COCODR 6%,VILPLT 6!+G_BONIN2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_BONIN2 ID 1 |  | No violation: CLECO facility
104465 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359 | 262.9 | 335 | 107.2 |  |  |  |  | 198 | P1_2-1642_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104466 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.8 | 262.9 | 335 | 107.4 |  |  |  |  | 199 | P1_2-1642_COCODR 6%,VILPLT 6!+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104467 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360 | 262.9 | 335 | 107.5 |  |  |  |  | 200 | P1_2-1642_COCODR 6%,VILPLT 6!+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility
104468 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 360.3 | 262.9 | 335 | 107.5 |  |  |  |  | 201 | P1_2-1642_COCODR 6%,VILPLT 6!+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_HOUMA 3 ID 1 |  | No violation: CLECO facility
104469 | 23S | Proposed | P3 | 42 | 335366 4RICHARD% 138 335375 4COL_ACADMY! 138 1 | LN | 202.8 | 153.8 | 225 | 90.2 |  |  |  |  | 212 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335366 | 335375 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 |  | No violation: below Rate A
104470 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.5 | 262.9 | 335 | 104.6 |  |  |  |  | 216 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104471 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.5 | 262.9 | 335 | 104.6 |  |  |  |  | 217 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN1_U4% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN1_U4% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104472 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.3 | 262.9 | 335 | 107 |  |  |  |  | 218 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U1% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U1% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104473 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.7 | 262.9 | 335 | 107.1 |  |  |  |  | 219 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U2% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U2% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104474 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 358.7 | 262.9 | 335 | 107.1 |  |  |  |  | 220 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1BCAJUN2_U3% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1BCAJUN2_U3% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104475 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351 | 262.9 | 335 | 104.8 |  |  |  |  | 221 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_S26! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_S26! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104476 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 262.9 | 335 | 104.7 |  |  |  |  | 222 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_C25! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_C25! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104477 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 262.9 | 335 | 104.7 |  |  |  |  | 223 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ACADIA_C24! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ACADIA_C24! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104478 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.7 | 262.9 | 335 | 104.1 |  |  |  |  | 224 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104479 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.5 | 262.9 | 335 | 104.3 |  |  |  |  | 225 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 2 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 2 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104480 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.7 | 262.9 | 335 | 104.4 |  |  |  |  | 226 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104481 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 262.9 | 335 | 104.3 |  |  |  |  | 227 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104482 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 262.9 | 335 | 104.3 |  |  |  |  | 228 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 5 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 5 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104483 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.6 | 262.9 | 335 | 104.1 |  |  |  |  | 229 | P1_2-1726_VILPLT 6!,WELLS 6%+G_6DOW_COGEN% ID 6 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_6DOW_COGEN% ID 6 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104484 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.2 | 262.9 | 335 | 105.1 |  |  |  |  | 230 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_C1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_C1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104485 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.2 | 262.9 | 335 | 105.1 |  |  |  |  | 231 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_C2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_C2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104486 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.1 | 262.9 | 335 | 105.1 |  |  |  |  | 232 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1CARVLE_S1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1CARVLE_S1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104487 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.2 | 262.9 | 335 | 105.1 |  |  |  |  | 233 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104488 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.1 | 262.9 | 335 | 105.7 |  |  |  |  | 234 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104489 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 356.7 | 262.9 | 335 | 106.5 |  |  |  |  | 235 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WILL_GL_G4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WILL_GL_G4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104490 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.8 | 262.9 | 335 | 104.1 |  |  |  |  | 236 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ENCO_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ENCO_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104491 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.2 | 262.9 | 335 | 104.2 |  |  |  |  | 237 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1LA_STA_U5A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1LA_STA_U5A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104492 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.2 | 262.9 | 335 | 103.9 |  |  |  |  | 238 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1LA_STA_U4A! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1LA_STA_U4A! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104493 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 379.4 | 262.9 | 335 | 113.2 |  |  |  |  | 239 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1RVR_BND_G1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility
104494 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 357.9 | 262.9 | 335 | 106.8 |  |  |  |  | 240 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104495 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 357.9 | 262.9 | 335 | 106.8 |  |  |  |  | 241 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104496 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 383.4 | 262.9 | 335 | 114.4 |  |  |  |  | 242 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1WAT U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility
104497 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 356.2 | 262.9 | 335 | 106.3 |  |  |  |  | 243 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1SOXY U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1SOXY U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104498 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 262.9 | 335 | 104.3 |  |  |  |  | 244 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1UCARBGT1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1UCARBGT1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104499 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 262.9 | 335 | 104.3 |  |  |  |  | 245 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1UCARBGT2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1UCARBGT2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104500 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362.7 | 262.9 | 335 | 108.3 |  |  |  |  | 246 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U3! ID 1 |  | No violation: CLECO facility
104501 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 354.5 | 262.9 | 335 | 105.8 |  |  |  |  | 247 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U1! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104502 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 359.2 | 262.9 | 335 | 107.2 |  |  |  |  | 248 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GYP U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GYP U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104503 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.1 | 262.9 | 335 | 105.1 |  |  |  |  | 249 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 CT1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 CT1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104504 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 352.1 | 262.9 | 335 | 105.1 |  |  |  |  | 250 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 CT2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 CT2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104505 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.1 | 262.9 | 335 | 105.4 |  |  |  |  | 251 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL6 ST1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL6 ST1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104506 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 367.9 | 262.9 | 335 | 109.8 |  |  |  |  | 252 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U4! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U4! ID 1 |  | No violation: CLECO facility
104507 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 368.3 | 262.9 | 335 | 109.9 |  |  |  |  | 253 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U5! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U5! ID 1 |  | No violation: CLECO facility
104508 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350 | 262.9 | 335 | 104.5 |  |  |  |  | 254 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1NMIL U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1NMIL U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104509 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.5 | 262.9 | 335 | 105.5 |  |  |  |  | 255 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1MICH U2! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1MICH U2! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104510 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 362 | 262.9 | 335 | 108.1 |  |  |  |  | 256 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1MICH U3! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1MICH U3! ID 1 |  | No violation: CLECO facility
104511 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.1 | 262.9 | 335 | 104.2 |  |  |  |  | 257 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1B.WLSN U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1B.WLSN U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104512 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 363 | 262.9 | 335 | 108.4 |  |  |  |  | 258 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1GGNS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1GGNS U1 ID 1 |  | No violation: CLECO facility
104513 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.4 | 262.9 | 335 | 104.6 |  |  |  |  | 259 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1B.WLSN U2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1B.WLSN U2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104514 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.7 | 262.9 | 335 | 104.1 |  |  |  |  | 260 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104515 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.7 | 262.9 | 335 | 104.1 |  |  |  |  | 261 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104516 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.3 | 262.9 | 335 | 104 |  |  |  |  | 262 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1HINDS S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1HINDS S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104517 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.3 | 262.9 | 335 | 104 |  |  |  |  | 263 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA G1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA G1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104518 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.3 | 262.9 | 335 | 104 |  |  |  |  | 264 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA G2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA G2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104519 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.3 | 262.9 | 335 | 104 |  |  |  |  | 265 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ATTALA S1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ATTALA S1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104520 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.7 | 262.9 | 335 | 104.1 |  |  |  |  | 266 | P1_2-1726_VILPLT 6!,WELLS 6%+G_1ANDRUS U1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1ANDRUS U1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104521 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 365.7 | 262.9 | 335 | 109.2 |  |  |  |  | 267 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G3TECHE! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G3TECHE! ID 1 |  | No violation: CLECO facility
104522 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.9 | 262.9 | 335 | 104.1 |  |  |  |  | 268 | P1_2-1726_VILPLT 6!,WELLS 6%+G_TECHE_BS! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_TECHE_BS! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104523 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 353.8 | 262.9 | 335 | 105.6 |  |  |  |  | 269 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1 ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1 ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104524 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.8 | 262.9 | 335 | 105 |  |  |  |  | 270 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1-1ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1-1ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104525 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.7 | 262.9 | 335 | 105 |  |  |  |  | 271 | P1_2-1726_VILPLT 6!,WELLS 6%+G_G1-2ACAD! ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_G1-2ACAD! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104526 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.3 | 262.9 | 335 | 104 |  |  |  |  | 272 | P1_2-1726_VILPLT 6!,WELLS 6%+G_LABBE1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_LABBE1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104527 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.7 | 262.9 | 335 | 104.1 |  |  |  |  | 273 | P1_2-1726_VILPLT 6!,WELLS 6%+G_LABBE2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_LABBE2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104528 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350 | 262.9 | 335 | 104.5 |  |  |  |  | 274 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HARGIS1 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HARGIS1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104529 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350 | 262.9 | 335 | 104.5 |  |  |  |  | 275 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HARGIS2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HARGIS2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104530 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 351.4 | 262.9 | 335 | 104.9 |  |  |  |  | 276 | P1_2-1726_VILPLT 6!,WELLS 6%+G_BONIN2 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_BONIN2 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104531 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 348.2 | 262.9 | 335 | 103.9 |  |  |  |  | 277 | P1_2-1726_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 3 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 3 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104532 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349 | 262.9 | 335 | 104.2 |  |  |  |  | 278 | P1_2-1726_VILPLT 6!,WELLS 6%+G_MRGNCTY4 ID 4 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_MRGNCTY4 ID 4 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104533 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.2 | 262.9 | 335 | 104.2 |  |  |  |  | 279 | P1_2-1726_VILPLT 6!,WELLS 6%+G_PLAQUEM6 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_PLAQUEM6 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104534 | 23S | Proposed | P3 | 42 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 349.4 | 262.9 | 335 | 104.3 |  |  |  |  | 280 | P1_2-1726_VILPLT 6!,WELLS 6%+G_HOUMA 3 ID 1 | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_HOUMA 3 ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104535 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.3 | 65.3 | 115 | 97.7 |  |  |  |  | 281 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+74 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104536 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.3 | 65.3 | 115 | 97.7 |  |  |  |  | 282 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+190 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104537 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.4 | 65.3 | 115 | 97.7 |  |  |  |  | 283 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+196 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104538 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 112.4 | 65.3 | 115 | 97.7 |  |  |  |  | 284 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+197 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104539 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 132.9 | 65.3 | 115 | 115.6 |  |  |  |  | 285 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+198 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104540 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 90.3 | 56.9 | 95 | 95.1 |  |  |  |  | 285 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+198 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: below Rate A
104541 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 132.9 | 65.3 | 115 | 115.6 |  |  |  |  | 286 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+199 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104542 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502419 LUKE2 69.0 1 | LN | 90.3 | 56.9 | 95 | 95.1 |  |  |  |  | 286 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+199 | 502405 | 502419 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: below Rate A
104543 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 101.8 | 100.7 | 95 | 107.2 |  |  |  |  | 287 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+74 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
104544 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.9 | 100.7 | 95 | 108.3 |  |  |  |  | 288 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+188 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | Facility: Radial
104545 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.1 | 100.7 | 95 | 107.5 |  |  |  |  | 289 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+190 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | Facility: Radial
104546 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 101.8 | 100.7 | 95 | 107.1 |  |  |  |  | 290 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+196 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | Facility: Radial
104547 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 101.8 | 100.7 | 95 | 107.2 |  |  |  |  | 291 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+197 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 |  | Facility: Radial
104548 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117 | 65.3 | 115 | 101.7 |  |  |  |  | 292 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+198 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104549 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 117 | 65.3 | 115 | 101.7 |  |  |  |  | 293 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+199 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104550 | 23S | Proposed | P3 | 42 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.4 | 100.7 | 95 | 107.8 |  |  |  |  | 294 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+200 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
104553 | 23S | Proposed | P3 | 42 | 334398 4HAMPTON 138 334430 4SABINE! 138 1 | LN | 264.1 | 153.4 | 287 | 92 |  |  |  |  | 303 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334398 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104554 | 23S | Proposed | P3 | 42 | 334396 47NECHES! 138 334397 4OILLA 138 1 | LN | 254.9 | 147.5 | 282 | 90.4 |  |  |  |  | 304 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334396 | 334397 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104555 | 23S | Proposed | P3 | 42 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 262.5 | 152.3 | 282 | 93.1 |  |  |  |  | 304 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104558 | 23S | Proposed | P3 | 42 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 622 | 339.6 | 600 | 103.7 |  |  |  |  | 319 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104559 | 23S | Proposed | P3 | 42 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | LN | 443.3 | 163.7 | 462 | 95.9 |  |  |  |  | 320 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 336866 | 337015 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
104560 | 23S | Proposed | P3 | 42 | 337016 3PICKENS! 115 337018 3MIDWAY MS+ 115 1 | LN | 118.8 | 52.7 | 108 | 110 |  |  |  |  | 320 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337016 | 337018 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104561 | 23S | Proposed | P3 | 42 | 337028 3CONEHOMA 115 337031 3CARTHAGE MS 115 1 | LN | 100.8 | 48.1 | 108 | 93.4 |  |  |  |  | 320 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337031 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 |  | No violation: below Rate A
104562 | 23S | Proposed | P3 | 42 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 113 | 60.5 | 108 | 104.6 |  |  |  |  | 320 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104563 | 23S | Proposed | P3 | 42 | 337023 3GREENWOOD+ 115 337054 3GREENWOOD! 115 1 | LN | 72 | 38.3 | 70 | 102.8 |  |  |  |  | 327 | G_3GREENWOOD! ID 1+P1_2-1100_6MCADAMS%,3ATTALA! | 337023 | 337054 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1100_6MCADAMS%,3ATTALA! | G_3GREENWOOD! ID 1
104564 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160 | 109.6 | 159 | 100.6 |  |  |  |  | 329 | G_1WHT BLUF U1 ID 1+1549 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1WHT BLUF U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104565 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160 | 109.6 | 159 | 100.6 |  |  |  |  | 330 | G_1WHT BLUF U1 ID 1+1586 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1WHT BLUF U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104566 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.4 | 109.6 | 159 | 100.9 |  |  |  |  | 333 | G_1WHT BLUF U2 ID 1+1549 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1WHT BLUF U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104567 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 160.4 | 109.6 | 159 | 100.9 |  |  |  |  | 334 | G_1WHT BLUF U2 ID 1+1586 | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1WHT BLUF U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104568 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 164.4 | 109.6 | 159 | 103.4 |  |  |  |  | 339 | G_1ANO U1 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ANO U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104569 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 164.4 | 109.6 | 159 | 103.4 |  |  |  |  | 340 | G_1ANO U1 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ANO U1 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104570 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 166.9 | 109.6 | 159 | 105 |  |  |  |  | 343 | G_1ANO U2 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ANO U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104571 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 166.9 | 109.6 | 159 | 105 |  |  |  |  | 344 | G_1ANO U2 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ANO U2 ID 1 | Project Approved |  | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104572 | 23S | Proposed | P3 | 42 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 239.6 | 116.9 | 223 | 107.4 |  |  |  |  | 347 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1
104573 | 23S | Proposed | P3 | 42 | 338413 5WM LEHI-E 161 338414 5WM POLK AVE 161 1 | LN | 202.3 | 79.9 | 223 | 90.7 |  |  |  |  | 347 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338413 | 338414 | 1 |  | 161 | 161 | 334 | WMU | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1 |  | No violation: below Rate A
104574 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 158.8 | 109.6 | 159 | 99.8 |  |  |  |  | 350 | G_1ISES U2 ID 1+P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1311_8SHERIDAN%,8MAGNETCOVE% | G_1ISES U2 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104575 | 23S | Proposed | P3 | 42 | 337800 3HASKELL 115 337801 3WOODLAWN% 115 1 | LN | 158.7 | 109.6 | 159 | 99.8 |  |  |  |  | 351 | G_1ISES U2 ID 1+P1_2-1348_8HS EHV%,8MAGNETCOVE% | 337800 | 337801 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1348_8HS EHV%,8MAGNETCOVE% | G_1ISES U2 ID 1 | Project Approved | No violation: below Rate A | 14-EAI-008-CP | 2014-12-01 | Haskell to Woodlawn 115 kV line - Upgrade line
104576 | 23S | Proposed | P3 | 42 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 76.8 | 32.5 | 77 | 99.8 |  |  |  |  | 367 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104577 | 23S | Proposed | P3 | 42 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 79.6 | 33.9 | 77 | 103.4 |  |  |  |  | 367 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104578 | 23S | Proposed | P3 | 42 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 389.7 | 260.3 | 386 | 101 |  |  |  |  | 368 | G_G1DOLHIL! ID 1+P1_2-1172_6MONTGOMERY!,COLFAX 6! | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1172_6MONTGOMERY!,COLFAX 6! | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104579 | 23S | Proposed | P3 | 42 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 400.2 | 260.3 | 386 | 103.7 |  |  |  |  | 370 | G_G1DOLHIL! ID 1+P1_2-1646_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1646_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104580 | 23S | Proposed | P3 | 42 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 308.5 | 178.5 | 336 | 91.8 |  |  |  |  | 370 | G_G1DOLHIL! ID 1+P1_2-1646_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1646_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104582 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 115.8 | 65.3 | 115 | 100.7 |  |  |  |  | 376 | G_HARGIS1 ID 1+2133 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104583 | 23S | Proposed | P3 | 42 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 115.8 | 65.3 | 115 | 100.7 |  |  |  |  | 377 | G_HARGIS2 ID 1+2133 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502402 ACADIAN6 230 502403 BONIN6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104584 | 23S | Proposed | P3 | 42 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 389.6 | 260.3 | 386 | 100.9 |  |  |  |  | 389 | G_PIRKEY 1 ID 1+P1_2-1646_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1646_COLFAX 6!,RODEMR 6% | G_PIRKEY 1 ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104589 | 23S | Proposed | P3 | 42 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 363.8 | 333.3 | 360 | 101.1 |  |  |  |  | 406 | Unit:303033 1G2INTHB18.0 Id:1+349 | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | P1_2-101_8COTNWOOD2!,8HARTBRG% | Unit:303033 1G2INTHB18.0 Id:1 | backing down Cottonwood units output
104590 | 18S | Proposed | P0 | 43 | 303028 8COTNWOOD1! 500 303029 8XFMRINT1 500 1 | TR | 332.1 | 332.1 | 360 | 92.2 | [5 empty] | ** Base Case ** | 303028 | 303029 | 1 |  | 500 | 500 | 332 | LAGN | 332 | LAGN | ** Base Case ** |  |  | No violation: below Rate A
104591 | 18S | Proposed | P0 | 43 | 335030 2LINE-285_TP69.0 335031 2LN-633_TP 69.0 1 | LN | 35.2 | 35.2 | 39 | 90.3 | [5 empty] | ** Base Case ** | 335030 | 335031 | 1 |  | 69 | 69 | 351 | EES | 351 | EES | ** Base Case ** |  |  | No violation: below Rate A
104592 | 18S | Proposed | P0 | 43 | 336848 6LAKEOVER% 230 336850 6HINDS-2 230 1 | LN | 179.7 | 179.7 | 193 | 93.1 | [5 empty] | ** Base Case ** | 336848 | 336850 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | ** Base Case ** |  |  | No violation: below Rate A
104593 | 18S | Proposed | P0 | 43 | 337321 3VIDALIA_LA 115 503309 VIDALIA3 115 Z1 | LN | 36.2 | 36.2 | 39 | 92.9 | [5 empty] | ** Base Case ** | 337321 | 503309 | Z1 |  | 115 | 115 | 351 | EES | 504 | LEPA | ** Base Case ** |  |  | No violation: below Rate A
104594 | 18S | Proposed | P0 | 43 | 337581 3CROSSETT.N! 115 337582 3CROSSETT PM 115 1 | LN | 101.3 | 101.3 | 112 | 90.4 | [5 empty] | ** Base Case ** | 337581 | 337582 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | ** Base Case ** |  |  | No violation: below Rate A
104595 | 18S | Proposed | P0 | 43 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 100.7 | 100.7 | 95 | 106 | [5 empty] | ** Base Case ** | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | ** Base Case **
104636 | 18S | Proposed | P3 | 43 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 105.9 | 54.2 | 100 | 105.9 |  |  |  |  | 21 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1WAT U3! ID 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104637 | 18S | Proposed | P3 | 43 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 104.5 | 53.5 | 100 | 104.5 |  |  |  |  | 21 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1WAT U3! ID 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104654 | 18S | Proposed | P3 | 43 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 104 | 54.2 | 100 | 104 |  |  |  |  | 30 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1GYP U3! ID 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104655 | 18S | Proposed | P3 | 43 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 102.6 | 53.5 | 100 | 102.6 |  |  |  |  | 30 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1GYP U3! ID 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1GYP U3! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104666 | 18S | Proposed | P3 | 43 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 104.4 | 54.2 | 100 | 104.4 |  |  |  |  | 36 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1NMIL U4! ID 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104667 | 18S | Proposed | P3 | 43 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 103 | 53.5 | 100 | 103 |  |  |  |  | 36 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1NMIL U4! ID 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104668 | 18S | Proposed | P3 | 43 | 335782 2PORT_HUD_A!69.0 335805 4PORT_HUD! 138 1 | TR | 104.4 | 54.2 | 100 | 104.4 |  |  |  |  | 37 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1NMIL U5! ID 1 | 335782 | 335805 | 1 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104669 | 18S | Proposed | P3 | 43 | 335796 2PORT_HUD_B!69.0 335805 4PORT_HUD! 138 2 | TR | 103 | 53.5 | 100 | 103 |  |  |  |  | 37 | P1_2-760_2PORT_HUD_A!,6PORT_HUD%+G_1NMIL U5! ID 1 | 335796 | 335805 | 2 |  | 138 | 69 | 351 | EES | 351 | EES | P1_2-760_2PORT_HUD_A!,6PORT_HUD% | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EGL-018-CP | 2019-06-01 | Replace Port Hudson Substation 138-69 kV autos with 200 MVA units
104686 | 18S | Proposed | P3 | 43 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 119.8 | 18.5 | 115 | 104.2 |  |  |  |  | 46 | P1_2-1341_3BLAKELY!,3CARPENTER!+141 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
104687 | 18S | Proposed | P3 | 43 | 337714 3ROYAL 115 337715 3MILTON 115 1 | LN | 119.8 | 18.5 | 115 | 104.2 |  |  |  |  | 47 | P1_2-1341_3BLAKELY!,3CARPENTER!+142 | 337714 | 337715 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1341_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
104688 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 249.1 | 119.9 | 226 | 110.2 |  |  |  |  | 48 | P1_2-1563_8FREEPORTTN%+G_1NM G1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1NM G1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104689 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 255.6 | 119.9 | 226 | 113.1 |  |  |  |  | 49 | P1_2-1563_8FREEPORTTN%+G_1PLUM PT U1 ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1PLUM PT U1 ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104690 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.6 | 119.9 | 226 | 111.3 |  |  |  |  | 50 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104691 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.6 | 119.9 | 226 | 111.3 |  |  |  |  | 51 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F1HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F1HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104692 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.6 | 119.9 | 226 | 111.3 |  |  |  |  | 52 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 1 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 1 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104693 | 18S | Proposed | P3 | 43 | 337181 5HORN LAKE% 161 360174 5ALLEN FP 161 1 | LN | 251.5 | 119.9 | 226 | 111.3 |  |  |  |  | 53 | P1_2-1563_8FREEPORTTN%+G_1CUMBRL F2HL ID 2 | 337181 | 360174 | 1 |  | 161 | 161 | 326 | EES-EMI | 347 | TVA | P1_2-1563_8FREEPORTTN% | G_1CUMBRL F2HL ID 2 |  | Model: Horn Lake 230/161 kV Auto energization plan cancelled. No longer a valid issue.
104695 | 18S | Proposed | P3 | 43 | 335452 4BLOOMFLD% 138 335454 4COLTON 138 1 | LN | 202.9 | 25.7 | 225 | 90.2 |  |  |  |  | 140 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335452 | 335454 | 1 |  | 138 | 138 | 332 | LAGN | 351 | EES | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 |  | No violation: below Rate A
104696 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.3 | 112.2 | 700 | 92.9 |  |  |  |  | 148 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104697 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 210.9 | 84.3 | 204 | 103.4 |  |  |  |  | 148 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104698 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 190.7 | 61 | 188 | 101.4 |  |  |  |  | 148 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project External |  | Messick 500/230
104699 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.3 | 112.2 | 700 | 92.9 |  |  |  |  | 149 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104700 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 210.9 | 84.3 | 204 | 103.4 |  |  |  |  | 149 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104701 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 190.7 | 61 | 188 | 101.4 |  |  |  |  | 149 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project External |  | Messick 500/230
104702 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.4 | 112.2 | 700 | 92.9 |  |  |  |  | 150 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104703 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 211.1 | 84.3 | 204 | 103.5 |  |  |  |  | 150 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104704 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 191 | 61 | 188 | 101.6 |  |  |  |  | 150 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project External |  | Messick 500/230
104705 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.5 | 112.2 | 700 | 92.9 |  |  |  |  | 151 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104706 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 211.4 | 84.3 | 204 | 103.6 |  |  |  |  | 151 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104707 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 191.3 | 61 | 188 | 101.8 |  |  |  |  | 151 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project External |  | Messick 500/230
104708 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.5 | 112.2 | 700 | 92.9 |  |  |  |  | 152 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104709 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 213.4 | 84.3 | 204 | 104.6 |  |  |  |  | 152 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104710 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 193.4 | 61 | 188 | 102.9 |  |  |  |  | 152 | P1_2-1661_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project External |  | Messick 500/230
104711 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.5 | 112.2 | 700 | 92.9 |  |  |  |  | 153 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104712 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 212.7 | 84.3 | 204 | 104.3 |  |  |  |  | 153 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104713 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 192.7 | 61 | 188 | 102.5 |  |  |  |  | 153 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project External |  | Messick 500/230
104714 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.4 | 112.2 | 700 | 92.9 |  |  |  |  | 154 | P1_2-1661_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104715 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 210.7 | 84.3 | 204 | 103.3 |  |  |  |  | 154 | P1_2-1661_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104716 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 190.5 | 61 | 188 | 101.3 |  |  |  |  | 154 | P1_2-1661_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project External |  | Messick 500/230
104717 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.6 | 112.2 | 700 | 92.9 |  |  |  |  | 155 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104718 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 214.2 | 84.3 | 204 | 105 |  |  |  |  | 155 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104719 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 194.2 | 61 | 188 | 103.3 |  |  |  |  | 155 | P1_2-1661_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project External |  | Messick 500/230
104720 | 18S | Proposed | P3 | 43 | 334334 4LEACH! 138 700411 SIXMILE4 138 1 | LN | 150.2 | 91.3 | 166 | 90.5 |  |  |  |  | 156 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 334334 | 700411 | 1 |  | 138 | 138 | 351 | EES | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104721 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 652.2 | 112.2 | 700 | 93.2 |  |  |  |  | 156 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104722 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 236.5 | 84.3 | 204 | 115.9 |  |  |  |  | 156 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104723 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 217.7 | 61 | 188 | 115.8 |  |  |  |  | 156 | P1_2-1661_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
104724 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.9 | 112.2 | 700 | 93.1 |  |  |  |  | 157 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104725 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.9 | 84.3 | 204 | 113.7 |  |  |  |  | 157 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104726 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.8 | 61 | 188 | 113.2 |  |  |  |  | 157 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
104727 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.9 | 112.2 | 700 | 93.1 |  |  |  |  | 158 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External | No violation: below Rate A | Messick 500/230
104728 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 231.9 | 84.3 | 204 | 113.7 |  |  |  |  | 158 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104729 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 212.8 | 61 | 188 | 113.2 |  |  |  |  | 158 | P1_2-1661_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
104730 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 651.7 | 112.2 | 700 | 93.1 |  |  |  |  | 159 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External | No violation: below Rate A | Messick 500/230
104731 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 230.2 | 84.3 | 204 | 112.8 |  |  |  |  | 159 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104732 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 211.1 | 61 | 188 | 112.3 |  |  |  |  | 159 | P1_2-1661_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
104733 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.6 | 112.2 | 700 | 92.9 |  |  |  |  | 160 | P1_2-1661_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: below Rate A | Messick 500/230
104734 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 215 | 84.3 | 204 | 105.4 |  |  |  |  | 160 | P1_2-1661_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104735 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 195 | 61 | 188 | 103.7 |  |  |  |  | 160 | P1_2-1661_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project External |  | Messick 500/230
104736 | 18S | Proposed | P3 | 43 | 500250 DOLHILL7 345 500260 DOLHILL6 230 1 | TR | 650.4 | 112.2 | 700 | 92.9 |  |  |  |  | 161 | P1_2-1661_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500250 | 500260 | 1 |  | 345 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: below Rate A | Messick 500/230
104737 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 500530 MANSFLD4 138 1 | LN | 211.3 | 84.3 | 204 | 103.6 |  |  |  |  | 161 | P1_2-1661_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 500530 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1661_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External | No violation: CLECO facility, loading is less than rate B 219MVA | Messick 500/230
104738 | 18S | Proposed | P3 | 43 | 500430 IPAPER 4 138 507765 WALLAKE4 138 1 | LN | 191.2 | 61 | 188 | 101.7 |  |  |  |  | 161 | P1_2-1661_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 500430 | 507765 | 1 |  | 138 | 138 | 502 | CLEC | 520 | AEPW | P1_2-1661_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project External |  | Messick 500/230
104739 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 162 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+12 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G3INTHB ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104740 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 163 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+14 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G4INTHB ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104741 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 164 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+16 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1G1INTHB ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104742 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 165 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+17 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1FRNTR 1! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104743 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 166 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+18 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1FRNTR 2! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104744 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 167 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+27 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_4TOLEDO% ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104745 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 168 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+28 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1EXXONGT1! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104746 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 169 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+37 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DYNEGY_U1! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104747 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 170 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+38 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DYNEGY_U2! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104748 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 171 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+42 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_2PPG_GEN ID C4 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104749 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 172 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+43 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_2PPG_GEN ID C5 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104750 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 173 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+46 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1NELSON_G1! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104751 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 174 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+47 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1NELSON_G2! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104752 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 175 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+75 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104753 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 176 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+133 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WHT BLUF U1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104754 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 177 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+134 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1WHT BLUF U2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104755 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 178 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+137 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1CATHRINE U4 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104756 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 179 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+143 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1DUKE HS S1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104757 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 180 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+146 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ANO U1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104758 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 181 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+148 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104759 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 182 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+149 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104760 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 183 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+170 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1CAL G1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104761 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 184 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+178 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1WKRAFT! ID 3 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104762 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 185 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104763 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 186 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+185 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104764 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 187 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+188 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G7COUGH! ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104765 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 188 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+191 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104766 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 124.3 | 60.6 | 115 | 108.1 |  |  |  |  | 189 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+192 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104767 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 124.3 | 60.6 | 115 | 108.1 |  |  |  |  | 190 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+193 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104768 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.7 | 60.6 | 115 | 90.2 |  |  |  |  | 191 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+194 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104769 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 192 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+230 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_FLINTCR1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104770 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 103.6 | 60.6 | 115 | 90.1 |  |  |  |  | 193 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+235 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_MUSKOG4G ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104771 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 109.2 | 60.6 | 115 | 94.9 |  |  |  |  | 194 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+192 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104772 | 18S | Proposed | P3 | 43 | 502405 BONIN 2 69.0 502412 GILMAN 2 69.0 1 | LN | 109.2 | 60.6 | 115 | 94.9 |  |  |  |  | 195 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+193 | 502405 | 502412 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | No violation: LAFA facility, loading is less than rate B 135MVA
104773 | 18S | Proposed | P3 | 43 | 502413 ELKS 2 69.0 502422 HARGIS 69.0 1 | LN | 102.2 | 100.7 | 95 | 107.6 |  |  |  |  | 196 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+194 | 502413 | 502422 | 1 |  | 69 | 69 | 503 | LAFA | 503 | LAFA | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
104774 | 18S | Proposed | P3 | 43 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.8 | 167.7 | 243 | 92.1 |  |  |  |  | 200 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
104775 | 18S | Proposed | P3 | 43 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.7 | 167.7 | 243 | 92.1 |  |  |  |  | 201 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
104776 | 18S | Proposed | P3 | 43 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.4 | 167.7 | 243 | 91.9 |  |  |  |  | 202 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
104777 | 18S | Proposed | P3 | 43 | 334084 4CLVELND! 138 334208 4JACINTO% 138 1 | LN | 223.4 | 167.7 | 243 | 91.9 |  |  |  |  | 203 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334084 | 334208 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Horizon | No violation: below Rate A | 13-ETI-020-HZ | 2021-06-01 | Jacinto to Cleveland 138 kV Line: Upgrade line bay risers at both Jacinto and Cleveland
104778 | 18S | Proposed | P3 | 43 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | LN | 123.8 | 92.4 | 134 | 92.4 |  |  |  |  | 204 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334316 | 334317 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 |  | No violation: below Rate A
104779 | 18S | Proposed | P3 | 43 | 334391 4CARROLS% 138 334396 47NECHES! 138 2 | LN | 240.2 | 81.5 | 220 | 109.2 |  |  |  |  | 205 | G_1EXXONGT1! ID 1+P1_2-291_4CARROLS%,47NECHES! | 334391 | 334396 | 2 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-291_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-002-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 1
104780 | 18S | Proposed | P3 | 43 | 334391 4CARROLS% 138 334396 47NECHES! 138 1 | LN | 245.3 | 96.2 | 220 | 111.5 |  |  |  |  | 206 | G_1EXXONGT1! ID 1+P1_2-292_4CARROLS%,47NECHES! | 334391 | 334396 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-292_4CARROLS%,47NECHES! | G_1EXXONGT1! ID 1 | Project Horizon |  | 14-ETI-003-HZ | 2020-06-01 | Upgrade Carroll St-Neches 138 kV ckt 2
104781 | 18S | Proposed | P3 | 43 | 334398 4HAMPTON 138 334430 4SABINE! 138 1 | LN | 259.9 | 151.4 | 287 | 90.6 |  |  |  |  | 207 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334398 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104782 | 18S | Proposed | P3 | 43 | 334397 4OILLA 138 334430 4SABINE! 138 1 | LN | 258 | 149.9 | 282 | 91.5 |  |  |  |  | 208 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334397 | 334430 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | No violation: below Rate A
104785 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 346.8 | 235.9 | 335 | 103.5 |  |  |  |  | 222 | G_1RVR_BND_G1! ID 1+P1_2-1642_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104786 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 335.8 | 235.9 | 335 | 100.3 |  |  |  |  | 223 | G_1RVR_BND_G1! ID 1+P1_2-1726_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1RVR_BND_G1! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104787 | 18S | Proposed | P3 | 43 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | LN | 180.7 | 120.8 | 199 | 90.8 |  |  |  |  | 224 | G_1WAT U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336552 | 336553 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed | No violation: below Rate A | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104788 | 18S | Proposed | P3 | 43 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 204.4 | 141.9 | 199 | 102.7 |  |  |  |  | 224 | G_1WAT U3! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1WAT U3! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104789 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 350.8 | 235.9 | 335 | 104.7 |  |  |  |  | 226 | G_1WAT U3! ID 1+P1_2-1642_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1WAT U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104790 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 339.8 | 235.9 | 335 | 101.4 |  |  |  |  | 227 | G_1WAT U3! ID 1+P1_2-1726_VILPLT 6!,WELLS 6% | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1726_VILPLT 6!,WELLS 6% | G_1WAT U3! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104791 | 18S | Proposed | P3 | 43 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 200.7 | 141.9 | 199 | 100.9 |  |  |  |  | 232 | G_1NMIL U4! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U4! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104792 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 335.3 | 235.9 | 335 | 100.1 |  |  |  |  | 234 | G_1NMIL U4! ID 1+P1_2-1642_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U4! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104793 | 18S | Proposed | P3 | 43 | 336553 3MALLALIEU+ 115 336554 3BROOKHAVEN! 115 1 | LN | 201 | 141.9 | 199 | 101 |  |  |  |  | 235 | G_1NMIL U5! ID 1+P1_2-865_6ADMSCRK%,8FRANKLIN% | 336553 | 336554 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-865_6ADMSCRK%,8FRANKLIN% | G_1NMIL U5! ID 1 | Project Proposed |  | 12-EMI-001-CP | 2020-06-01 | Construct new Franklin-McComb 115 kV, constructed to 230 kV
104794 | 18S | Proposed | P3 | 43 | 500230 COUGH 4 138 500720 PLAISAN4 138 1 | LN | 335.8 | 235.9 | 335 | 100.2 |  |  |  |  | 237 | G_1NMIL U5! ID 1+P1_2-1642_COCODR 6%,VILPLT 6! | 500230 | 500720 | 1 |  | 138 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1642_COCODR 6%,VILPLT 6! | G_1NMIL U5! ID 1 |  | No violation: CLECO facility, loading is less than rate B 360MVA
104795 | 18S | Proposed | P3 | 43 | 336280 39MILE% 115 336286 3HARVEY2 115 1 | LN | 236 | 137.2 | 229 | 103 |  |  |  |  | 238 | G_1MICH U3! ID 1+P1_2-951_39MILE%,3WSTWGO! | 336280 | 336286 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-951_39MILE%,3WSTWGO! | G_1MICH U3! ID 1 | Project Horizon |  | 14-ELL-006-HZ | 2022-06-01 | Ninemile to Harvey2 115 kV: Reconductor line and change station limiting elements
104796 | 18S | Proposed | P3 | 43 | 336280 39MILE% 115 336284 3WSTWGO! 115 1 | LN | 230.8 | 162.9 | 229 | 100.8 |  |  |  |  | 239 | G_1MICH U3! ID 1+P1_2-952_39MILE%,3GRETNA! | 336280 | 336284 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-952_39MILE%,3GRETNA! | G_1MICH U3! ID 1 | Project Horizon |  | 13-ELL-006-HZ | 2020-06-01 | Ninemile to Westwego 115 kV: Reconductor Line
104797 | 18S | Proposed | P3 | 43 | 336907 3MIAMI ST 115 336938 3REX BRWN-W! 115 1 | LN | 294.8 | 227.2 | 320 | 92.1 |  |  |  |  | 243 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336907 | 336938 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104798 | 18S | Proposed | P3 | 43 | 336919 3LAKEOVER! 115 336945 8LAKEOVER% 500 1 | TR | 652.8 | 350.1 | 600 | 108.8 |  |  |  |  | 243 | G_1GGNS U1 ID 1+P1_2-1041_8R.BRASWELL%,8LAKEOVER% | 336919 | 336945 | 1 |  | 500 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1041_8R.BRASWELL%,8LAKEOVER% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104799 | 18S | Proposed | P3 | 43 | 336866 6CANTON 230 337015 6PICKENS! 230 1 | LN | 435.1 | 152 | 462 | 94.2 |  |  |  |  | 244 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 336866 | 337015 | 1 |  | 230 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104800 | 18S | Proposed | P3 | 43 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 593.4 | 318.1 | 561 | 105.8 |  |  |  |  | 244 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
104801 | 18S | Proposed | P3 | 43 | 337016 3PICKENS! 115 337018 3MIDWAY MS+ 115 1 | LN | 111.7 | 47 | 108 | 103.4 |  |  |  |  | 244 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337016 | 337018 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104802 | 18S | Proposed | P3 | 43 | 337028 3CONEHOMA 115 337031 3CARTHAGE MS 115 1 | LN | 101.5 | 48.3 | 108 | 93.9 |  |  |  |  | 244 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337031 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed | No violation: below Rate A | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104803 | 18S | Proposed | P3 | 43 | 337028 3CONEHOMA 115 337032 3ATTALA! 115 1 | LN | 113.5 | 60.7 | 108 | 105.1 |  |  |  |  | 244 | G_1GGNS U1 ID 1+P1_2-1088_8LAKEOVER%,8MCADAMS% | 337028 | 337032 | 1 |  | 115 | 115 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1088_8LAKEOVER%,8MCADAMS% | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
104804 | 18S | Proposed | P3 | 43 | 337000 6MCADAMS% 230 337009 8MCADAMS% 500 2 | TR | 634.4 | 318.1 | 561 | 113.1 |  |  |  |  | 248 | G_1ANDRUS U1 ID 1+P1_2-1097_6MCADAMS%,8MCADAMS% | 337000 | 337009 | 2 |  | 500 | 230 | 326 | EES-EMI | 326 | EES-EMI | P1_2-1097_6MCADAMS%,8MCADAMS% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 14-EMI-004-CP | 2020-06-01 | Install McAdams 3rd 500-230 kV autotransformer
104805 | 18S | Proposed | P3 | 43 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | LN | 306 | 174.8 | 266 | 115 |  |  |  |  | 254 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338016 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
104806 | 18S | Proposed | P3 | 43 | 338006 3CABOT 115 338756 3WARD# 115 1 | LN | 267.9 | 135.4 | 266 | 100.7 |  |  |  |  | 254 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338006 | 338756 | 1 |  | 115 | 115 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
104807 | 18S | Proposed | P3 | 43 | 338161 5W.MEMPHIS! 161 338162 8W.MEMPHIS% 500 1 | TR | 443 | 248.8 | 450 | 98.5 |  |  |  |  | 254 | G_1ISES U1 ID 1+P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | 338161 | 338162 | 1 |  | 500 | 161 | 327 | EES-EAI | 327 | EES-EAI | P1_2-1486_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U1 ID 1 | Generation redispatch: Turn on Ritchie unit 500 MW | No violation: below Rate A
104808 | 18S | Proposed | P3 | 43 | 338161 5W.MEMPHIS! 161 338414 5WM POLK AVE 161 1 | LN | 231.1 | 111.3 | 223 | 103.6 |  |  |  |  | 255 | G_1ISES U1 ID 1+P1_2-1500_5EBONY%,5W.MEMPHIS! | 338161 | 338414 | 1 |  | 161 | 161 | 327 | EES-EAI | 334 | WMU | P1_2-1500_5EBONY%,5W.MEMPHIS! | G_1ISES U1 ID 1
104809 | 18S | Proposed | P3 | 43 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 104 | 52.1 | 98 | 106.1 |  |  |  |  | 259 | G_G1DOLHIL! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104810 | 18S | Proposed | P3 | 43 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | LN | 123.4 | 92.4 | 134 | 92.1 |  |  |  |  | 259 | G_G1DOLHIL! ID 1+P1_2-247_4BUNA!,4EVADALE! | 334316 | 334317 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104811 | 18S | Proposed | P3 | 43 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 86.8 | 37.4 | 77 | 112.7 |  |  |  |  | 260 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104812 | 18S | Proposed | P3 | 43 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 90.2 | 38.8 | 77 | 117.1 |  |  |  |  | 260 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104813 | 18S | Proposed | P3 | 43 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 82.9 | 38.2 | 77 | 107.7 |  |  |  |  | 260 | G_G1DOLHIL! ID 1+P1_2-1171_6MONTGOMERY!,CLARN 6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104814 | 18S | Proposed | P3 | 43 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | LN | 100.1 | 52.3 | 111 | 90.2 |  |  |  |  | 261 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337367 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104815 | 18S | Proposed | P3 | 43 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | LN | 117.6 | 67.1 | 115 | 102.3 |  |  |  |  | 261 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 303310 | 337371 | 1 |  | 115 | 115 | 332 | LAGN | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104816 | 18S | Proposed | P3 | 43 | 337304 6MONTGOMERY! 230 500170 CLARN 6 230 1 | LN | 374.1 | 223.4 | 414 | 90.4 |  |  |  |  | 261 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 337304 | 500170 | 1 |  | 230 | 230 | 351 | EES | 502 | CLEC | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 |  | No violation: below Rate A
104817 | 18S | Proposed | P3 | 43 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 72.4 | 38.2 | 77 | 94 |  |  |  |  | 261 | G_G1DOLHIL! ID 1+P1_2-1204_7SAREPTA%,8EL DORADO% | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1204_7SAREPTA%,8EL DORADO% | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104818 | 18S | Proposed | P3 | 43 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 78.3 | 37.4 | 77 | 101.7 |  |  |  |  | 263 | G_G1DOLHIL! ID 1+P1_2-1631_CARROLL6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104819 | 18S | Proposed | P3 | 43 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 81.1 | 38.8 | 77 | 105.3 |  |  |  |  | 263 | G_G1DOLHIL! ID 1+P1_2-1631_CARROLL6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104820 | 18S | Proposed | P3 | 43 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 76 | 38.2 | 77 | 98.7 |  |  |  |  | 263 | G_G1DOLHIL! ID 1+P1_2-1631_CARROLL6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1631_CARROLL6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104821 | 18S | Proposed | P3 | 43 | 337303 3CANE_RIVER! 115 337342 3WINN_PRISON 115 1 | LN | 79 | 37.4 | 77 | 102.5 |  |  |  |  | 264 | G_G1DOLHIL! ID 1+P1_2-1636_CLARN 6!,MESSICK6! | 337303 | 337342 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1636_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104822 | 18S | Proposed | P3 | 43 | 337342 3WINN_PRISON 115 337343 3WINNFIELD! 115 1 | LN | 81.7 | 38.8 | 77 | 106.1 |  |  |  |  | 264 | G_G1DOLHIL! ID 1+P1_2-1636_CLARN 6!,MESSICK6! | 337342 | 337343 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1636_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
104823 | 18S | Proposed | P3 | 43 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | LN | 76.6 | 38.2 | 77 | 99.5 |  |  |  |  | 264 | G_G1DOLHIL! ID 1+P1_2-1636_CLARN 6!,MESSICK6! | 337347 | 337349 | 1 |  | 115 | 115 | 351 | EES | 351 | EES | P1_2-1636_CLARN 6!,MESSICK6! | G_G1DOLHIL! ID 1 | Project External | No violation: below Rate A | Messick 500/230
104824 | 18S | Proposed | P3 | 43 | 500280 ELEESV 6 230 500770 RODEMR 6 230 1 | LN | 397.2 | 245.2 | 386 | 102.9 |  |  |  |  | 265 | G_G1DOLHIL! ID 1+P1_2-1646_COLFAX 6!,RODEMR 6% | 500280 | 500770 | 1 |  | 230 | 230 | 502 | CLEC | 502 | CLEC | P1_2-1646_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 416MVA
104825 | 18S | Proposed | P3 | 43 | 500470 LEESV 6 230 500480 LEESV 4 138 1 | TR | 309.1 | 168 | 336 | 92 |  |  |  |  | 265 | G_G1DOLHIL! ID 1+P1_2-1646_COLFAX 6!,RODEMR 6% | 500470 | 500480 | 1 |  | 230 | 138 | 502 | CLEC | 502 | CLEC | P1_2-1646_COLFAX 6!,RODEMR 6% | G_G1DOLHIL! ID 1 |  | No violation: CLECO facility, loading is less than rate B 370MVA
104826 | 18S | Proposed | P3 | 43 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 106 | 52.1 | 98 | 108.1 |  |  |  |  | 277 | G_PIRKEY 1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_PIRKEY 1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104827 | 18S | Proposed | P3 | 43 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | LN | 121.2 | 92.4 | 134 | 90.5 |  |  |  |  | 277 | G_PIRKEY 1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334316 | 334317 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_PIRKEY 1 ID 1 |  | No violation: below Rate A
104828 | 18S | Proposed | P3 | 43 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 103.4 | 52.1 | 98 | 105.5 |  |  |  |  | 279 | G_WELSH2-1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_WELSH2-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104829 | 18S | Proposed | P3 | 43 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 103.4 | 52.1 | 98 | 105.5 |  |  |  |  | 281 | G_WELSH3-1 ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_WELSH3-1 ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
104830 | 18S | Proposed | P3 | 43 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | LN | 102.5 | 52.1 | 98 | 104.5 |  |  |  |  | 283 | G_TURKCOAL ID 1+P1_2-247_4BUNA!,4EVADALE! | 334282 | 334283 | 1 |  | 138 | 138 | 351 | EES | 351 | EES | P1_2-247_4BUNA!,4EVADALE! | G_TURKCOAL ID 1 | Project Target Area |  | Rayburn-Mill Creek | TBD
200000 | 15S | Approved | P0 | 1 | 5HORN LAKE% | VH |  |  |  |  | 1.0574 | 1.0574 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
200001 | 15S | Approved | P0 | 1 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200002 | 15S | Approved | P0 | 1 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200003 | 15S | Approved | P0 | 1 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
200004 | 15S | Approved | P1 | 1 | 3ROHWER | VL |  |  |  |  | 0.9163 | 0.9674 | 0.92 | 1.05 | 91 | 337597 3DERMOTT+ 115 337599 3MCGEHEE 115 1 | 337601 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337597 3DERMOTT+ 115 337599 3MCGEHEE 115 1 |  | Project Approved | Contingency: invalid, no breakers | 12-EAI-008-02-CP | 2017-06-01 | Macon Lake to Reed: Construct new 230 kV line and operate at 115 kV
200004 | 15S | Approved | P1 | 1 | 3ROHWER | VL |  |  |  |  | 0.9163 | 0.9674 | 0.92 | 1.05 | 91 | 337597 3DERMOTT+ 115 337599 3MCGEHEE 115 1 | 337601 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337597 3DERMOTT+ 115 337599 3MCGEHEE 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
200005 | 15S | Approved | P1 | 1 | 3 34TH&MAIN | VL |  |  |  |  | 0.9162 | 0.9512 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200006 | 15S | Approved | P1 | 1 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9065 | 0.9498 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200007 | 15S | Approved | P1 | 1 | 3MCCAMANT! | VL |  |  |  |  | 0.9041 | 0.9553 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200008 | 15S | Approved | P1 | 1 | 3PINEBLUF.W | VL |  |  |  |  | 0.9041 | 0.9587 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337626 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200009 | 15S | Approved | P1 | 1 | 3PB IP SS% | VL |  |  |  |  | 0.9035 | 0.9436 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200010 | 15S | Approved | P1 | 1 | 3PB IP! | VL |  |  |  |  | 0.9029 | 0.943 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200011 | 15S | Approved | P1 | 1 | 3PB PORT | VL |  |  |  |  | 0.903 | 0.9431 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200012 | 15S | Approved | P1 | 1 | 3PB ENERGY! | VL |  |  |  |  | 0.9029 | 0.943 | 0.92 | 1.05 | 111 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200013 | 15S | Approved | P1 | 1 | 3PB IP SS% | VL |  |  |  |  | 0.9184 | 0.9436 | 0.92 | 1.05 | 122 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200014 | 15S | Approved | P1 | 1 | 3PB IP! | VL |  |  |  |  | 0.9178 | 0.943 | 0.92 | 1.05 | 122 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200015 | 15S | Approved | P1 | 1 | 3PB PORT | VL |  |  |  |  | 0.9179 | 0.9431 | 0.92 | 1.05 | 122 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200016 | 15S | Approved | P1 | 1 | 3PB ENERGY! | VL |  |  |  |  | 0.9178 | 0.943 | 0.92 | 1.05 | 122 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200017 | 15S | Approved | P1 | 1 | 3PB IP SS% | VL |  |  |  |  | 0.9172 | 0.9436 | 0.92 | 1.05 | 123 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200018 | 15S | Approved | P1 | 1 | 3PB IP! | VL |  |  |  |  | 0.9166 | 0.943 | 0.92 | 1.05 | 123 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200019 | 15S | Approved | P1 | 1 | 3PB PORT | VL |  |  |  |  | 0.9167 | 0.9431 | 0.92 | 1.05 | 123 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200020 | 15S | Approved | P1 | 1 | 3PB ENERGY! | VL |  |  |  |  | 0.9166 | 0.943 | 0.92 | 1.05 | 123 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200021 | 15S | Approved | P1 | 1 | 3 34TH&MAIN | VL |  |  |  |  | 0.9162 | 0.9512 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200022 | 15S | Approved | P1 | 1 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9064 | 0.9498 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200023 | 15S | Approved | P1 | 1 | 3MCCAMANT! | VL |  |  |  |  | 0.904 | 0.9553 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200024 | 15S | Approved | P1 | 1 | 3PB IP SS% | VL |  |  |  |  | 0.9035 | 0.9436 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200025 | 15S | Approved | P1 | 1 | 3PB IP! | VL |  |  |  |  | 0.9028 | 0.943 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200026 | 15S | Approved | P1 | 1 | 3PB PORT | VL |  |  |  |  | 0.903 | 0.9431 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200027 | 15S | Approved | P1 | 1 | 3PB ENERGY! | VL |  |  |  |  | 0.9029 | 0.943 | 0.92 | 1.05 | 124 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200028 | 15S | Approved | P1 | 1 | 3PB IP SS% | VL |  |  |  |  | 0.919 | 0.9436 | 0.92 | 1.05 | 145 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200029 | 15S | Approved | P1 | 1 | 3PB IP! | VL |  |  |  |  | 0.9184 | 0.943 | 0.92 | 1.05 | 145 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200030 | 15S | Approved | P1 | 1 | 3PB PORT | VL |  |  |  |  | 0.9185 | 0.9431 | 0.92 | 1.05 | 145 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200031 | 15S | Approved | P1 | 1 | 3PB ENERGY! | VL |  |  |  |  | 0.9184 | 0.943 | 0.92 | 1.05 | 145 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200032 | 15S | Approved | P2 | 1 | 3MALVERN.S | VL |  |  |  |  | 0.9151 | 0.9765 | 0.92 | 1.05 | 196 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337746 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200033 | 15S | Approved | P2 | 1 | 3T.E.P/S-4+ | VL |  |  |  |  | 0.9165 | 0.9755 | 0.92 | 1.05 | 196 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337747 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200034 | 15S | Approved | P2 | 1 | 3T.E.P/S-4 | VL |  |  |  |  | 0.9073 | 0.9674 | 0.92 | 1.05 | 196 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337748 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200035 | 15S | Approved | P2 | 1 | 3BAUCUM | VL |  |  |  |  | 0.9154 | 0.9805 | 0.92 | 1.05 | 317 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 337956 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200036 | 15S | Approved | P2 | 1 | 3KEO# | VL |  |  |  |  | 0.9185 | 0.97 | 0.92 | 1.05 | 317 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 338754 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200037 | 15S | Approved | P2 | 1 | 3STUTGART.N | VL |  |  |  |  | 0.9198 | 0.9891 | 0.92 | 1.05 | 329 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200038 | 15S | Approved | P1 | 1 | 3WABBASEKA | VL |  |  |  |  | 0.9191 | 0.9748 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200039 | 15S | Approved | P1 | 1 | 3STUTGART.N+ | VL |  |  |  |  | 0.9023 | 0.991 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200040 | 15S | Approved | P1 | 1 | 3STUTGART.N | VL |  |  |  |  | 0.9001 | 0.9891 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200041 | 15S | Approved | P1 | 1 | 3RICUSKEY! | VL |  |  |  |  | 0.9019 | 0.9959 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200042 | 15S | Approved | P1 | 1 | 3STUTGART IN | VL |  |  |  |  | 0.9012 | 0.9909 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200043 | 15S | Approved | P1 | 1 | 3ULM | VL |  |  |  |  | 0.9089 | 0.9901 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200044 | 15S | Approved | P1 | 1 | 3ALMYRA | VL |  |  |  |  | 0.8967 | 0.9799 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200045 | 15S | Approved | P1 | 1 | 3DEWITT | VL |  |  |  |  | 0.8962 | 0.971 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200046 | 15S | Approved | P1 | 1 | 3GILLETT! | VL |  |  |  |  | 0.9027 | 0.9695 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200047 | 15S | Approved | P1 | 1 | 3HUMPHREY# | VL |  |  |  |  | 0.909 | 0.982 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200048 | 15S | Approved | P1 | 1 | 3DELUCE# | VL |  |  |  |  | 0.8985 | 0.9681 | 0.92 | 1.05 | 331 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200049 | 15S | Approved | P2 | 1 | 3STUTGART IN | VL |  |  |  |  | 0.899 | 0.9909 | 0.92 | 1.05 | 332 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
200050 | 15S | Approved | P2 | 1 | 3ULM | VL |  |  |  |  | 0.9075 | 0.9901 | 0.92 | 1.05 | 332 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
200051 | 15S | Approved | P2 | 1 | 3ALMYRA | VL |  |  |  |  | 0.7822 | 0.9799 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200052 | 15S | Approved | P2 | 1 | 3DEWITT | VL |  |  |  |  | 0.7857 | 0.971 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200053 | 15S | Approved | P2 | 1 | 3GILLETT! | VL |  |  |  |  | 0.8012 | 0.9695 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200054 | 15S | Approved | P2 | 1 | 3ELAINE | VL |  |  |  |  | 0.8447 | 0.9694 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200055 | 15S | Approved | P2 | 1 | 3MARVELL | VL |  |  |  |  | 0.8768 | 0.9712 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200056 | 15S | Approved | P2 | 1 | 3BARTON | VL |  |  |  |  | 0.8905 | 0.9718 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200057 | 15S | Approved | P2 | 1 | 3HELENA.W+ | VL |  |  |  |  | 0.9175 | 0.9728 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200058 | 15S | Approved | P2 | 1 | 2DELUCE | VL |  |  |  |  | 0.8141 | 0.9929 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200059 | 15S | Approved | P2 | 1 | 3DELUCE# | VL |  |  |  |  | 0.7938 | 0.9681 | 0.92 | 1.05 | 333 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200060 | 15S | Approved | P1 | 1 | 3DEWITT | VL |  |  |  |  | 0.9035 | 0.971 | 0.92 | 1.05 | 338 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200061 | 15S | Approved | P1 | 1 | 3GILLETT! | VL |  |  |  |  | 0.9114 | 0.9695 | 0.92 | 1.05 | 338 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200062 | 15S | Approved | P1 | 1 | 3DELUCE# | VL |  |  |  |  | 0.9067 | 0.9681 | 0.92 | 1.05 | 338 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200063 | 15S | Approved | P1 | 1 | 3ELAINE | VL |  |  |  |  | 0.911 | 0.9694 | 0.92 | 1.05 | 346 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200064 | 15S | Approved | P1 | 1 | 3MARVELL | VL |  |  |  |  | 0.9047 | 0.9712 | 0.92 | 1.05 | 346 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200065 | 15S | Approved | P1 | 1 | 3BARTON | VL |  |  |  |  | 0.9024 | 0.9718 | 0.92 | 1.05 | 346 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200066 | 15S | Approved | P1 | 1 | 3HELENA.W+ | VL |  |  |  |  | 0.8985 | 0.9728 | 0.92 | 1.05 | 346 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200067 | 15S | Approved | P1 | 1 | 3HELENA.C | VL |  |  |  |  | 0.897 | 0.9731 | 0.92 | 1.05 | 346 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200068 | 15S | Approved | P1 | 1 | 3ELAINE | VL |  |  |  |  | 0.897 | 0.9694 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200069 | 15S | Approved | P1 | 1 | 3MARVELL | VL |  |  |  |  | 0.8895 | 0.9712 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200070 | 15S | Approved | P1 | 1 | 3BARTON | VL |  |  |  |  | 0.8869 | 0.9718 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200071 | 15S | Approved | P1 | 1 | 3HELENA.W+ | VL |  |  |  |  | 0.8826 | 0.9728 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200072 | 15S | Approved | P1 | 1 | 3HELENA.C | VL |  |  |  |  | 0.8809 | 0.9731 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200073 | 15S | Approved | P1 | 1 | 3HELENA IN#! | VL |  |  |  |  | 0.8806 | 0.9753 | 0.92 | 1.05 | 349 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200074 | 15S | Approved | P2 | 1 | 3CABOT | VL |  |  |  |  | 0.9113 | 0.9939 | 0.92 | 1.05 | 367 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338006 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 12-EAI-035-CP | 2015-06-01 | Install 21.6 Mvar capacitor bank at Beebe 115 kV
200075 | 15S | Approved | P2 | 1 | 3WARD# | VL |  |  |  |  | 0.909 | 0.9879 | 0.92 | 1.05 | 367 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 12-EAI-035-CP | 2015-06-01 | Install 21.6 Mvar capacitor bank at Beebe 115 kV
200076 | 15S | Approved | P1 | 1 | 3WARD# | VL |  |  |  |  | 0.917 | 0.9879 | 0.92 | 1.05 | 368 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 12-EAI-035-CP | 2015-06-01 | Install 21.6 Mvar capacitor bank at Beebe 115 kV
200076 | 15S | Approved | P1 | 1 | 3WARD# | VL |  |  |  |  | 0.917 | 0.9879 | 0.92 | 1.05 | 368 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200077 | 15S | Approved | P1 | 1 | 2HARRISON.S | VH |  |  |  |  | 1.0561 | 1.0406 | 0.92 | 1.05 | 410 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
200078 | 15S | Approved | P1 | 1 | 8SANS SOUCI% | VH |  |  |  |  | 1.0547 | 1.0363 | 0.92 | 1.05 | 482 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
200079 | 15S | Approved | P1 | 1 | 5POCHNTAS.N | VL |  |  |  |  | 0.876 | 0.9975 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200080 | 15S | Approved | P1 | 1 | 5DATTO | VL |  |  |  |  | 0.8693 | 0.9886 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200081 | 15S | Approved | P1 | 1 | 3DATTO | VL |  |  |  |  | 0.8895 | 1.0115 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200082 | 15S | Approved | P1 | 1 | 3CORNING | VL |  |  |  |  | 0.8838 | 1.0016 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200083 | 15S | Approved | P1 | 1 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8756 | 0.997 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200084 | 15S | Approved | P1 | 1 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8755 | 0.9967 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200085 | 15S | Approved | P1 | 1 | 3CORNING.N# | VL |  |  |  |  | 0.8844 | 1.0027 | 0.92 | 1.05 | 516 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200086 | 15S | Approved | P1 | 1 | 5DATTO | VL |  |  |  |  | 0.8895 | 0.9886 | 0.92 | 1.05 | 517 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200087 | 15S | Approved | P1 | 1 | 3DATTO | VL |  |  |  |  | 0.9167 | 1.0115 | 0.92 | 1.05 | 517 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200088 | 15S | Approved | P1 | 1 | 3CORNING | VL |  |  |  |  | 0.9187 | 1.0016 | 0.92 | 1.05 | 517 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200089 | 15S | Approved | P1 | 1 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8876 | 0.997 | 0.92 | 1.05 | 517 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200090 | 15S | Approved | P1 | 1 | 3CORNING.N# | VL |  |  |  |  | 0.9183 | 1.0027 | 0.92 | 1.05 | 517 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200091 | 15S | Approved | P1 | 1 | 2IMBODEN! | VL |  |  |  |  | 0.8782 | 0.9974 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338221 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200092 | 15S | Approved | P1 | 1 | 2WTR VALLEY! | VL |  |  |  |  | 0.878 | 0.9971 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338222 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200093 | 15S | Approved | P1 | 1 | 5WTR VALLEY+ | VL |  |  |  |  | 0.8775 | 0.9965 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338223 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200094 | 15S | Approved | P1 | 1 | 5WTR VALLEY | VL |  |  |  |  | 0.8775 | 0.9965 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338224 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200095 | 15S | Approved | P1 | 1 | 5POCHNTAS.N | VL |  |  |  |  | 0.8779 | 0.9975 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200096 | 15S | Approved | P1 | 1 | 5DATTO | VL |  |  |  |  | 0.8709 | 0.9886 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200097 | 15S | Approved | P1 | 1 | 3DATTO | VL |  |  |  |  | 0.891 | 1.0115 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200098 | 15S | Approved | P1 | 1 | 3CORNING | VL |  |  |  |  | 0.885 | 1.0016 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200099 | 15S | Approved | P1 | 1 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8775 | 0.997 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200100 | 15S | Approved | P1 | 1 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8775 | 0.9967 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200101 | 15S | Approved | P1 | 1 | 3CORNING.N# | VL |  |  |  |  | 0.8856 | 1.0027 | 0.92 | 1.05 | 676 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200102 | 15S | Approved | P1 | 1 | 2CALVERT! | VL |  |  |  |  | 0.8467 | 0.9807 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200103 | 15S | Approved | P1 | 1 | 2SINHERN | VL |  |  |  |  | 0.8794 | 1.0002 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200104 | 15S | Approved | P1 | 1 | 2HEARNE! | VL |  |  |  |  | 0.911 | 1.019 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200105 | 15S | Approved | P1 | 1 | 2TXHEARN | VL |  |  |  |  | 0.9112 | 1.0195 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200106 | 15S | Approved | P1 | 1 | 2APLHERN | VL |  |  |  |  | 0.9118 | 1.021 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200107 | 15S | Approved | P1 | 1 | 2BRYAN A! | VL |  |  |  |  | 0.9168 | 1.028 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200108 | 15S | Approved | P1 | 1 | 2HUMBHRN | VL |  |  |  |  | 0.9178 | 1.0195 | 0.92 | 1.05 | 690 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200109 | 15S | Approved | P1 | 1 | 4FISHCRK | VL |  |  |  |  | 0.9054 | 0.9863 | 0.92 | 1.05 | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334045 |  |  |  | 138 | 138 | 351 | EES |  |  | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
200110 | 15S | Approved | P1 | 1 | 4SPRINGBRNCH | VL |  |  |  |  | 0.9146 | 0.9855 | 0.92 | 1.05 | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334046 |  |  |  | 138 | 138 | 351 | EES |  |  | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
200111 | 15S | Approved | P1 | 1 | 4EGYPT | VL |  |  |  |  | 0.901 | 0.9926 | 0.92 | 1.05 | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334073 |  |  |  | 138 | 138 | 351 | EES |  |  | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
200112 | 15S | Approved | P1 | 1 | 4PANORAM | VL |  |  |  |  | 0.9016 | 0.9909 | 0.92 | 1.05 | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334074 |  |  |  | 138 | 138 | 351 | EES |  |  | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
200113 | 15S | Approved | P1 | 1 | 4LONGMIR! | VL |  |  |  |  | 0.9036 | 0.9872 | 0.92 | 1.05 | 746 | 334072 4LEWIS% 138 334073 4EGYPT 138 1 | 334075 |  |  |  | 138 | 138 | 351 | EES |  |  | 334072 4LEWIS% 138 334073 4EGYPT 138 1 |  | Project Proposed |  | 12-ETI-004-CP | 2013-12-01 | Construct Ponderosa 138 kV Switching Station: tie Longmire-Fish Creek and Conroe-Woodhaven
200114 | 15S | Approved | P1 | 1 | 4MILLCR! | VL |  |  |  |  | 0.916 | 0.9955 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200115 | 15S | Approved | P1 | 1 | 4PINELND | VL |  |  |  |  | 0.9108 | 0.9798 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200116 | 15S | Approved | P1 | 1 | 4BROADUS | VL |  |  |  |  | 0.9069 | 0.9764 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200117 | 15S | Approved | P1 | 1 | 4ETOIL | VL |  |  |  |  | 0.9054 | 0.9751 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200118 | 15S | Approved | P1 | 1 | 4HRTNHIL | VL |  |  |  |  | 0.9123 | 0.9867 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200119 | 15S | Approved | P1 | 1 | 2WEIRGAT | VL |  |  |  |  | 0.9149 | 0.9778 | 0.92 | 1.05 | 883 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200120 | 15S | Approved | P1 | 1 | 2SABRA | VL |  |  |  |  | 0.9176 | 0.9903 | 0.92 | 1.05 | 1142 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334704 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
200121 | 15S | Approved | P1 | 1 | 2DEWEYVL! | VL |  |  |  |  | 0.9183 | 0.9827 | 0.92 | 1.05 | 1142 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
200122 | 15S | Approved | P1 | 1 | 2SKBVREG | VL |  |  |  |  | 0.9199 | 0.9844 | 0.92 | 1.05 | 1142 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
200123 | 15S | Approved | P1 | 1 | 4LEBLANC! | VL |  |  |  |  | 0.9172 | 0.9705 | 0.92 | 1.05 | 1382 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
200124 | 15S | Approved | P1 | 1 | 4DELCAMBRE | VL |  |  |  |  | 0.9167 | 0.975 | 0.92 | 1.05 | 1382 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
200125 | 15S | Approved | P1 | 1 | 2ST_MARTIN | VL |  |  |  |  | 0.9195 | 0.9573 | 0.92 | 1.05 | 1394 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
200126 | 15S | Approved | P1 | 1 | LONGFL 2 | VL |  |  |  |  | 0.9195 | 0.9573 | 0.92 | 1.05 | 1394 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
200127 | 15S | Approved | P1 | 1 | 2LINE-625_OP | VL |  |  |  |  | 0.9124 | 0.9622 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
200127 | 15S | Approved | P1 | 1 | 2LINE-625_OP | VL |  |  |  |  | 0.9124 | 0.9622 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
200128 | 15S | Approved | P1 | 1 | 2ST_MARTIN | VL |  |  |  |  | 0.9072 | 0.9573 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
200128 | 15S | Approved | P1 | 1 | 2ST_MARTIN | VL |  |  |  |  | 0.9072 | 0.9573 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
200129 | 15S | Approved | P1 | 1 | LONGFL 2 | VL |  |  |  |  | 0.9072 | 0.9573 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
200129 | 15S | Approved | P1 | 1 | LONGFL 2 | VL |  |  |  |  | 0.9072 | 0.9573 | 0.92 | 1.05 | 1396 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
200130 | 15S | Approved | P1 | 1 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9122 | 0.9628 | 0.92 | 1.05 | 1423 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200131 | 15S | Approved | P1 | 1 | 4BOBCAT | VL |  |  |  |  | 0.9086 | 0.9702 | 0.92 | 1.05 | 1423 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200132 | 15S | Approved | P1 | 1 | 4LINE-642_TP | VL |  |  |  |  | 0.9123 | 0.9628 | 0.92 | 1.05 | 1423 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200133 | 15S | Approved | P1 | 1 | 4COL_SPRINGS | VL |  |  |  |  | 0.9122 | 0.9628 | 0.92 | 1.05 | 1423 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200134 | 15S | Approved | P1 | 1 | 2NESSER_TP | VL |  |  |  |  | 0.8875 | 0.9718 | 0.92 | 1.05 | 1560 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
200135 | 15S | Approved | P1 | 1 | 2NESSER | VL |  |  |  |  | 0.8826 | 0.9674 | 0.92 | 1.05 | 1560 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
200136 | 15S | Approved | P1 | 1 | 2LN-372A_TP | VL |  |  |  |  | 0.9024 | 0.9853 | 0.92 | 1.05 | 1560 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335710 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
200137 | 15S | Approved | P1 | 1 | 2JONESCREEK! | VL |  |  |  |  | 0.9057 | 0.9823 | 0.92 | 1.05 | 1560 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
200138 | 15S | Approved | P1 | 1 | 2FRANCIS! | VH |  |  |  |  | 1.0514 | 1.0206 | 0.92 | 1.05 | 1632 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200139 | 15S | Approved | P2 | 1 | 3LEEVLL | VL |  |  |  |  | 0.8944 | 1.0009 | 0.92 | 1.05 | 1707 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  | None
200140 | 15S | Approved | P2 | 1 | 3FOURCHN | VL |  |  |  |  | 0.8839 | 0.9915 | 0.92 | 1.05 | 1707 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  | None
200141 | 15S | Approved | P1 | 1 | 3CARLSL | VL |  |  |  |  | 0.8841 | 0.9845 | 0.92 | 1.05 | 1717 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
200142 | 15S | Approved | P1 | 1 | 3LORMAN+ | VL |  |  |  |  | 0.9129 | 1.0179 | 0.92 | 1.05 | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200143 | 15S | Approved | P1 | 1 | 3LORMAN | VL |  |  |  |  | 0.9127 | 1.0177 | 0.92 | 1.05 | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200144 | 15S | Approved | P1 | 1 | 3PORTGIBSON! | VL |  |  |  |  | 0.9007 | 1.0169 | 0.92 | 1.05 | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200145 | 15S | Approved | P1 | 1 | 3GGNS | VL |  |  |  |  | 0.8995 | 1.0159 | 0.975 | 1.05 | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200146 | 15S | Approved | P1 | 1 | 3S.VICKSBURG | VL |  |  |  |  | 0.8958 | 1.0189 | 0.92 | 1.05 | 1941 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200148 | 15S | Approved | P1 | 1 | 3ROLING FRK! | VH |  |  |  |  | 1.0507 | 0.9995 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336968 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200149 | 15S | Approved | P1 | 1 | 3NITTA YUMA+ | VH |  |  |  |  | 1.057 | 0.9946 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336970 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200150 | 15S | Approved | P1 | 1 | 3MURPHY+ | VH |  |  |  |  | 1.0636 | 0.9901 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336992 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200151 | 15S | Approved | P1 | 1 | 3GREENVILLE+ | VH |  |  |  |  | 1.0531 | 1.0042 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200152 | 15S | Approved | P1 | 1 | 3HOLLANDALE | VH |  |  |  |  | 1.0652 | 0.9919 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337048 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200153 | 15S | Approved | P1 | 1 | 3ARCOLA+ | VH |  |  |  |  | 1.0584 | 0.9973 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200154 | 15S | Approved | P1 | 1 | 3SWIFTWATER | VH |  |  |  |  | 1.0525 | 1.0036 | 0.92 | 1.05 | 2117 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200155 | 15S | Approved | P1 | 1 | 3JNESBORO_LA | VL |  |  |  |  | 0.8712 | 1.0069 | 0.92 | 1.05 | 2238 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337346 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
200156 | 15S | Approved | P1 | 1 | 3HODGE_LA! | VL |  |  |  |  | 0.8724 | 1.0059 | 0.92 | 1.05 | 2238 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
200157 | 15S | Approved | P1 | 1 | 3MINDEN_LG | VL |  |  |  |  | 0.9146 | 0.9856 | 0.92 | 1.05 | 2444 | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 |  | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
200158 | 15S | Approved | P1 | 1 | 3GILBERT | VL |  |  |  |  | 0.9132 | 1.0224 | 0.92 | 1.05 | 2461 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
200159 | 15S | Approved | P1 | 1 | 3WINNSBORO! | VL |  |  |  |  | 0.8991 | 1.0112 | 0.92 | 1.05 | 2461 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
200160 | 15S | Approved | P1 | 1 | 3GILBERT | VH |  |  |  |  | 1.0506 | 1.0224 | 0.92 | 1.05 | 2462 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | VH
200161 | 15S | Approved | P1 | 1 | 3METROPOLIS | VH |  |  |  |  | 1.0509 | 1.0296 | 0.92 | 1.05 | 2462 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200162 | 15S | Approved | P1 | 1 | 3WISNER | VH |  |  |  |  | 1.053 | 1.03 | 0.92 | 1.05 | 2462 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200163 | 15S | Approved | P1 | 1 | 4CANEY | VL |  |  |  |  | 0.8787 | 0.9964 | 0.92 | 1.05 | 2638 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
200164 | 15S | Approved | P1 | 1 | OAKDALE4 | VL |  |  |  |  | 0.8806 | 0.9947 | 0.92 | 1.05 | 2638 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
200165 | 15S | Approved | P1 | 1 | PNPRARIE 4 | VL |  |  |  |  | 0.8716 | 1.0078 | 0.92 | 1.05 | 2638 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
200166 | 15S | Approved | P1 | 1 | WSTBAY 4 | VL |  |  |  |  | 0.8923 | 0.9938 | 0.92 | 1.05 | 2638 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
200170 | 15S | Approved | P1 | 1 | ELKS 6 | VL |  |  |  |  | 0.9185 | 0.9875 | 0.92 | 1.05 | 2731 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  | turn on switch shunt at BEADLE 230kV sub
200171 | 15S | Approved | P1 | 1 | BEADLE 6 | VL |  |  |  |  | 0.9191 | 0.9886 | 0.92 | 1.05 | 2731 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1
200172 | 15S | Approved | P1 | 1 | ELKS 6 | VL |  |  |  |  | 0.903 | 0.9875 | 0.92 | 1.05 | 2755 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
200173 | 15S | Approved | P1 | 1 | 8MCCALL RD | VH |  |  |  |  | 1.0677 | 1.0372 | 0.92 | 1.05 | 2847 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
200174 | 15S | Approved | P1 | 1 | 8DANIEL | VH |  |  |  |  | 1.0742 | 1.0444 | 0.92 | 1.05 | 3560 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
200175 | 15S | Approved | P1 | 1 | 7SHAWNEE FP | VH |  |  |  |  | 1.051 | 1.0386 | 0.92 | 1.05 | 3860 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
200176 | 15S | Approved | P1 | 1 | TENRUSK7 | VH |  |  |  |  | 1.0524 | 1.019 | 0.92 | 1.05 | 4538 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
200177 | 15S | Approved | P1 | 1 | TENGEN 7 | VH |  |  |  |  | 1.0524 | 1.019 | 0.92 | 1.05 | 4538 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
200178 | 15S | Approved | P0 | 2 | 5HORN LAKE% | VH |  |  |  |  | 1.0574 | 1.0574 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
200179 | 15S | Approved | P0 | 2 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200180 | 15S | Approved | P0 | 2 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200181 | 15S | Approved | P0 | 2 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
200182 | 15S | Approved | P1 | 2 | 2TUPPER | VL |  |  |  |  | 0.914 | 1.0105 | 0.92 | 1.05 | 319 | P1_2-92 | 335256 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-92 |  |  | Solution: Adjust caps
200183 | 15S | Approved | P1 | 2 | 2ELTON! | VL |  |  |  |  | 0.9151 | 1.0116 | 0.92 | 1.05 | 319 | P1_2-92 | 335257 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-92 |  |  | Solution: Adjust caps
200184 | 15S | Approved | P1 | 2 | 2CALVERT! | VL |  |  |  |  | 0.7924 | 0.9807 | 0.92 | 1.05 | 352 | P1_2-125 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200185 | 15S | Approved | P1 | 2 | 2SINHERN | VL |  |  |  |  | 0.8328 | 1.0002 | 0.92 | 1.05 | 352 | P1_2-125 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200186 | 15S | Approved | P1 | 2 | 2HEARNE! | VL |  |  |  |  | 0.8697 | 1.019 | 0.92 | 1.05 | 352 | P1_2-125 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200187 | 15S | Approved | P1 | 2 | 2TXHEARN | VL |  |  |  |  | 0.8697 | 1.0195 | 0.92 | 1.05 | 352 | P1_2-125 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200188 | 15S | Approved | P1 | 2 | 2APLHERN | VL |  |  |  |  | 0.8694 | 1.021 | 0.92 | 1.05 | 352 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200189 | 15S | Approved | P1 | 2 | 2BRYAN A! | VL |  |  |  |  | 0.8696 | 1.028 | 0.92 | 1.05 | 352 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200190 | 15S | Approved | P1 | 2 | 2HUMBHRN | VL |  |  |  |  | 0.8803 | 1.0195 | 0.92 | 1.05 | 352 | P1_2-125 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
200191 | 15S | Approved | P1 | 2 | 4MILLCR! | VL |  |  |  |  | 0.916 | 0.9955 | 0.92 | 1.05 | 458 | P1_2-231 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200192 | 15S | Approved | P1 | 2 | 4PINELND | VL |  |  |  |  | 0.9108 | 0.9798 | 0.92 | 1.05 | 458 | P1_2-231 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200193 | 15S | Approved | P1 | 2 | 4BROADUS | VL |  |  |  |  | 0.9069 | 0.9764 | 0.92 | 1.05 | 458 | P1_2-231 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200194 | 15S | Approved | P1 | 2 | 4ETOIL | VL |  |  |  |  | 0.9054 | 0.9751 | 0.92 | 1.05 | 458 | P1_2-231 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200195 | 15S | Approved | P1 | 2 | 4HRTNHIL | VL |  |  |  |  | 0.9123 | 0.9867 | 0.92 | 1.05 | 458 | P1_2-231 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200196 | 15S | Approved | P1 | 2 | 2WEIRGAT | VL |  |  |  |  | 0.9149 | 0.9778 | 0.92 | 1.05 | 458 | P1_2-231 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200197 | 15S | Approved | P1 | 2 | 2ST_MARTIN | VL |  |  |  |  | 0.9194 | 0.9573 | 0.92 | 1.05 | 800 | P1_2-573 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-573 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
200198 | 15S | Approved | P1 | 2 | LONGFL 2 | VL |  |  |  |  | 0.9194 | 0.9573 | 0.92 | 1.05 | 800 | P1_2-573 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-573 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
200199 | 15S | Approved | P1 | 2 | 3LEEVLL | VL |  |  |  |  | 0.8944 | 1.0009 | 0.92 | 1.05 | 1029 | P1_2-802 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
200200 | 15S | Approved | P1 | 2 | 3FOURCHN | VL |  |  |  |  | 0.8839 | 0.9915 | 0.92 | 1.05 | 1029 | P1_2-802 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  | Project Proposed |  | 11-ELL-012-CP | 2015-06-01 | Upgrade Valentine-Clovelly 115 kV
200201 | 15S | Approved | P1 | 2 | 8GGNS% | VL |  |  |  |  | 0.9793 | 1.0157 | 0.982 | 1.05 | 1255 | P1_2-1028 | 336820 |  |  |  | 500 | 500 | 326 | EES-EMI |  |  | P1_2-1028_8GGNS%,8BXTRWILSON% |  | None
200202 | 15S | Approved | P1 | 2 | 3GILBERT | VL |  |  |  |  | 0.9134 | 1.0224 | 0.92 | 1.05 | 1400 | P1_2-1173 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200203 | 15S | Approved | P1 | 2 | 3WINNSBORO! | VL |  |  |  |  | 0.8994 | 1.0112 | 0.92 | 1.05 | 1400 | P1_2-1173 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200204 | 15S | Approved | P1 | 2 | 3 34TH&MAIN | VL |  |  |  |  | 0.9159 | 0.9512 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200205 | 15S | Approved | P1 | 2 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9062 | 0.9498 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200206 | 15S | Approved | P1 | 2 | 3MCCAMANT! | VL |  |  |  |  | 0.9038 | 0.9553 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200207 | 15S | Approved | P1 | 2 | 3PB IP SS% | VL |  |  |  |  | 0.9032 | 0.9436 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200208 | 15S | Approved | P1 | 2 | 3PB IP! | VL |  |  |  |  | 0.9026 | 0.943 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200209 | 15S | Approved | P1 | 2 | 3PB PORT | VL |  |  |  |  | 0.9027 | 0.9431 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200210 | 15S | Approved | P1 | 2 | 3PB ENERGY! | VL |  |  |  |  | 0.9026 | 0.943 | 0.92 | 1.05 | 1515 | P1_2-1288 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1288 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200211 | 15S | Approved | P1 | 2 | 3PB IP SS% | VL |  |  |  |  | 0.9167 | 0.9436 | 0.92 | 1.05 | 1524 | P1_2-1297 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1297 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200212 | 15S | Approved | P1 | 2 | 3PB IP! | VL |  |  |  |  | 0.9161 | 0.943 | 0.92 | 1.05 | 1524 | P1_2-1297 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1297 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200213 | 15S | Approved | P1 | 2 | 3PB PORT | VL |  |  |  |  | 0.9162 | 0.9431 | 0.92 | 1.05 | 1524 | P1_2-1297 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1297 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200214 | 15S | Approved | P1 | 2 | 3PB ENERGY! | VL |  |  |  |  | 0.9161 | 0.943 | 0.92 | 1.05 | 1524 | P1_2-1297 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1297 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200215 | 15S | Approved | P1 | 2 | 3PB IP SS% | VL |  |  |  |  | 0.9156 | 0.9436 | 0.92 | 1.05 | 1525 | P1_2-1298 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1298 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200216 | 15S | Approved | P1 | 2 | 3PB IP! | VL |  |  |  |  | 0.915 | 0.943 | 0.92 | 1.05 | 1525 | P1_2-1298 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1298 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200217 | 15S | Approved | P1 | 2 | 3PB PORT | VL |  |  |  |  | 0.9151 | 0.9431 | 0.92 | 1.05 | 1525 | P1_2-1298 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1298 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200218 | 15S | Approved | P1 | 2 | 3PB ENERGY! | VL |  |  |  |  | 0.915 | 0.943 | 0.92 | 1.05 | 1525 | P1_2-1298 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1298 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200219 | 15S | Approved | P1 | 2 | 3PB IP SS% | VL |  |  |  |  | 0.919 | 0.9436 | 0.92 | 1.05 | 1535 | P1_2-1308 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200220 | 15S | Approved | P1 | 2 | 3PB IP! | VL |  |  |  |  | 0.9184 | 0.943 | 0.92 | 1.05 | 1535 | P1_2-1308 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200221 | 15S | Approved | P1 | 2 | 3PB PORT | VL |  |  |  |  | 0.9186 | 0.9431 | 0.92 | 1.05 | 1535 | P1_2-1308 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200222 | 15S | Approved | P1 | 2 | 3PB ENERGY! | VL |  |  |  |  | 0.9185 | 0.943 | 0.92 | 1.05 | 1535 | P1_2-1308 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200223 | 15S | Approved | P1 | 2 | 3STUTGART.N+ | VL |  |  |  |  | 0.9051 | 0.991 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200224 | 15S | Approved | P1 | 2 | 3STUTGART.N | VL |  |  |  |  | 0.903 | 0.9891 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200225 | 15S | Approved | P1 | 2 | 3RICUSKEY! | VL |  |  |  |  | 0.9047 | 0.9959 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200226 | 15S | Approved | P1 | 2 | 3STUTGART IN | VL |  |  |  |  | 0.9042 | 0.9909 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200227 | 15S | Approved | P1 | 2 | 3ULM | VL |  |  |  |  | 0.9118 | 0.9901 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200228 | 15S | Approved | P1 | 2 | 3ALMYRA | VL |  |  |  |  | 0.8997 | 0.9799 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200229 | 15S | Approved | P1 | 2 | 3DEWITT | VL |  |  |  |  | 0.8993 | 0.971 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200230 | 15S | Approved | P1 | 2 | 3GILLETT! | VL |  |  |  |  | 0.9061 | 0.9695 | 0.92 | 1.05 | 1663 | P1_2-1436 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200231 | 15S | Approved | P1 | 2 | 3HUMPHREY# | VL |  |  |  |  | 0.9116 | 0.982 | 0.92 | 1.05 | 1663 | P1_2-1436 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200232 | 15S | Approved | P1 | 2 | 3DELUCE# | VL |  |  |  |  | 0.9019 | 0.9681 | 0.92 | 1.05 | 1663 | P1_2-1436 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200233 | 15S | Approved | P1 | 2 | 3ELAINE | VL |  |  |  |  | 0.8954 | 0.9694 | 0.92 | 1.05 | 1670 | P1_2-1443 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200234 | 15S | Approved | P1 | 2 | 3MARVELL | VL |  |  |  |  | 0.8877 | 0.9712 | 0.92 | 1.05 | 1670 | P1_2-1443 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200235 | 15S | Approved | P1 | 2 | 3BARTON | VL |  |  |  |  | 0.885 | 0.9718 | 0.92 | 1.05 | 1670 | P1_2-1443 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200236 | 15S | Approved | P1 | 2 | 3HELENA.W+ | VL |  |  |  |  | 0.8806 | 0.9728 | 0.92 | 1.05 | 1670 | P1_2-1443 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200237 | 15S | Approved | P1 | 2 | 3HELENA.C | VL |  |  |  |  | 0.8789 | 0.9731 | 0.92 | 1.05 | 1670 | P1_2-1443 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200238 | 15S | Approved | P1 | 2 | 3HELENA IN#! | VL |  |  |  |  | 0.8786 | 0.9753 | 0.92 | 1.05 | 1670 | P1_2-1443 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200239 | 15S | Approved | P1 | 2 | 8SANS SOUCI% | VH |  |  |  |  | 1.0546 | 1.0363 | 0.92 | 1.05 | 1738 | P1_2-1514 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1514 |  |  | VH
200240 | 15S | Approved | P1 | 2 | 8DANIEL | VH |  |  |  |  | 1.0742 | 1.0444 | 0.92 | 1.05 | 1823 | P1_2-1599 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1599 |  |  | VH
200241 | 15S | Approved | P1 | 2 | 4CANEY | VL |  |  |  |  | 0.8788 | 0.9964 | 0.92 | 1.05 | 1872 | P1_2-1648 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648
200242 | 15S | Approved | P1 | 2 | OAKDALE4 | VL |  |  |  |  | 0.8807 | 0.9947 | 0.92 | 1.05 | 1872 | P1_2-1648 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
200243 | 15S | Approved | P1 | 2 | PNPRARIE 4 | VL |  |  |  |  | 0.8717 | 1.0078 | 0.92 | 1.05 | 1872 | P1_2-1648 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
200244 | 15S | Approved | P1 | 2 | WSTBAY 4 | VL |  |  |  |  | 0.8924 | 0.9938 | 0.92 | 1.05 | 1872 | P1_2-1648 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
200245 | 15S | Approved | P1 | 2 | 4VEAZIE | VL |  |  |  |  | 0.894 | 0.9785 | 0.92 | 1.05 | 1873 | P1_2-1649 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200246 | 15S | Approved | P1 | 2 | GUIDRY 4 | VL |  |  |  |  | 0.8926 | 0.9773 | 0.92 | 1.05 | 1873 | P1_2-1649 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200247 | 15S | Approved | P1 | 2 | PLAISAN4 | VL |  |  |  |  | 0.9075 | 0.9909 | 0.92 | 1.05 | 1873 | P1_2-1649 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
200248 | 15S | Approved | P1 | 2 | TENRUSK7 | VH |  |  |  |  | 1.0524 | 1.019 | 0.92 | 1.05 | 2082 | P1_2-1858 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1858 |  |  | VH
200249 | 15S | Approved | P1 | 2 | TENGEN 7 | VH |  |  |  |  | 1.0524 | 1.019 | 0.92 | 1.05 | 2082 | P1_2-1858 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1858 |  |  | VH
200250 | 18L | Approved | P0 | 3 | 8GPDELL | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
200251 | 18L | Approved | P0 | 3 | 7GOBKNOB | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 | 0 | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
200252 | 18L | Approved | P0 | 3 | 2BATSON! | VH |  |  |  |  | 1.0536 | 1.0536 | 0.92 | 1.05 | 0 | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
200253 | 18L | Approved | P0 | 3 | 26L102TAP | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 334256 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
200254 | 18L | Approved | P0 | 3 | 5HORN LAKE% | VH |  |  |  |  | 1.0667 | 1.0667 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
200255 | 18L | Approved | P0 | 3 | 8DELL% | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200256 | 18L | Approved | P0 | 3 | 8SANS SOUCI% | VH |  |  |  |  | 1.0614 | 1.0614 | 0.92 | 1.05 | 0 | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200257 | 18L | Approved | P0 | 3 | 3PARAGOULD! | VH |  |  |  |  | 1.0589 | 1.0589 | 0.92 | 1.05 | 0 | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200258 | 18L | Approved | P0 | 3 | 2BLACK ROCK | VH |  |  |  |  | 1.0691 | 1.0691 | 0.92 | 1.05 | 0 | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200259 | 18L | Approved | P0 | 3 | 2OPPELLO | VH |  |  |  |  | 1.0526 | 1.0526 | 0.92 | 1.05 | 0 | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200260 | 18L | Approved | P0 | 3 | 5DELL# | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200261 | 18L | Approved | P0 | 3 | 3LIGHT# | VH |  |  |  |  | 1.0517 | 1.0517 | 0.92 | 1.05 | 0 | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200262 | 18L | Approved | P0 | 3 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0549 | 1.0549 | 0.92 | 1.05 | 0 | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200263 | 18L | Approved | P0 | 3 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 | 0 | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200264 | 18L | Approved | P0 | 3 | 7SHAWNEE FP | VH |  |  |  |  | 1.0765 | 1.0765 | 0.92 | 1.05 | 0 | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200265 | 18L | Approved | P0 | 3 | 8RUTHERFORD | VH |  |  |  |  | 1.0685 | 1.0685 | 0.92 | 1.05 | 0 | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200266 | 18L | Approved | P0 | 3 | 8MARSHALL KY | VH |  |  |  |  | 1.0817 | 1.0817 | 0.92 | 1.05 | 0 | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200267 | 18L | Approved | P0 | 3 | 8WEAKLEY TN | VH |  |  |  |  | 1.0777 | 1.0777 | 0.92 | 1.05 | 0 | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200268 | 18L | Approved | P0 | 3 | 8JACKSON TN | VH |  |  |  |  | 1.0665 | 1.0665 | 0.92 | 1.05 | 0 | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200269 | 18L | Approved | P0 | 3 | 8SHELBY TN | VH |  |  |  |  | 1.0602 | 1.0602 | 0.92 | 1.05 | 0 | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200270 | 18L | Approved | P0 | 3 | 8CORDOVA TN | VH |  |  |  |  | 1.0556 | 1.0556 | 0.92 | 1.05 | 0 | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200271 | 18L | Approved | P0 | 3 | 8JVILLE FP | VH |  |  |  |  | 1.0824 | 1.0824 | 0.92 | 1.05 | 0 | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200272 | 18L | Approved | P0 | 3 | 8CUMBERLAND | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 | 0 | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200273 | 18L | Approved | P0 | 3 | 8PARADISE FP | VH |  |  |  |  | 1.0869 | 1.0869 | 0.92 | 1.05 | 0 | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200274 | 18L | Approved | P0 | 3 | 8MONTGOMERY | VH |  |  |  |  | 1.0805 | 1.0805 | 0.92 | 1.05 | 0 | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200275 | 18L | Approved | P0 | 3 | 8DAVIDSON TN | VH |  |  |  |  | 1.0796 | 1.0796 | 0.92 | 1.05 | 0 | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200276 | 18L | Approved | P0 | 3 | 8MAURY TN | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 | 0 | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200277 | 18L | Approved | P0 | 3 | 8FRANKLIN TN | VH |  |  |  |  | 1.0522 | 1.0522 | 0.92 | 1.05 | 0 | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200278 | 18L | Approved | P0 | 3 | 8WILSON TN | VH |  |  |  |  | 1.0767 | 1.0767 | 0.92 | 1.05 | 0 | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200279 | 18L | Approved | P0 | 3 | 8PLATEAU TN | VH |  |  |  |  | 1.0611 | 1.0611 | 0.92 | 1.05 | 0 | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200280 | 18L | Approved | P0 | 3 | 8BULL RUN FP | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 | 0 | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200281 | 18L | Approved | P0 | 3 | 8VOLUNTEER | VH |  |  |  |  | 1.0562 | 1.0562 | 0.92 | 1.05 | 0 | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200282 | 18L | Approved | P0 | 3 | 8PHIPPS B NP | VH |  |  |  |  | 1.0674 | 1.0674 | 0.92 | 1.05 | 0 | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200283 | 18L | Approved | P0 | 3 | 8SULLIVAN TN | VH |  |  |  |  | 1.0608 | 1.0608 | 0.92 | 1.05 | 0 | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200284 | 18L | Approved | P0 | 3 | 8PLEASANT HL | VH |  |  |  |  | 1.0524 | 1.0524 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200285 | 18L | Approved | P0 | 3 | 8HAYWOOD TN | VH |  |  |  |  | 1.0647 | 1.0647 | 0.92 | 1.05 | 0 | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200286 | 18L | Approved | P0 | 3 | 8LAG CRK CT | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 | 0 | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200287 | 18L | Approved | P0 | 3 | 8PIN HOOK TN | VH |  |  |  |  | 1.0775 | 1.0775 | 0.92 | 1.05 | 0 | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200288 | 18L | Approved | P0 | 3 | 8GLEASON CT | VH |  |  |  |  | 1.0802 | 1.0802 | 0.92 | 1.05 | 0 | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200289 | 18L | Approved | P0 | 3 | 8BENTON MS | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200290 | 18L | Approved | P0 | 3 | 8MAGNOL CC1 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200291 | 18L | Approved | P0 | 3 | 8MAGNOL CC2 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200292 | 18L | Approved | P0 | 3 | 8LAG CRK CC | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 | 0 | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200293 | 18L | Approved | P1 | 3 | 3BLACK_RIV | VH |  |  |  |  | 1.096 | 0.9963 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200294 | 18L | Approved | P1 | 3 | 3GILBERT | VH |  |  |  |  | 1.1285 | 1.0234 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200295 | 18L | Approved | P1 | 3 | 3PERSIM_MIL | VH |  |  |  |  | 1.1209 | 1.0237 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200296 | 18L | Approved | P1 | 3 | 3BASKIN | VH |  |  |  |  | 1.0962 | 1.0183 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200297 | 18L | Approved | P1 | 3 | 3NATCHEZSES% | VH |  |  |  |  | 1.1481 | 1.034 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200298 | 18L | Approved | P1 | 3 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1473 | 1.034 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200299 | 18L | Approved | P1 | 3 | 3PINE RIDGE | VH |  |  |  |  | 1.1471 | 1.0339 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200300 | 18L | Approved | P1 | 3 | 3NATCHEZ! | VH |  |  |  |  | 1.1453 | 1.0347 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200301 | 18L | Approved | P1 | 3 | 3J.MANVILLE | VH |  |  |  |  | 1.1425 | 1.0333 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200302 | 18L | Approved | P1 | 3 | 3INTL PAPER | VH |  |  |  |  | 1.1404 | 1.0328 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200303 | 18L | Approved | P1 | 3 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1389 | 1.0324 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200304 | 18L | Approved | P1 | 3 | 3NATCHEZ IND | VH |  |  |  |  | 1.1352 | 1.0315 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200305 | 18L | Approved | P1 | 3 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1377 | 1.032 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200306 | 18L | Approved | P1 | 3 | 3CROSBY+ | VH |  |  |  |  | 1.1153 | 1.0276 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200307 | 18L | Approved | P1 | 3 | 3GLOSTER | VH |  |  |  |  | 1.1087 | 1.0265 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200308 | 18L | Approved | P1 | 3 | 3LIBERTY P/L | VH |  |  |  |  | 1.0768 | 1.0357 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200309 | 18L | Approved | P1 | 3 | 3WOODVILLE | VH |  |  |  |  | 1.0893 | 1.0052 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200310 | 18L | Approved | P1 | 3 | 3LIBERTY! | VH |  |  |  |  | 1.0769 | 1.0357 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200311 | 18L | Approved | P1 | 3 | 3INTRSTE P/L | VH |  |  |  |  | 1.0769 | 1.0357 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200312 | 18L | Approved | P1 | 3 | 3GILLSBURG+ | VH |  |  |  |  | 1.0546 | 1.0259 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336517 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200313 | 18L | Approved | P1 | 3 | 3GILLSBURG | VH |  |  |  |  | 1.053 | 1.0243 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336518 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200314 | 18L | Approved | P1 | 3 | 3KINGSTON MS | VH |  |  |  |  | 1.1365 | 1.0307 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200315 | 18L | Approved | P1 | 3 | 3CENTREVILLE | VH |  |  |  |  | 1.0948 | 1.0113 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200316 | 18L | Approved | P1 | 3 | 3SMITHDALE+ | VH |  |  |  |  | 1.0553 | 1.0354 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336525 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200317 | 18L | Approved | P1 | 3 | 3WASHINGTON+ | VH |  |  |  |  | 1.1375 | 1.0329 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200318 | 18L | Approved | P1 | 3 | 3ROXIE | VH |  |  |  |  | 1.1034 | 1.0323 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200319 | 18L | Approved | P1 | 3 | 3MEADVILLE | VH |  |  |  |  | 1.0773 | 1.0338 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200320 | 18L | Approved | P1 | 3 | 3CRANFIELD+ | VH |  |  |  |  | 1.1255 | 1.0322 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200321 | 18L | Approved | P1 | 3 | 3FAYETTE | VH |  |  |  |  | 1.2142 | 1.0326 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200322 | 18L | Approved | P1 | 3 | 3LORMAN+ | VH |  |  |  |  | 1.2418 | 1.0335 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200323 | 18L | Approved | P1 | 3 | 3LORMAN | VH |  |  |  |  | 1.2417 | 1.0334 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200324 | 18L | Approved | P1 | 3 | 3PORTGIBSON! | VH |  |  |  |  | 1.2672 | 1.0373 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200325 | 18L | Approved | P1 | 3 | 3GGNS | VH |  |  |  |  | 1.2663 | 1.0362 | 0.975 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200326 | 18L | Approved | P1 | 3 | 3S.VICKSBURG | VH |  |  |  |  | 1.3012 | 1.0325 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200327 | 18L | Approved | P1 | 3 | 3BEAVER_CRK! | VH |  |  |  |  | 1.0504 | 1.0351 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337310 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200328 | 18L | Approved | P1 | 3 | 3BLACK_RIVER | VH |  |  |  |  | 1.096 | 0.9963 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200329 | 18L | Approved | P1 | 3 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1204 | 1.0233 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200330 | 18L | Approved | P1 | 3 | 3PLANTATION! | VH |  |  |  |  | 1.1208 | 1.0273 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200331 | 18L | Approved | P1 | 3 | 3VIDALIA_LA | VH |  |  |  |  | 1.125 | 1.0276 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200332 | 18L | Approved | P1 | 3 | 3RED_GUM! | VH |  |  |  |  | 1.1341 | 1.034 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200333 | 18L | Approved | P1 | 3 | 3METROPOLIS | VH |  |  |  |  | 1.1375 | 1.0252 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200334 | 18L | Approved | P1 | 3 | 3WISNER | VH |  |  |  |  | 1.1378 | 1.0247 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200335 | 18L | Approved | P1 | 3 | 3WINNSBORO! | VH |  |  |  |  | 1.1137 | 1.0244 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200336 | 18L | Approved | P1 | 3 | 3ALTO_LA | VH |  |  |  |  | 1.0729 | 1.0127 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337331 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200337 | 18L | Approved | P1 | 3 | 3STANDARD! | VH |  |  |  |  | 1.0529 | 1.0182 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337340 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200338 | 18L | Approved | P1 | 3 | JNESVIL3 | VH |  |  |  |  | 1.096 | 0.9963 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200339 | 18L | Approved | P1 | 3 | VIDALIA3 | VH |  |  |  |  | 1.125 | 1.0276 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
200340 | 18L | Approved | P2 | 3 | 3NITTA YUMA+ | VL |  |  |  |  | 0.9141 | 1.0194 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336970 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200341 | 18L | Approved | P2 | 3 | 3MURPHY+ | VL |  |  |  |  | 0.8992 | 1.021 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336992 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200342 | 18L | Approved | P2 | 3 | 3SE.GREENVL | VL |  |  |  |  | 0.8836 | 1.0387 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337045 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200343 | 18L | Approved | P2 | 3 | 3GREENVILLE+ | VL |  |  |  |  | 0.8848 | 1.0355 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200344 | 18L | Approved | P2 | 3 | 3HOLLANDALE | VL |  |  |  |  | 0.9003 | 1.0219 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337048 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200345 | 18L | Approved | P2 | 3 | 3ARCOLA+ | VL |  |  |  |  | 0.892 | 1.0284 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200346 | 18L | Approved | P2 | 3 | 3SWIFTWATER | VL |  |  |  |  | 0.8844 | 1.0352 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
200347 | 18L | Approved | P1 | 3 | 5HORN LAKE% | VH |  |  |  |  | 1.0518 | 1.0667 | 0.92 | 1.05 | 361 | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 |  |  | VH
200348 | 18L | Approved | P1 | 3 | 6TUNICA! | VH |  |  |  |  | 1.0502 | 1.0354 | 0.92 | 1.05 | 399 | 337160 6TUNICA! 230 337998 6RITCHIE-1! 230 1 | 337160 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 337160 6TUNICA! 230 337998 6RITCHIE-1! 230 1 |  |  | VH
200349 | 18L | Approved | P1 | 3 | 8ETTA% | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 612 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
200350 | 18L | Approved | P1 | 3 | 8DUKE HS-1! | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 612 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
200351 | 18L | Approved | P1 | 3 | 8DUKE HS-2! | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 612 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
200352 | 18L | Approved | P1 | 3 | 8HOLND BTM% | VH |  |  |  |  | 1.0532 | 1.0342 | 0.92 | 1.05 | 723 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
200353 | 18L | Approved | P1 | 3 | 8ISES-XF | VH |  |  |  |  | 1.0553 | 1.0439 | 0.92 | 1.05 | 723 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
200354 | 18L | Approved | P1 | 3 | 8ISES% | VH |  |  |  |  | 1.0554 | 1.0439 | 0.92 | 1.05 | 723 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
200355 | 18L | Approved | P1 | 3 | 2WARD | VH |  |  |  |  | 1.0624 | 1.0493 | 0.92 | 1.05 | 723 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
200356 | 18L | Approved | P1 | 3 | 3RICUSKEY! | VH |  |  |  |  | 1.0506 | 1.0394 | 0.92 | 1.05 | 731 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  |  | VH
200357 | 18L | Approved | P2 | 3 | 3RICUSKEY! | VH |  |  |  |  | 1.0517 | 1.0394 | 0.92 | 1.05 | 734 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  |  | VH
200358 | 18L | Approved | P1 | 3 | 2WYNNE.E | VH |  |  |  |  | 1.0555 | 1.0451 | 0.92 | 1.05 | 783 | 338022 5MOSES% 161 338029 5FORSTCTY.N+ 161 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338022 5MOSES% 161 338029 5FORSTCTY.N+ 161 1 |  |  | VH
200359 | 18L | Approved | P1 | 3 | 2WYNNE.E | VH |  |  |  |  | 1.0566 | 1.0451 | 0.92 | 1.05 | 785 | 338022 5MOSES% 161 338882 5PALESTINE# 161 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338022 5MOSES% 161 338882 5PALESTINE# 161 1 |  |  | VH
200360 | 18L | Approved | P1 | 3 | 2WYNNE.E | VH |  |  |  |  | 1.056 | 1.0451 | 0.92 | 1.05 | 791 | 338029 5FORSTCTY.N+ 161 338031 5WYNNE.S 161 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338029 5FORSTCTY.N+ 161 338031 5WYNNE.S 161 1 |  |  | VH
200361 | 18L | Approved | P1 | 3 | 2WYNNE.E | VH |  |  |  |  | 1.0626 | 1.0451 | 0.92 | 1.05 | 793 | 338031 5WYNNE.S 161 338883 5WYNNE.E# 161 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338031 5WYNNE.S 161 338883 5WYNNE.E# 161 1 |  |  | VH
200362 | 18L | Approved | P1 | 3 | 2BLACK ROCK | VH |  |  |  |  | 1.0585 | 1.0691 | 0.92 | 1.05 | 851 | 338145 8ISES% 500 338187 8DELL% 500 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338145 8ISES% 500 338187 8DELL% 500 1 |  |  | VH
200363 | 18L | Approved | P1 | 3 | 3LIGHT# | VH |  |  |  |  | 1.0648 | 1.0517 | 0.92 | 1.05 | 906 | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 |  |  | VH
200364 | 18L | Approved | P1 | 3 | 3CROWLEYRDG# | VH |  |  |  |  | 1.065 | 1.0549 | 0.92 | 1.05 | 906 | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 |  |  | VH
200365 | 18L | Approved | P1 | 3 | 3SEDGWICK | VH |  |  |  |  | 1.0598 | 1.0484 | 0.92 | 1.05 | 907 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
200366 | 18L | Approved | P1 | 3 | 3T.E.P/S-7 | VH |  |  |  |  | 1.051 | 1.0396 | 0.92 | 1.05 | 907 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
200367 | 18L | Approved | P1 | 3 | 3WALNUT RDG! | VH |  |  |  |  | 1.0601 | 1.0461 | 0.92 | 1.05 | 907 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
200368 | 18L | Approved | P1 | 3 | 5POCHNTAS.N | VL |  |  |  |  | 0.8929 | 1.0226 | 0.92 | 1.05 | 918 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200369 | 18L | Approved | P1 | 3 | 5DATTO | VL |  |  |  |  | 0.8971 | 1.0177 | 0.92 | 1.05 | 918 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200370 | 18L | Approved | P1 | 3 | 5POCHNTAS.E# | VL |  |  |  |  | 0.893 | 1.0223 | 0.92 | 1.05 | 918 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200371 | 18L | Approved | P1 | 3 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8926 | 1.0246 | 0.92 | 1.05 | 918 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200372 | 18L | Approved | P1 | 3 | 5POCHNTAS.N | VL |  |  |  |  | 0.9168 | 1.0226 | 0.92 | 1.05 | 920 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200373 | 18L | Approved | P1 | 3 | 5POCHNTAS.E# | VL |  |  |  |  | 0.9169 | 1.0223 | 0.92 | 1.05 | 920 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200374 | 18L | Approved | P1 | 3 | 3DATTO | VH |  |  |  |  | 1.0632 | 1.0445 | 0.92 | 1.05 | 923 | 338227 3DATTO 115 338691 3CORNING.N# 115 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338227 3DATTO 115 338691 3CORNING.N# 115 1 |  |  | VH
200375 | 18L | Approved | P1 | 3 | 3DATTO | VH |  |  |  |  | 1.0572 | 1.0445 | 0.92 | 1.05 | 924 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 |  |  | VH
200376 | 18L | Approved | P1 | 3 | 3CORNING | VH |  |  |  |  | 1.0556 | 1.0385 | 0.92 | 1.05 | 924 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 |  |  | VH
200377 | 18L | Approved | P1 | 3 | 3CORNING.N# | VH |  |  |  |  | 1.0558 | 1.0391 | 0.92 | 1.05 | 924 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 |  |  | VH
200378 | 18L | Approved | P1 | 3 | 3DATTO | VH |  |  |  |  | 1.0623 | 1.0445 | 0.92 | 1.05 | 925 | 338228 3CORNING 115 338691 3CORNING.N# 115 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338691 3CORNING.N# 115 1 |  |  | VH
200379 | 18L | Approved | P1 | 3 | 3CORNING.N# | VH |  |  |  |  | 1.0621 | 1.0391 | 0.92 | 1.05 | 925 | 338228 3CORNING 115 338691 3CORNING.N# 115 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338691 3CORNING.N# 115 1 |  |  | VH
200380 | 18L | Approved | P1 | 3 | 8ISES-XF | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 973 | Unit:338146 1ISES U2 26.0 Id:1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | Unit:338146 1ISES U2 26.0 Id:1 |  |  | VH
200381 | 18L | Approved | P1 | 3 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 973 | Unit:338146 1ISES U2 26.0 Id:1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | Unit:338146 1ISES U2 26.0 Id:1 |  |  | VH
200382 | 18L | Approved | P1 | 3 | 2IMBODEN! | VL |  |  |  |  | 0.8954 | 1.0261 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338221 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200383 | 18L | Approved | P1 | 3 | 2WTR VALLEY! | VL |  |  |  |  | 0.8952 | 1.0258 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338222 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200384 | 18L | Approved | P1 | 3 | 5WTR VALLEY+ | VL |  |  |  |  | 0.8947 | 1.0252 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338223 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200385 | 18L | Approved | P1 | 3 | 5WTR VALLEY | VL |  |  |  |  | 0.8947 | 1.0252 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338224 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200386 | 18L | Approved | P1 | 3 | 5POCHNTAS.N | VL |  |  |  |  | 0.8949 | 1.0226 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200387 | 18L | Approved | P1 | 3 | 5DATTO | VL |  |  |  |  | 0.8989 | 1.0177 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200388 | 18L | Approved | P1 | 3 | 5POCHNTAS.E# | VL |  |  |  |  | 0.895 | 1.0223 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200389 | 18L | Approved | P1 | 3 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8947 | 1.0246 | 0.92 | 1.05 | 1057 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200390 | 18L | Approved | P1 | 3 | 2APLHERN | VH |  |  |  |  | 1.0519 | 1.0129 | 0.92 | 1.05 | 1071 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
200391 | 18L | Approved | P1 | 3 | 2BRYAN A! | VH |  |  |  |  | 1.0944 | 1.0213 | 0.92 | 1.05 | 1071 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
200392 | 18L | Approved | P1 | 3 | 2CALDWEL! | VH |  |  |  |  | 1.0555 | 1.0209 | 0.92 | 1.05 | 1074 | 334008 2BRYAN B! 69.0 334009 2CALDWEL! 69.0 1 | 334009 |  |  |  | 69 | 69 | 351 | EES |  |  | 334008 2BRYAN B! 69.0 334009 2CALDWEL! 69.0 1 |  |  | VH
200393 | 18L | Approved | P1 | 3 | 2SOMERVL! | VH |  |  |  |  | 1.0565 | 1.0186 | 0.92 | 1.05 | 1077 | 334010 2SOMERVL! 69.0 334011 2INDEPEN 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334010 2SOMERVL! 69.0 334011 2INDEPEN 69.0 1 |  |  | VH
200394 | 18L | Approved | P1 | 3 | 2SOMERVL! | VH |  |  |  |  | 1.0572 | 1.0186 | 0.92 | 1.05 | 1078 | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 |  |  | VH
200395 | 18L | Approved | P1 | 3 | 2INDEPEN | VH |  |  |  |  | 1.0572 | 1.0136 | 0.92 | 1.05 | 1078 | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 |  |  | VH
200396 | 18L | Approved | P1 | 3 | 2SOMERVL! | VH |  |  |  |  | 1.0586 | 1.0186 | 0.92 | 1.05 | 1079 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
200397 | 18L | Approved | P1 | 3 | 2INDEPEN | VH |  |  |  |  | 1.0587 | 1.0136 | 0.92 | 1.05 | 1079 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
200398 | 18L | Approved | P1 | 3 | 2IN.AT$T | VH |  |  |  |  | 1.0588 | 1.0101 | 0.92 | 1.05 | 1079 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
200399 | 18L | Approved | P1 | 3 | 2SOMERVL! | VH |  |  |  |  | 1.0622 | 1.0186 | 0.92 | 1.05 | 1080 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
200400 | 18L | Approved | P1 | 3 | 2INDEPEN | VH |  |  |  |  | 1.0629 | 1.0136 | 0.92 | 1.05 | 1080 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
200401 | 18L | Approved | P1 | 3 | 2IN.AT$T | VH |  |  |  |  | 1.0633 | 1.0101 | 0.92 | 1.05 | 1080 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
200402 | 18L | Approved | P1 | 3 | 2ANAVSOT! | VH |  |  |  |  | 1.0637 | 1.0013 | 0.92 | 1.05 | 1080 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334013 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
200403 | 18L | Approved | P1 | 3 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200404 | 18L | Approved | P1 | 3 | 4SHECORR | VH |  |  |  |  | 1.0681 | 1.0237 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200405 | 18L | Approved | P1 | 3 | 4CAMDEN | VH |  |  |  |  | 1.0652 | 1.0221 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200406 | 18L | Approved | P1 | 3 | 4DEER 1 | VH |  |  |  |  | 1.0591 | 1.0209 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200407 | 18L | Approved | P1 | 3 | 4TURKEYCRK | VH |  |  |  |  | 1.0564 | 1.0207 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200408 | 18L | Approved | P1 | 3 | 4DOUCETT! | VH |  |  |  |  | 1.0568 | 1.0207 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200409 | 18L | Approved | P1 | 3 | 4FORK CK | VH |  |  |  |  | 1.0515 | 1.0207 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200410 | 18L | Approved | P1 | 3 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200411 | 18L | Approved | P1 | 3 | 4WOODVILLE | VH |  |  |  |  | 1.0535 | 1.0211 | 0.92 | 1.05 | 1183 | 334127 4L111T411 138 334129 4CORIGAN! 138 1 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | 334127 4L111T411 138 334129 4CORIGAN! 138 1 |  |  | VH
200412 | 18L | Approved | P1 | 3 | 4CORIGAN! | VH |  |  |  |  | 1.0501 | 1.0242 | 0.92 | 1.05 | 1184 | 334129 4CORIGAN! 138 334130 4SHECORR 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334129 4CORIGAN! 138 334130 4SHECORR 138 1 |  |  | VH
200413 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0521 | 1.0418 | 0.92 | 1.05 | 1234 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
200414 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0533 | 1.0418 | 0.92 | 1.05 | 1235 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
200415 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0418 | 0.92 | 1.05 | 1237 | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 |  |  | VH
200416 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0552 | 1.0418 | 0.92 | 1.05 | 1238 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  |  | VH
200417 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.072 | 1.0418 | 0.92 | 1.05 | 1239 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 |  |  | VH
200418 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0551 | 1.0418 | 0.92 | 1.05 | 1240 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 2 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 2 |  |  | VH
200419 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0548 | 1.0418 | 0.92 | 1.05 | 1241 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  |  | VH
200420 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0596 | 1.0418 | 0.92 | 1.05 | 1247 | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 |  |  | VH
200421 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0562 | 1.0418 | 0.92 | 1.05 | 1259 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 |  |  | VH
200422 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0418 | 0.92 | 1.05 | 1260 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 |  |  | VH
200423 | 18L | Approved | P1 | 3 | 2HIMEX | VH |  |  |  |  | 1.054 | 1.0418 | 0.92 | 1.05 | 1262 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 |  |  | VH
200424 | 18L | Approved | P1 | 3 | 4CORIGAN! | VH |  |  |  |  | 1.0549 | 1.0242 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200425 | 18L | Approved | P1 | 3 | 4SHECORR | VH |  |  |  |  | 1.055 | 1.0237 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200426 | 18L | Approved | P1 | 3 | 4CAMDEN | VH |  |  |  |  | 1.0557 | 1.0221 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200427 | 18L | Approved | P1 | 3 | 4DEER 1 | VH |  |  |  |  | 1.0615 | 1.0209 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200428 | 18L | Approved | P1 | 3 | 4TURKEYCRK | VH |  |  |  |  | 1.0635 | 1.0207 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200429 | 18L | Approved | P1 | 3 | 4DOUCETT! | VH |  |  |  |  | 1.0638 | 1.0207 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200430 | 18L | Approved | P1 | 3 | 4FORK CK | VH |  |  |  |  | 1.0601 | 1.0207 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200431 | 18L | Approved | P1 | 3 | 4RAYBURN% | VH |  |  |  |  | 1.0548 | 1.0225 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334282 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200432 | 18L | Approved | P1 | 3 | 4MILLCR! | VH |  |  |  |  | 1.0512 | 1.0202 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200433 | 18L | Approved | P1 | 3 | 2PINELND | VH |  |  |  |  | 1.0585 | 1.0264 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200434 | 18L | Approved | P1 | 3 | 2TEMPL1* | VH |  |  |  |  | 1.0577 | 1.0256 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200435 | 18L | Approved | P1 | 3 | 2TEMPLE1 | VH |  |  |  |  | 1.0576 | 1.0254 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200436 | 18L | Approved | P1 | 3 | 2TEMPL2* | VH |  |  |  |  | 1.0576 | 1.0255 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200437 | 18L | Approved | P1 | 3 | 2TEMPLE2 | VH |  |  |  |  | 1.0575 | 1.0254 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200438 | 18L | Approved | P1 | 3 | 2TMPLSWC | VH |  |  |  |  | 1.0576 | 1.0255 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200439 | 18L | Approved | P1 | 3 | 2WEIRGAT | VH |  |  |  |  | 1.054 | 1.0216 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  | Project Proposed | VH | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200440 | 18L | Approved | P1 | 3 | 4URLAND! | VH |  |  |  |  | 1.0626 | 1.0213 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200441 | 18L | Approved | P1 | 3 | 4WOODVILLE | VH |  |  |  |  | 1.0629 | 1.0211 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200442 | 18L | Approved | P1 | 3 | 4WARREN! | VH |  |  |  |  | 1.0611 | 1.0224 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334316 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200443 | 18L | Approved | P1 | 3 | 4JASPER | VH |  |  |  |  | 1.0544 | 1.0207 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334330 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200444 | 18L | Approved | P1 | 3 | 4JASON | VH |  |  |  |  | 1.0528 | 1.019 | 0.92 | 1.05 | 1300 | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 | 334331 |  |  |  | 138 | 138 | 351 | EES |  |  | 334316 4WARREN! 138 334317 4KOUNTZE% 138 1 |  |  | VH
200445 | 18L | Approved | P1 | 3 | 4L111T411 | VH |  |  |  |  | 1.0531 | 1.0216 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200446 | 18L | Approved | P1 | 3 | 4KICKAPO | VH |  |  |  |  | 1.053 | 1.0215 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200447 | 18L | Approved | P1 | 3 | 4CORIGAN! | VH |  |  |  |  | 1.0633 | 1.0242 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200448 | 18L | Approved | P1 | 3 | 4SHECORR | VH |  |  |  |  | 1.0634 | 1.0237 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200449 | 18L | Approved | P1 | 3 | 4CAMDEN | VH |  |  |  |  | 1.0647 | 1.0221 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200450 | 18L | Approved | P1 | 3 | 4DEER 1 | VH |  |  |  |  | 1.0723 | 1.0209 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200451 | 18L | Approved | P1 | 3 | 4TURKEYCRK | VH |  |  |  |  | 1.0758 | 1.0207 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200452 | 18L | Approved | P1 | 3 | 4DOUCETT! | VH |  |  |  |  | 1.0754 | 1.0207 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200453 | 18L | Approved | P1 | 3 | 4FORK CK | VH |  |  |  |  | 1.0821 | 1.0207 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200454 | 18L | Approved | P1 | 3 | 4RAYBURN% | VH |  |  |  |  | 1.0974 | 1.0225 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334282 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200455 | 18L | Approved | P1 | 3 | 4MILLCR! | VH |  |  |  |  | 1.0922 | 1.0202 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200456 | 18L | Approved | P1 | 3 | 4PINELND | VH |  |  |  |  | 1.0869 | 1.0139 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200457 | 18L | Approved | P1 | 3 | 4BROADUS | VH |  |  |  |  | 1.086 | 1.0127 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200458 | 18L | Approved | P1 | 3 | 4ETOIL | VH |  |  |  |  | 1.0856 | 1.0122 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200459 | 18L | Approved | P1 | 3 | 4HRTNHIL | VH |  |  |  |  | 1.0891 | 1.0166 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200460 | 18L | Approved | P1 | 3 | 2PINELND | VH |  |  |  |  | 1.1008 | 1.0264 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200461 | 18L | Approved | P1 | 3 | 2TEMPL1* | VH |  |  |  |  | 1.1001 | 1.0256 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200462 | 18L | Approved | P1 | 3 | 2TEMPLE1 | VH |  |  |  |  | 1.0999 | 1.0254 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200463 | 18L | Approved | P1 | 3 | 2TEMPL2* | VH |  |  |  |  | 1.1 | 1.0255 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200464 | 18L | Approved | P1 | 3 | 2TEMPLE2 | VH |  |  |  |  | 1.0999 | 1.0254 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200465 | 18L | Approved | P1 | 3 | 2TMPLSWC | VH |  |  |  |  | 1.1 | 1.0255 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200466 | 18L | Approved | P1 | 3 | 2WEIRGAT | VH |  |  |  |  | 1.0967 | 1.0216 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  | Project Proposed | VH | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200467 | 18L | Approved | P1 | 3 | 4PEACH! | VH |  |  |  |  | 1.0826 | 1.0194 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200468 | 18L | Approved | P1 | 3 | 4UNONGSU! | VH |  |  |  |  | 1.0708 | 1.0185 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200469 | 18L | Approved | P1 | 3 | 4KIRBY | VH |  |  |  |  | 1.0624 | 1.0181 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200470 | 18L | Approved | P1 | 3 | 4CALL! | VH |  |  |  |  | 1.057 | 1.0182 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200471 | 18L | Approved | P1 | 3 | 4URLAND! | VH |  |  |  |  | 1.068 | 1.0213 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200472 | 18L | Approved | P1 | 3 | 4WOODVILLE | VH |  |  |  |  | 1.0702 | 1.0211 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200473 | 18L | Approved | P1 | 3 | 4WARREN! | VH |  |  |  |  | 1.0581 | 1.0224 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334316 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200474 | 18L | Approved | P1 | 3 | 4JASPER | VH |  |  |  |  | 1.117 | 1.0207 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334330 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200475 | 18L | Approved | P1 | 3 | 4JASON | VH |  |  |  |  | 1.1155 | 1.019 | 0.92 | 1.05 | 1318 | 334330 4JASPER 138 334332 4HLYSPG# 138 1 | 334331 |  |  |  | 138 | 138 | 351 | EES |  |  | 334330 4JASPER 138 334332 4HLYSPG# 138 1 |  |  | VH
200476 | 18L | Approved | P1 | 3 | 2JACKSON! | VH |  |  |  |  | 1.1511 | 1.0213 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200477 | 18L | Approved | P1 | 3 | 2FELICIANA | VH |  |  |  |  | 1.1565 | 1.0143 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200478 | 18L | Approved | P1 | 3 | 2MCMANUS | VH |  |  |  |  | 1.1602 | 1.0101 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200479 | 18L | Approved | P1 | 3 | 2BRADY_HGHTS | VH |  |  |  |  | 1.1565 | 1.0058 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200480 | 18L | Approved | P1 | 3 | 2CLINTON | VH |  |  |  |  | 1.1561 | 1.0054 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200481 | 18L | Approved | P1 | 3 | 2CLINTON_REA | VH |  |  |  |  | 1.1565 | 1.0058 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200482 | 18L | Approved | P1 | 3 | 2TEJAC | VH |  |  |  |  | 1.1453 | 1.027 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200483 | 18L | Approved | P1 | 3 | 2MARYDALE | VH |  |  |  |  | 1.1392 | 1.0329 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200484 | 18L | Approved | P1 | 3 | 2FRANCIS! | VH |  |  |  |  | 1.1079 | 1.032 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200485 | 18L | Approved | P1 | 3 | 2ANGOLA | VH |  |  |  |  | 1.0941 | 1.017 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200486 | 18L | Approved | P1 | 3 | 2GRANT | VH |  |  |  |  | 1.0791 | 1.0255 | 0.92 | 1.05 | 2009 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
200487 | 18L | Approved | P1 | 3 | 2JACKSON! | VH |  |  |  |  | 1.0936 | 1.0213 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200488 | 18L | Approved | P1 | 3 | 2FELICIANA | VH |  |  |  |  | 1.0981 | 1.0143 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200489 | 18L | Approved | P1 | 3 | 2MCMANUS | VH |  |  |  |  | 1.1012 | 1.0101 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200490 | 18L | Approved | P1 | 3 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0973 | 1.0058 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200491 | 18L | Approved | P1 | 3 | 2CLINTON | VH |  |  |  |  | 1.0969 | 1.0054 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200492 | 18L | Approved | P1 | 3 | 2CLINTON_REA | VH |  |  |  |  | 1.0973 | 1.0058 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200493 | 18L | Approved | P1 | 3 | 2TEJAC | VH |  |  |  |  | 1.1043 | 1.027 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200494 | 18L | Approved | P1 | 3 | 2MARYDALE | VH |  |  |  |  | 1.1156 | 1.0329 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200495 | 18L | Approved | P1 | 3 | 2FRANCIS! | VH |  |  |  |  | 1.1253 | 1.032 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200496 | 18L | Approved | P1 | 3 | 2ANGOLA | VH |  |  |  |  | 1.1116 | 1.017 | 0.92 | 1.05 | 2019 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
200497 | 18L | Approved | P1 | 3 | 2JACKSON! | VH |  |  |  |  | 1.0922 | 1.0213 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200498 | 18L | Approved | P1 | 3 | 2FELICIANA | VH |  |  |  |  | 1.0967 | 1.0143 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200499 | 18L | Approved | P1 | 3 | 2MCMANUS | VH |  |  |  |  | 1.0997 | 1.0101 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200500 | 18L | Approved | P1 | 3 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0958 | 1.0058 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200501 | 18L | Approved | P1 | 3 | 2CLINTON | VH |  |  |  |  | 1.0955 | 1.0054 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200502 | 18L | Approved | P1 | 3 | 2CLINTON_REA | VH |  |  |  |  | 1.0958 | 1.0058 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200503 | 18L | Approved | P1 | 3 | 2TEJAC | VH |  |  |  |  | 1.1027 | 1.027 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200504 | 18L | Approved | P1 | 3 | 2MARYDALE | VH |  |  |  |  | 1.1139 | 1.0329 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200505 | 18L | Approved | P1 | 3 | 2FRANCIS! | VH |  |  |  |  | 1.123 | 1.032 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200506 | 18L | Approved | P1 | 3 | 2ANGOLA | VH |  |  |  |  | 1.1094 | 1.017 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200507 | 18L | Approved | P1 | 3 | 2GRANT | VH |  |  |  |  | 1.1227 | 1.0255 | 0.92 | 1.05 | 2020 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
200508 | 18L | Approved | P1 | 3 | 3GMEADW! | VH |  |  |  |  | 1.1709 | 1.0185 | 0.92 | 1.05 | 2093 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
200509 | 18L | Approved | P1 | 3 | 3LEEVLL | VH |  |  |  |  | 1.1953 | 1.0114 | 0.92 | 1.05 | 2093 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
200510 | 18L | Approved | P1 | 3 | 3FOURCHN | VH |  |  |  |  | 1.195 | 1.0018 | 0.92 | 1.05 | 2093 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
200511 | 18L | Approved | P1 | 3 | 3CARLSL | VL |  |  |  |  | 0.8822 | 0.9825 | 0.92 | 1.05 | 2103 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
200512 | 18L | Approved | P1 | 3 | 3LUCKY | VH |  |  |  |  | 1.0524 | 1.0323 | 0.92 | 1.05 | 2259 | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 |  |  | VH
200513 | 18L | Approved | P1 | 3 | 3LUCKY | VH |  |  |  |  | 1.053 | 1.0323 | 0.92 | 1.05 | 2260 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
200514 | 18L | Approved | P1 | 3 | 3TX_EAST_E | VH |  |  |  |  | 1.053 | 1.0283 | 0.92 | 1.05 | 2260 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337350 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
200515 | 18L | Approved | P1 | 3 | 3DELHI_LA! | VH |  |  |  |  | 1.0541 | 1.0187 | 0.92 | 1.05 | 2318 | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 |  |  | VH
200516 | 18L | Approved | P1 | 3 | 3DELHI_LA! | VH |  |  |  |  | 1.0541 | 1.0187 | 0.92 | 1.05 | 2322 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
200517 | 18L | Approved | P1 | 3 | 3DELHI_RX | VH |  |  |  |  | 1.0541 | 1.01 | 0.92 | 1.05 | 2322 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
200518 | 18L | Approved | P1 | 3 | 3BLACK_RIV | VH |  |  |  |  | 1.0899 | 0.9963 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200519 | 18L | Approved | P1 | 3 | 3GILBERT | VH |  |  |  |  | 1.2259 | 1.0234 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200520 | 18L | Approved | P1 | 3 | 3PERSIM_MIL | VH |  |  |  |  | 1.1153 | 1.0237 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200521 | 18L | Approved | P2 | 3 | 3NATCHEZSES% | VH |  |  |  |  | 1.1235 | 1.034 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200522 | 18L | Approved | P2 | 3 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1232 | 1.034 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200523 | 18L | Approved | P2 | 3 | 3PINE RIDGE | VH |  |  |  |  | 1.123 | 1.0339 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200524 | 18L | Approved | P2 | 3 | 3NATCHEZ! | VH |  |  |  |  | 1.1225 | 1.0347 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200525 | 18L | Approved | P2 | 3 | 3J.MANVILLE | VH |  |  |  |  | 1.1208 | 1.0333 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200526 | 18L | Approved | P2 | 3 | 3INTL PAPER | VH |  |  |  |  | 1.1198 | 1.0328 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200527 | 18L | Approved | P2 | 3 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1191 | 1.0324 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200528 | 18L | Approved | P2 | 3 | 3NATCHEZ IND | VH |  |  |  |  | 1.1174 | 1.0315 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200529 | 18L | Approved | P2 | 3 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1151 | 1.032 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200530 | 18L | Approved | P2 | 3 | 3CROSBY+ | VH |  |  |  |  | 1.093 | 1.0276 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200531 | 18L | Approved | P2 | 3 | 3GLOSTER | VH |  |  |  |  | 1.0864 | 1.0265 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200532 | 18L | Approved | P2 | 3 | 3LIBERTY P/L | VH |  |  |  |  | 1.0564 | 1.0357 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200533 | 18L | Approved | P2 | 3 | 3WOODVILLE | VH |  |  |  |  | 1.0665 | 1.0052 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200534 | 18L | Approved | P2 | 3 | 3LIBERTY! | VH |  |  |  |  | 1.0564 | 1.0357 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200535 | 18L | Approved | P2 | 3 | 3INTRSTE P/L | VH |  |  |  |  | 1.0564 | 1.0357 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200536 | 18L | Approved | P2 | 3 | 3KINGSTON MS | VH |  |  |  |  | 1.1139 | 1.0307 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200537 | 18L | Approved | P2 | 3 | 3CENTREVILLE | VH |  |  |  |  | 1.0722 | 1.0113 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200538 | 18L | Approved | P2 | 3 | 3WASHINGTON+ | VH |  |  |  |  | 1.1156 | 1.0329 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200539 | 18L | Approved | P2 | 3 | 3ROXIE | VH |  |  |  |  | 1.0908 | 1.0323 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200540 | 18L | Approved | P2 | 3 | 3MEADVILLE | VH |  |  |  |  | 1.0716 | 1.0338 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200541 | 18L | Approved | P2 | 3 | 3CRANFIELD+ | VH |  |  |  |  | 1.1069 | 1.0322 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200542 | 18L | Approved | P2 | 3 | 3FAYETTE | VH |  |  |  |  | 1.1151 | 1.0326 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200543 | 18L | Approved | P2 | 3 | 3LORMAN+ | VH |  |  |  |  | 1.0961 | 1.0335 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200544 | 18L | Approved | P2 | 3 | 3LORMAN | VH |  |  |  |  | 1.096 | 1.0334 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200545 | 18L | Approved | P2 | 3 | 3PORTGIBSON! | VH |  |  |  |  | 1.0834 | 1.0373 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200546 | 18L | Approved | P2 | 3 | 3GGNS | VH |  |  |  |  | 1.0824 | 1.0362 | 0.975 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200547 | 18L | Approved | P2 | 3 | 3BLACK_RIVER | VH |  |  |  |  | 1.0899 | 0.9963 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200548 | 18L | Approved | P2 | 3 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1144 | 1.0233 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200549 | 18L | Approved | P2 | 3 | 3PLANTATION! | VH |  |  |  |  | 1.1096 | 1.0273 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200550 | 18L | Approved | P2 | 3 | 3VIDALIA_LA | VH |  |  |  |  | 1.1113 | 1.0276 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200551 | 18L | Approved | P2 | 3 | 3RED_GUM! | VH |  |  |  |  | 1.1358 | 1.034 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200552 | 18L | Approved | P2 | 3 | 3METROPOLIS | VH |  |  |  |  | 1.2138 | 1.0252 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200553 | 18L | Approved | P2 | 3 | 3WISNER | VH |  |  |  |  | 1.2194 | 1.0247 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200554 | 18L | Approved | P2 | 3 | 3WINNSBORO! | VH |  |  |  |  | 1.2411 | 1.0244 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200555 | 18L | Approved | P2 | 3 | JNESVIL3 | VH |  |  |  |  | 1.0899 | 0.9963 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200556 | 18L | Approved | P2 | 3 | VIDALIA3 | VH |  |  |  |  | 1.1113 | 1.0276 | 0.92 | 1.05 | 2455 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
200557 | 18L | Approved | P1 | 3 | 3GILBERT | VH |  |  |  |  | 1.1181 | 1.0234 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | VH
200558 | 18L | Approved | P1 | 3 | 3BASKIN | VH |  |  |  |  | 1.1253 | 1.0183 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | VH
200559 | 18L | Approved | P1 | 3 | 3RED_GUM! | VH |  |  |  |  | 1.055 | 1.034 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200560 | 18L | Approved | P1 | 3 | 3METROPOLIS | VH |  |  |  |  | 1.1108 | 1.0252 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200561 | 18L | Approved | P1 | 3 | 3WISNER | VH |  |  |  |  | 1.115 | 1.0247 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200562 | 18L | Approved | P1 | 3 | 3WINNSBORO! | VH |  |  |  |  | 1.1275 | 1.0244 | 0.92 | 1.05 | 2456 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
200563 | 18L | Approved | P1 | 3 | PNPRARIE 4 | VL |  |  |  |  | 0.9157 | 1.0028 | 0.92 | 1.05 | 2610 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
200564 | 18L | Approved | P1 | 3 | ELKS 6 | VL |  |  |  |  | 0.9044 | 1.0071 | 0.92 | 1.05 | 2720 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
200565 | 18L | Approved | P1 | 3 | 7FLETCH | VH |  |  |  |  | 1.0632 | 1.0468 | 0.92 | 1.05 | 2731 | 3Wnd: OPEN B$0909 FLETCHE1 1 | 300040 |  |  |  | 345 | 345 | 330 | AECI |  |  | 3Wnd: OPEN B$0909 FLETCHE1 1 |  |  | VH
200566 | 18L | Approved | P1 | 3 | 7SALEM | VH |  |  |  |  | 1.0578 | 1.0473 | 0.92 | 1.05 | 2731 | 3Wnd: OPEN B$0909 FLETCHE1 1 | 300047 |  |  |  | 345 | 345 | 330 | AECI |  |  | 3Wnd: OPEN B$0909 FLETCHE1 1 |  |  | VH
200567 | 18L | Approved | P1 | 3 | 7STFRAN | VH |  |  |  |  | 1.0739 | 1.047 | 0.92 | 1.05 | 2738 | 300046 7NEWMAD 345 300048 7STFRAN 345 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 300048 7STFRAN 345 1 |  |  | VH
200568 | 18L | Approved | P1 | 3 | 7GOBKNOB | VH |  |  |  |  | 1.072 | 1.0512 | 0.92 | 1.05 | 2738 | 300046 7NEWMAD 345 300048 7STFRAN 345 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 300048 7STFRAN 345 1 |  |  | VH
200569 | 18L | Approved | P1 | 3 | 7ESSEX | VH |  |  |  |  | 1.0562 | 1.046 | 0.92 | 1.05 | 2739 | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 |  |  | VH
200570 | 18L | Approved | P1 | 3 | 7WNEWMADRID | VH |  |  |  |  | 1.0543 | 1.0369 | 0.92 | 1.05 | 2739 | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 |  |  | VH
200571 | 18L | Approved | P1 | 3 | 8NEWMAD | VH |  |  |  |  | 1.0604 | 1.0455 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200572 | 18L | Approved | P1 | 3 | 7ESSEX | VH |  |  |  |  | 1.0587 | 1.046 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200573 | 18L | Approved | P1 | 3 | 7NEWMAD | VH |  |  |  |  | 1.0569 | 1.0368 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200574 | 18L | Approved | P1 | 3 | 7STFRAN | VH |  |  |  |  | 1.0632 | 1.047 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200575 | 18L | Approved | P1 | 3 | 7GOBKNOB | VH |  |  |  |  | 1.0641 | 1.0512 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200576 | 18L | Approved | P1 | 3 | 8WNEWMADRID | VH |  |  |  |  | 1.0604 | 1.0455 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200577 | 18L | Approved | P1 | 3 | 7WNEWMADRID | VH |  |  |  |  | 1.0569 | 1.0369 | 0.92 | 1.05 | 2746 | Unit:300007 1NM G2 22.0 Id:1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
200578 | 18L | Approved | P1 | 3 | 7BLACKBERRY | VH |  |  |  |  | 1.0503 | 1.039 | 0.92 | 1.05 | 2762 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 300739 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 |  |  | VH
200579 | 18L | Approved | P1 | 3 | 7SPORTSMAN | VH |  |  |  |  | 1.0525 | 1.0127 | 0.92 | 1.05 | 2762 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 300740 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 |  |  | VH
200580 | 18L | Approved | P1 | 3 | 8THALMANN | VH |  |  |  |  | 1.0577 | 1.0473 | 0.92 | 1.05 | 2789 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
200581 | 18L | Approved | P1 | 3 | 8MCCALL RD | VH |  |  |  |  | 1.0725 | 1.0369 | 0.92 | 1.05 | 2789 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
200582 | 18L | Approved | P1 | 3 | 8FORTSON | VH |  |  |  |  | 1.0594 | 1.0402 | 0.92 | 1.05 | 2791 | 380010 8FORTSON 500 380125 6FORTSON 230 1 | 380010 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380010 8FORTSON 500 380125 6FORTSON 230 1 |  |  | VH
200583 | 18L | Approved | P1 | 3 | 8TENASKA GA | VH |  |  |  |  | 1.054 | 1.0378 | 0.92 | 1.05 | 3305 | 383033 8TENASKA GA 500 383034 8HEARD CO 500 Z1 | 383033 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 383033 8TENASKA GA 500 383034 8HEARD CO 500 Z1 |  |  | VH
200584 | 18L | Approved | P1 | 3 | 8CLAY 8 | VH |  |  |  |  | 1.0667 | 1.0376 | 0.92 | 1.05 | 3319 | 384157 8MILLER8 500 385312 8CLAY 8 500 1 | 385312 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 384157 8MILLER8 500 385312 8CLAY 8 500 1 |  |  | VH
200585 | 18L | Approved | P1 | 3 | 8DANIEL | VH |  |  |  |  | 1.0812 | 1.0292 | 0.92 | 1.05 | 3503 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
200586 | 18L | Approved | P1 | 3 | 8E POINT AL | VH |  |  |  |  | 1.0614 | 1.0414 | 0.92 | 1.05 | 3601 | 360058 8E POINT AL 500 384157 8MILLER8 500 1 | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360058 8E POINT AL 500 384157 8MILLER8 500 1 |  |  | VH
200587 | 18L | Approved | P1 | 3 | 8SHAWNEE FP | VH |  |  |  |  | 1.1077 | 1.0839 | 0.92 | 1.05 | 3615 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
200588 | 18L | Approved | P1 | 3 | 7SHAWNEE FP | VH |  |  |  |  | 1.0609 | 1.0765 | 0.92 | 1.05 | 3615 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
200589 | 18L | Approved | P1 | 3 | 8MARSHALL KY | VH |  |  |  |  | 1.1019 | 1.0817 | 0.92 | 1.05 | 3615 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
200590 | 18L | Approved | P1 | 3 | 8MARSHALL KY | VH |  |  |  |  | 1.0695 | 1.0817 | 0.92 | 1.05 | 3622 | 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  | VH
200591 | 18L | Approved | P1 | 3 | 8LAG CRK CT | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 3623 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200592 | 18L | Approved | P1 | 3 | 8LAG CRK CC | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 3623 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200593 | 18L | Approved | P1 | 3 | 8WEAKLEY TN | VH |  |  |  |  | 1.061 | 1.0777 | 0.92 | 1.05 | 3624 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 |  |  | VH
200594 | 18L | Approved | P1 | 3 | 8GLEASON CT | VH |  |  |  |  | 1.0906 | 1.0802 | 0.92 | 1.05 | 3624 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 |  |  | VH
200595 | 18L | Approved | P1 | 3 | 8WEAKLEY TN | VH |  |  |  |  | 1.091 | 1.0777 | 0.92 | 1.05 | 3625 | 3Wnd: OPEN B$0188 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0188 1 |  |  | VH
200596 | 18L | Approved | P1 | 3 | 8GLEASON CT | VH |  |  |  |  | 1.0918 | 1.0802 | 0.92 | 1.05 | 3625 | 3Wnd: OPEN B$0188 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0188 1 |  |  | VH
200597 | 18L | Approved | P1 | 3 | 8WEAKLEY TN | VH |  |  |  |  | 1.0921 | 1.0777 | 0.92 | 1.05 | 3632 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200598 | 18L | Approved | P1 | 3 | 8LAG CRK CT | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 3632 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200599 | 18L | Approved | P1 | 3 | 8GLEASON CT | VH |  |  |  |  | 1.0922 | 1.0802 | 0.92 | 1.05 | 3632 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200600 | 18L | Approved | P1 | 3 | 8LAG CRK CC | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 3632 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
200601 | 18L | Approved | P1 | 3 | 5HORN LAKE% | VH |  |  |  |  | 1.0518 | 1.0667 | 0.92 | 1.05 | 3635 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 |  |  | VH
200602 | 18L | Approved | P1 | 3 | 8PLEASANT HL | VH |  |  |  |  | 1.0677 | 1.0524 | 0.92 | 1.05 | 3647 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | VH
200603 | 18L | Approved | P1 | 3 | 8WEAKLEY TN | VH |  |  |  |  | 1.0644 | 1.0777 | 0.92 | 1.05 | 3655 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 |  |  | VH
200604 | 18L | Approved | P1 | 3 | 8GLEASON CT | VH |  |  |  |  | 1.0648 | 1.0802 | 0.92 | 1.05 | 3655 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 |  |  | VH
200605 | 18L | Approved | P1 | 3 | 8PARADISE FP | VH |  |  |  |  | 1.0755 | 1.0869 | 0.92 | 1.05 | 3656 | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 |  |  | VH
200606 | 18L | Approved | P1 | 3 | 8MONTGOMERY | VH |  |  |  |  | 1.0691 | 1.0805 | 0.92 | 1.05 | 3656 | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 |  |  | VH
200607 | 18L | Approved | P1 | 3 | 8PARADISE FP | VH |  |  |  |  | 1.0971 | 1.0869 | 0.92 | 1.05 | 3662 | 3Wnd: OPEN B$0195 1 | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0195 1 |  |  | VH
200608 | 18L | Approved | P1 | 3 | 8MONTGOMERY | VH |  |  |  |  | 1.0906 | 1.0805 | 0.92 | 1.05 | 3662 | 3Wnd: OPEN B$0195 1 | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0195 1 |  |  | VH
200609 | 18L | Approved | P1 | 3 | 8RUTHERFORD | VH |  |  |  |  | 1.0556 | 1.0685 | 0.92 | 1.05 | 3663 | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 |  |  | VH
200610 | 18L | Approved | P1 | 3 | 8MAURY TN | VH |  |  |  |  | 1.0532 | 1.0679 | 0.92 | 1.05 | 3663 | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 |  |  | VH
200611 | 18L | Approved | P1 | 3 | 8PLATEAU TN | VH |  |  |  |  | 1.0713 | 1.0611 | 0.92 | 1.05 | 3683 | 360077 8PLATEAU TN 500 360090 8ROANE TN 500 1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360077 8PLATEAU TN 500 360090 8ROANE TN 500 1 |  |  | VH
200612 | 18L | Approved | P1 | 3 | 8PLATEAU TN | VH |  |  |  |  | 1.073 | 1.0611 | 0.92 | 1.05 | 3684 | 3Wnd: OPEN B$0033 1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0033 1 |  |  | VH
200613 | 18L | Approved | P1 | 3 | 8SULLIVAN TN | VH |  |  |  |  | 1.0734 | 1.0608 | 0.92 | 1.05 | 3700 | 3Wnd: OPEN B$0258 2 | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0258 2 |  |  | VH
200614 | 18L | Approved | P1 | 3 | 8CHOCTAW CC | VH |  |  |  |  | 1.0529 | 1.0348 | 0.92 | 1.05 | 3727 | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 | 360627 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 |  |  | VH
200615 | 18L | Approved | P1 | 3 | 8CHOCTAW MS | VH |  |  |  |  | 1.0529 | 1.0348 | 0.92 | 1.05 | 3727 | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 | 360654 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 |  |  | VH
200616 | 18L | Approved | P1 | 3 | 8FRANKLIN TN | VH |  |  |  |  | 1.0623 | 1.0522 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200617 | 18L | Approved | P1 | 3 | 8PLATEAU TN | VH |  |  |  |  | 1.0712 | 1.0611 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200618 | 18L | Approved | P1 | 3 | 8SEQUOYAH NP | VH |  |  |  |  | 1.0564 | 1.04 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360081 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200619 | 18L | Approved | P1 | 3 | 8WBNP #1 | VH |  |  |  |  | 1.0569 | 1.0418 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200620 | 18L | Approved | P1 | 3 | 8ROANE TN | VH |  |  |  |  | 1.0625 | 1.0494 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200621 | 18L | Approved | P1 | 3 | 8BULL RUN FP | VH |  |  |  |  | 1.064 | 1.0509 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200622 | 18L | Approved | P1 | 3 | 8VOLUNTEER | VH |  |  |  |  | 1.0688 | 1.0562 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200623 | 18L | Approved | P1 | 3 | 8HIWASSEE TN | VH |  |  |  |  | 1.0572 | 1.0415 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360110 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200624 | 18L | Approved | P1 | 3 | 8BRADLEY TN | VH |  |  |  |  | 1.052 | 1.0367 | 0.92 | 1.05 | 3742 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360662 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
200625 | 18L | Approved | P1 | 3 | 8PLATEAU TN | VH |  |  |  |  | 1.0743 | 1.0611 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200626 | 18L | Approved | P1 | 3 | 8SEQUOYAH NP | VH |  |  |  |  | 1.0512 | 1.04 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360081 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200627 | 18L | Approved | P1 | 3 | 8WBNP #1 | VH |  |  |  |  | 1.0625 | 1.0418 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200628 | 18L | Approved | P1 | 3 | 8ROANE TN | VH |  |  |  |  | 1.0673 | 1.0494 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200629 | 18L | Approved | P1 | 3 | 8BULL RUN FP | VH |  |  |  |  | 1.0693 | 1.0509 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200630 | 18L | Approved | P1 | 3 | 8VOLUNTEER | VH |  |  |  |  | 1.0737 | 1.0562 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200631 | 18L | Approved | P1 | 3 | 8HIWASSEE TN | VH |  |  |  |  | 1.0572 | 1.0415 | 0.92 | 1.05 | 3744 | Unit:364021 1WBNP N1 24.0 Id:1 | 360110 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
200632 | 18L | Approved | P1 | 3 | 8WBNP #1 | VH |  |  |  |  | 1.0543 | 1.0418 | 0.92 | 1.05 | 3745 | Unit:364022 1WBNP N2 24.0 Id:2 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
200633 | 18L | Approved | P1 | 3 | 8ROANE TN | VH |  |  |  |  | 1.0606 | 1.0494 | 0.92 | 1.05 | 3745 | Unit:364022 1WBNP N2 24.0 Id:2 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
200634 | 18L | Approved | P1 | 3 | 8BULL RUN FP | VH |  |  |  |  | 1.0622 | 1.0509 | 0.92 | 1.05 | 3745 | Unit:364022 1WBNP N2 24.0 Id:2 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
200635 | 18L | Approved | P1 | 3 | 8VOLUNTEER | VH |  |  |  |  | 1.0673 | 1.0562 | 0.92 | 1.05 | 3745 | Unit:364022 1WBNP N2 24.0 Id:2 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
200636 | 18L | Approved | P1 | 3 | 8PHIPPS B NP | VH |  |  |  |  | 1.0559 | 1.0674 | 0.92 | 1.05 | 3861 | 324073 8POCKETN 500 360102 8PHIPPS B NP 500 1 | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | 324073 8POCKETN 500 360102 8PHIPPS B NP 500 1 |  |  | VH
200637 | 18L | Approved | P1 | 3 | 8SHAWNEE FP | VH |  |  |  |  | 1.0969 | 1.0839 | 0.92 | 1.05 | 3863 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
200638 | 18L | Approved | P1 | 3 | 7SHAWNEE FP | VH |  |  |  |  | 1.0941 | 1.0765 | 0.92 | 1.05 | 3863 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
200639 | 18L | Approved | P1 | 3 | 8MARSHALL KY | VH |  |  |  |  | 1.0922 | 1.0817 | 0.92 | 1.05 | 3863 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
200640 | 18L | Approved | P1 | 3 | TENRUSK7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 4155 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
200641 | 18L | Approved | P1 | 3 | TENGEN 7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 4155 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
200642 | 18L | Approved | P1 | 3 | ELKCITY7 | VH |  |  |  |  | 1.0577 | 1.0351 | 0.92 | 1.05 | 4196 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
200643 | 18L | Approved | P1 | 3 | GRACMNT7 | VH |  |  |  |  | 1.0523 | 1.0292 | 0.92 | 1.05 | 4253 | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 515800 |  |  |  | 345 | 345 | 524 | OKGE |  |  | 514801 MINCO 7 345 515800 GRACMNT7 345 1 |  |  | VH
200644 | 18L | Approved | P1 | 3 | FTSMITH7 | VH |  |  |  |  | 1.0537 | 1.0373 | 0.92 | 1.05 | 4296 | 3Wnd: OPEN B$0929 FTSMITH1 1 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | 3Wnd: OPEN B$0929 FTSMITH1 1 |  |  | VH
200645 | 18L | Approved | P0 | 4 | 8GPDELL | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
200646 | 18L | Approved | P0 | 4 | 7GOBKNOB | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 | 0 | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
200647 | 18L | Approved | P0 | 4 | 2BATSON! | VH |  |  |  |  | 1.0536 | 1.0536 | 0.92 | 1.05 | 0 | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
200648 | 18L | Approved | P0 | 4 | 26L102TAP | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 334256 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
200649 | 18L | Approved | P0 | 4 | 5HORN LAKE% | VH |  |  |  |  | 1.0667 | 1.0667 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
200650 | 18L | Approved | P0 | 4 | 8DELL% | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200651 | 18L | Approved | P0 | 4 | 8SANS SOUCI% | VH |  |  |  |  | 1.0614 | 1.0614 | 0.92 | 1.05 | 0 | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200652 | 18L | Approved | P0 | 4 | 3PARAGOULD! | VH |  |  |  |  | 1.0589 | 1.0589 | 0.92 | 1.05 | 0 | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200653 | 18L | Approved | P0 | 4 | 2BLACK ROCK | VH |  |  |  |  | 1.0691 | 1.0691 | 0.92 | 1.05 | 0 | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200654 | 18L | Approved | P0 | 4 | 2OPPELLO | VH |  |  |  |  | 1.0526 | 1.0526 | 0.92 | 1.05 | 0 | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200655 | 18L | Approved | P0 | 4 | 5DELL# | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 | 0 | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200656 | 18L | Approved | P0 | 4 | 3LIGHT# | VH |  |  |  |  | 1.0517 | 1.0517 | 0.92 | 1.05 | 0 | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200657 | 18L | Approved | P0 | 4 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0549 | 1.0549 | 0.92 | 1.05 | 0 | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
200658 | 18L | Approved | P0 | 4 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 | 0 | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200659 | 18L | Approved | P0 | 4 | 7SHAWNEE FP | VH |  |  |  |  | 1.0765 | 1.0765 | 0.92 | 1.05 | 0 | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200660 | 18L | Approved | P0 | 4 | 8RUTHERFORD | VH |  |  |  |  | 1.0685 | 1.0685 | 0.92 | 1.05 | 0 | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200661 | 18L | Approved | P0 | 4 | 8MARSHALL KY | VH |  |  |  |  | 1.0817 | 1.0817 | 0.92 | 1.05 | 0 | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200662 | 18L | Approved | P0 | 4 | 8WEAKLEY TN | VH |  |  |  |  | 1.0777 | 1.0777 | 0.92 | 1.05 | 0 | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200663 | 18L | Approved | P0 | 4 | 8JACKSON TN | VH |  |  |  |  | 1.0665 | 1.0665 | 0.92 | 1.05 | 0 | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200664 | 18L | Approved | P0 | 4 | 8SHELBY TN | VH |  |  |  |  | 1.0602 | 1.0602 | 0.92 | 1.05 | 0 | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200665 | 18L | Approved | P0 | 4 | 8CORDOVA TN | VH |  |  |  |  | 1.0556 | 1.0556 | 0.92 | 1.05 | 0 | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200666 | 18L | Approved | P0 | 4 | 8JVILLE FP | VH |  |  |  |  | 1.0824 | 1.0824 | 0.92 | 1.05 | 0 | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200667 | 18L | Approved | P0 | 4 | 8CUMBERLAND | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 | 0 | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200668 | 18L | Approved | P0 | 4 | 8PARADISE FP | VH |  |  |  |  | 1.0869 | 1.0869 | 0.92 | 1.05 | 0 | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200669 | 18L | Approved | P0 | 4 | 8MONTGOMERY | VH |  |  |  |  | 1.0805 | 1.0805 | 0.92 | 1.05 | 0 | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200670 | 18L | Approved | P0 | 4 | 8DAVIDSON TN | VH |  |  |  |  | 1.0796 | 1.0796 | 0.92 | 1.05 | 0 | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200671 | 18L | Approved | P0 | 4 | 8MAURY TN | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 | 0 | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200672 | 18L | Approved | P0 | 4 | 8FRANKLIN TN | VH |  |  |  |  | 1.0522 | 1.0522 | 0.92 | 1.05 | 0 | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200673 | 18L | Approved | P0 | 4 | 8WILSON TN | VH |  |  |  |  | 1.0767 | 1.0767 | 0.92 | 1.05 | 0 | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200674 | 18L | Approved | P0 | 4 | 8PLATEAU TN | VH |  |  |  |  | 1.0611 | 1.0611 | 0.92 | 1.05 | 0 | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200675 | 18L | Approved | P0 | 4 | 8BULL RUN FP | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 | 0 | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200676 | 18L | Approved | P0 | 4 | 8VOLUNTEER | VH |  |  |  |  | 1.0562 | 1.0562 | 0.92 | 1.05 | 0 | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200677 | 18L | Approved | P0 | 4 | 8PHIPPS B NP | VH |  |  |  |  | 1.0674 | 1.0674 | 0.92 | 1.05 | 0 | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200678 | 18L | Approved | P0 | 4 | 8SULLIVAN TN | VH |  |  |  |  | 1.0608 | 1.0608 | 0.92 | 1.05 | 0 | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200679 | 18L | Approved | P0 | 4 | 8PLEASANT HL | VH |  |  |  |  | 1.0524 | 1.0524 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200680 | 18L | Approved | P0 | 4 | 8HAYWOOD TN | VH |  |  |  |  | 1.0647 | 1.0647 | 0.92 | 1.05 | 0 | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200681 | 18L | Approved | P0 | 4 | 8LAG CRK CT | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 | 0 | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200682 | 18L | Approved | P0 | 4 | 8PIN HOOK TN | VH |  |  |  |  | 1.0775 | 1.0775 | 0.92 | 1.05 | 0 | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200683 | 18L | Approved | P0 | 4 | 8GLEASON CT | VH |  |  |  |  | 1.0802 | 1.0802 | 0.92 | 1.05 | 0 | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200684 | 18L | Approved | P0 | 4 | 8BENTON MS | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200685 | 18L | Approved | P0 | 4 | 8MAGNOL CC1 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200686 | 18L | Approved | P0 | 4 | 8MAGNOL CC2 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 | 0 | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200687 | 18L | Approved | P0 | 4 | 8LAG CRK CC | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 | 0 | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200688 | 18L | Approved | P1 | 4 | 8ISES-XF | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 113 | G-338146-1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | G-338146-1 |  |  | VH
200689 | 18L | Approved | P1 | 4 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 113 | G-338146-1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | G-338146-1 |  |  | VH
200690 | 18L | Approved | P1 | 4 | 8NEWMAD | VH |  |  |  |  | 1.0604 | 1.0455 | 0.92 | 1.05 | 159 | P1_2-1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200691 | 18L | Approved | P1 | 4 | 7ESSEX | VH |  |  |  |  | 1.0587 | 1.046 | 0.92 | 1.05 | 159 | P1_2-1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200692 | 18L | Approved | P1 | 4 | 7NEWMAD | VH |  |  |  |  | 1.0569 | 1.0368 | 0.92 | 1.05 | 159 | P1_2-1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200693 | 18L | Approved | P1 | 4 | 7STFRAN | VH |  |  |  |  | 1.0632 | 1.047 | 0.92 | 1.05 | 159 | P1_2-1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200694 | 18L | Approved | P1 | 4 | 7GOBKNOB | VH |  |  |  |  | 1.0641 | 1.0512 | 0.92 | 1.05 | 159 | P1_2-1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200695 | 18L | Approved | P1 | 4 | 8WNEWMADRID | VH |  |  |  |  | 1.0604 | 1.0455 | 0.92 | 1.05 | 159 | P1_2-1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200696 | 18L | Approved | P1 | 4 | 7WNEWMADRID | VH |  |  |  |  | 1.0569 | 1.0369 | 0.92 | 1.05 | 159 | P1_2-1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
200697 | 18L | Approved | P1 | 4 | 7STFRAN | VH |  |  |  |  | 1.0739 | 1.047 | 0.92 | 1.05 | 165 | P1_2-7 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! |  |  | VH
200698 | 18L | Approved | P1 | 4 | 7GOBKNOB | VH |  |  |  |  | 1.072 | 1.0512 | 0.92 | 1.05 | 165 | P1_2-7 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! |  |  | VH
200699 | 18L | Approved | P1 | 4 | 7ESSEX | VH |  |  |  |  | 1.0562 | 1.046 | 0.92 | 1.05 | 169 | P1_2-11 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID |  |  | VH
200700 | 18L | Approved | P1 | 4 | 7WNEWMADRID | VH |  |  |  |  | 1.0543 | 1.0369 | 0.92 | 1.05 | 169 | P1_2-11 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID |  |  | VH
200701 | 18L | Approved | P1 | 4 | 5HARDY.N | VH |  |  |  |  | 1.0539 | 1.0418 | 0.92 | 1.05 | 196 | P1_2-38 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200702 | 18L | Approved | P1 | 4 | 5THAYER.S! | VH |  |  |  |  | 1.0559 | 1.0415 | 0.92 | 1.05 | 196 | P1_2-38 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200703 | 18L | Approved | P1 | 4 | 2THAYER.S! | VH |  |  |  |  | 1.0521 | 1.0395 | 0.92 | 1.05 | 196 | P1_2-38 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200704 | 18L | Approved | P1 | 4 | 2THAYER.N | VH |  |  |  |  | 1.0508 | 1.0389 | 0.92 | 1.05 | 196 | P1_2-38 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200705 | 18L | Approved | P1 | 4 | 5HARDY.E# | VH |  |  |  |  | 1.0531 | 1.042 | 0.92 | 1.05 | 196 | P1_2-38 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200706 | 18L | Approved | P1 | 4 | 5MAMMOTH# | VH |  |  |  |  | 1.0547 | 1.0417 | 0.92 | 1.05 | 196 | P1_2-38 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
200707 | 18L | Approved | P1 | 4 | 5HARDY.N | VH |  |  |  |  | 1.0529 | 1.0418 | 0.92 | 1.05 | 217 | P1_2-59 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200708 | 18L | Approved | P1 | 4 | 5THAYER.S! | VH |  |  |  |  | 1.0548 | 1.0415 | 0.92 | 1.05 | 217 | P1_2-59 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200709 | 18L | Approved | P1 | 4 | 2THAYER.S! | VH |  |  |  |  | 1.0514 | 1.0395 | 0.92 | 1.05 | 217 | P1_2-59 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200710 | 18L | Approved | P1 | 4 | 2THAYER.N | VH |  |  |  |  | 1.0502 | 1.0389 | 0.92 | 1.05 | 217 | P1_2-59 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200711 | 18L | Approved | P1 | 4 | 5HARDY.E# | VH |  |  |  |  | 1.0523 | 1.042 | 0.92 | 1.05 | 217 | P1_2-59 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200712 | 18L | Approved | P1 | 4 | 5MAMMOTH# | VH |  |  |  |  | 1.0537 | 1.0417 | 0.92 | 1.05 | 217 | P1_2-59 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
200713 | 18L | Approved | P1 | 4 | 2APLHERN | VH |  |  |  |  | 1.0519 | 1.0129 | 0.92 | 1.05 | 283 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
200714 | 18L | Approved | P1 | 4 | 2BRYAN A! | VH |  |  |  |  | 1.0944 | 1.0213 | 0.92 | 1.05 | 283 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
200715 | 18L | Approved | P1 | 4 | 2CALDWEL! | VH |  |  |  |  | 1.0555 | 1.0209 | 0.92 | 1.05 | 284 | P1_2-126 | 334009 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-126 |  |  | VH
200716 | 18L | Approved | P1 | 4 | 2SOMERVL! | VH |  |  |  |  | 1.0564 | 1.0186 | 0.92 | 1.05 | 287 | P1_2-129 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-129 |  |  | VH
200717 | 18L | Approved | P1 | 4 | 2SOMERVL! | VH |  |  |  |  | 1.0622 | 1.0186 | 0.92 | 1.05 | 288 | P1_2-130 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
200718 | 18L | Approved | P1 | 4 | 2INDEPEN | VH |  |  |  |  | 1.0629 | 1.0136 | 0.92 | 1.05 | 288 | P1_2-130 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
200719 | 18L | Approved | P1 | 4 | 2IN.AT$T | VH |  |  |  |  | 1.0633 | 1.0101 | 0.92 | 1.05 | 288 | P1_2-130 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
200720 | 18L | Approved | P1 | 4 | 2ANAVSOT! | VH |  |  |  |  | 1.0637 | 1.0013 | 0.92 | 1.05 | 288 | P1_2-130 | 334013 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
200721 | 18L | Approved | P1 | 4 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 347 | P1_2-189 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200722 | 18L | Approved | P1 | 4 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 347 | P1_2-189 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200723 | 18L | Approved | P1 | 4 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 347 | P1_2-189 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200724 | 18L | Approved | P1 | 4 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 347 | P1_2-189 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200725 | 18L | Approved | P1 | 4 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 347 | P1_2-189 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200726 | 18L | Approved | P1 | 4 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 347 | P1_2-189 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200727 | 18L | Approved | P1 | 4 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 347 | P1_2-189 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200728 | 18L | Approved | P1 | 4 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 347 | P1_2-189 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200729 | 18L | Approved | P1 | 4 | 4WOODVILLE | VH |  |  |  |  | 1.0536 | 1.0211 | 0.92 | 1.05 | 347 | P1_2-189 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! |  |  | VH
200730 | 18L | Approved | P1 | 4 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 348 | P1_2-190 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! |  |  | VH
200731 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0545 | 1.0418 | 0.92 | 1.05 | 377 | P1_2-219 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-219 |  |  | VH
200732 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0552 | 1.0418 | 0.92 | 1.05 | 378 | P1_2-220 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! |  |  | VH
200733 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.072 | 1.0418 | 0.92 | 1.05 | 379 | P1_2-221 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! |  |  | VH
200734 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0551 | 1.0418 | 0.92 | 1.05 | 380 | P1_2-222 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! |  |  | VH
200735 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0548 | 1.0418 | 0.92 | 1.05 | 381 | P1_2-223 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
200736 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0596 | 1.0418 | 0.92 | 1.05 | 387 | P1_2-229 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! |  |  | VH
200737 | 18L | Approved | P1 | 4 | 2HIMEX | VH |  |  |  |  | 1.0562 | 1.0418 | 0.92 | 1.05 | 391 | P1_2-233 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  |  | VH
200738 | 18L | Approved | P1 | 4 | 4CORIGAN! | VH |  |  |  |  | 1.0549 | 1.0242 | 0.92 | 1.05 | 412 | P1_2-254 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200739 | 18L | Approved | P1 | 4 | 4SHECORR | VH |  |  |  |  | 1.055 | 1.0237 | 0.92 | 1.05 | 412 | P1_2-254 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200740 | 18L | Approved | P1 | 4 | 4CAMDEN | VH |  |  |  |  | 1.0557 | 1.0221 | 0.92 | 1.05 | 412 | P1_2-254 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200741 | 18L | Approved | P1 | 4 | 4DEER 1 | VH |  |  |  |  | 1.0615 | 1.0209 | 0.92 | 1.05 | 412 | P1_2-254 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200742 | 18L | Approved | P1 | 4 | 4TURKEYCRK | VH |  |  |  |  | 1.0635 | 1.0207 | 0.92 | 1.05 | 412 | P1_2-254 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200743 | 18L | Approved | P1 | 4 | 4DOUCETT! | VH |  |  |  |  | 1.0638 | 1.0207 | 0.92 | 1.05 | 412 | P1_2-254 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200744 | 18L | Approved | P1 | 4 | 4FORK CK | VH |  |  |  |  | 1.0601 | 1.0207 | 0.92 | 1.05 | 412 | P1_2-254 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200745 | 18L | Approved | P1 | 4 | 4RAYBURN% | VH |  |  |  |  | 1.0548 | 1.0225 | 0.92 | 1.05 | 412 | P1_2-254 | 334282 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200746 | 18L | Approved | P1 | 4 | 4MILLCR! | VH |  |  |  |  | 1.0512 | 1.0202 | 0.92 | 1.05 | 412 | P1_2-254 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200747 | 18L | Approved | P1 | 4 | 2PINELND | VH |  |  |  |  | 1.0585 | 1.0264 | 0.92 | 1.05 | 412 | P1_2-254 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200748 | 18L | Approved | P1 | 4 | 2TEMPL1* | VH |  |  |  |  | 1.0577 | 1.0256 | 0.92 | 1.05 | 412 | P1_2-254 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200749 | 18L | Approved | P1 | 4 | 2TEMPLE1 | VH |  |  |  |  | 1.0576 | 1.0254 | 0.92 | 1.05 | 412 | P1_2-254 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200750 | 18L | Approved | P1 | 4 | 2TEMPL2* | VH |  |  |  |  | 1.0576 | 1.0255 | 0.92 | 1.05 | 412 | P1_2-254 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200751 | 18L | Approved | P1 | 4 | 2TEMPLE2 | VH |  |  |  |  | 1.0575 | 1.0254 | 0.92 | 1.05 | 412 | P1_2-254 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200752 | 18L | Approved | P1 | 4 | 2TMPLSWC | VH |  |  |  |  | 1.0576 | 1.0255 | 0.92 | 1.05 | 412 | P1_2-254 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  |  | VH
200753 | 18L | Approved | P1 | 4 | 2WEIRGAT | VH |  |  |  |  | 1.054 | 1.0216 | 0.92 | 1.05 | 412 | P1_2-254 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-254 |  | Project Proposed | VH | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200754 | 18L | Approved | P1 | 4 | 4URLAND! | VH |  |  |  |  | 1.0626 | 1.0213 | 0.92 | 1.05 | 412 | P1_2-254 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200755 | 18L | Approved | P1 | 4 | 4WOODVILLE | VH |  |  |  |  | 1.0629 | 1.0211 | 0.92 | 1.05 | 412 | P1_2-254 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200756 | 18L | Approved | P1 | 4 | 4WARREN! | VH |  |  |  |  | 1.0611 | 1.0224 | 0.92 | 1.05 | 412 | P1_2-254 | 334316 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200757 | 18L | Approved | P1 | 4 | 4JASPER | VH |  |  |  |  | 1.0544 | 1.0207 | 0.92 | 1.05 | 412 | P1_2-254 | 334330 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200758 | 18L | Approved | P1 | 4 | 4JASON | VH |  |  |  |  | 1.0528 | 1.019 | 0.92 | 1.05 | 412 | P1_2-254 | 334331 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-254 |  |  | VH
200759 | 18L | Approved | P1 | 4 | 2JACKSON! | VH |  |  |  |  | 1.1516 | 1.0213 | 0.92 | 1.05 | 916 | P1_2-758 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200760 | 18L | Approved | P1 | 4 | 2FELICIANA | VH |  |  |  |  | 1.1571 | 1.0143 | 0.92 | 1.05 | 916 | P1_2-758 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200761 | 18L | Approved | P1 | 4 | 2MCMANUS | VH |  |  |  |  | 1.1607 | 1.0101 | 0.92 | 1.05 | 916 | P1_2-758 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200762 | 18L | Approved | P1 | 4 | 2BRADY_HGHTS | VH |  |  |  |  | 1.157 | 1.0058 | 0.92 | 1.05 | 916 | P1_2-758 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200763 | 18L | Approved | P1 | 4 | 2CLINTON | VH |  |  |  |  | 1.1567 | 1.0054 | 0.92 | 1.05 | 916 | P1_2-758 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200764 | 18L | Approved | P1 | 4 | 2CLINTON_REA | VH |  |  |  |  | 1.157 | 1.0058 | 0.92 | 1.05 | 916 | P1_2-758 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200765 | 18L | Approved | P1 | 4 | 2TEJAC | VH |  |  |  |  | 1.1458 | 1.027 | 0.92 | 1.05 | 916 | P1_2-758 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200766 | 18L | Approved | P1 | 4 | 2MARYDALE | VH |  |  |  |  | 1.1396 | 1.0329 | 0.92 | 1.05 | 916 | P1_2-758 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200767 | 18L | Approved | P1 | 4 | 2FRANCIS! | VH |  |  |  |  | 1.1083 | 1.032 | 0.92 | 1.05 | 916 | P1_2-758 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200768 | 18L | Approved | P1 | 4 | 2ANGOLA | VH |  |  |  |  | 1.0945 | 1.017 | 0.92 | 1.05 | 916 | P1_2-758 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200769 | 18L | Approved | P1 | 4 | 2GRANT | VH |  |  |  |  | 1.0795 | 1.0255 | 0.92 | 1.05 | 916 | P1_2-758 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
200770 | 18L | Approved | P1 | 4 | 2JACKSON! | VH |  |  |  |  | 1.0937 | 1.0213 | 0.92 | 1.05 | 923 | P1_2-765 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200771 | 18L | Approved | P1 | 4 | 2FELICIANA | VH |  |  |  |  | 1.0982 | 1.0143 | 0.92 | 1.05 | 923 | P1_2-765 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200772 | 18L | Approved | P1 | 4 | 2MCMANUS | VH |  |  |  |  | 1.1012 | 1.0101 | 0.92 | 1.05 | 923 | P1_2-765 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200773 | 18L | Approved | P1 | 4 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0973 | 1.0058 | 0.92 | 1.05 | 923 | P1_2-765 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200774 | 18L | Approved | P1 | 4 | 2CLINTON | VH |  |  |  |  | 1.097 | 1.0054 | 0.92 | 1.05 | 923 | P1_2-765 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200775 | 18L | Approved | P1 | 4 | 2CLINTON_REA | VH |  |  |  |  | 1.0973 | 1.0058 | 0.92 | 1.05 | 923 | P1_2-765 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200776 | 18L | Approved | P1 | 4 | 2TEJAC | VH |  |  |  |  | 1.1044 | 1.027 | 0.92 | 1.05 | 923 | P1_2-765 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200777 | 18L | Approved | P1 | 4 | 2MARYDALE | VH |  |  |  |  | 1.1157 | 1.0329 | 0.92 | 1.05 | 923 | P1_2-765 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200778 | 18L | Approved | P1 | 4 | 2FRANCIS! | VH |  |  |  |  | 1.1253 | 1.032 | 0.92 | 1.05 | 923 | P1_2-765 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200779 | 18L | Approved | P1 | 4 | 2ANGOLA | VH |  |  |  |  | 1.1117 | 1.017 | 0.92 | 1.05 | 923 | P1_2-765 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
200780 | 18L | Approved | P1 | 4 | 3GMEADW! | VH |  |  |  |  | 1.1709 | 1.0185 | 0.92 | 1.05 | 966 | P1_2-808 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
200781 | 18L | Approved | P1 | 4 | 3LEEVLL | VH |  |  |  |  | 1.1952 | 1.0114 | 0.92 | 1.05 | 966 | P1_2-808 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
200782 | 18L | Approved | P1 | 4 | 3FOURCHN | VH |  |  |  |  | 1.1949 | 1.0018 | 0.92 | 1.05 | 966 | P1_2-808 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
200783 | 18L | Approved | P1 | 4 | 6TUNICA! | VH |  |  |  |  | 1.0502 | 1.0354 | 0.92 | 1.05 | 1318 | P1_2-1160 | 337160 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! |  |  | VH
200784 | 18L | Approved | P1 | 4 | 5HORN LAKE% | VH |  |  |  |  | 1.0518 | 1.0667 | 0.92 | 1.05 | 1320 | P1_2-1162 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% |  |  | VH
200785 | 18L | Approved | P1 | 4 | 3BLACK_RIV | VH |  |  |  |  | 1.09 | 0.9963 | 0.92 | 1.05 | 1339 | P1_2-1181 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200786 | 18L | Approved | P1 | 4 | 3GILBERT | VH |  |  |  |  | 1.2261 | 1.0234 | 0.92 | 1.05 | 1339 | P1_2-1181 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200787 | 18L | Approved | P1 | 4 | 3PERSIM_MIL | VH |  |  |  |  | 1.1154 | 1.0237 | 0.92 | 1.05 | 1339 | P1_2-1181 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200788 | 18L | Approved | P1 | 4 | 3NATCHEZSES% | VH |  |  |  |  | 1.1236 | 1.034 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200789 | 18L | Approved | P1 | 4 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1233 | 1.034 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200790 | 18L | Approved | P1 | 4 | 3PINE RIDGE | VH |  |  |  |  | 1.1231 | 1.0339 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200791 | 18L | Approved | P1 | 4 | 3NATCHEZ! | VH |  |  |  |  | 1.1227 | 1.0347 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200792 | 18L | Approved | P1 | 4 | 3J.MANVILLE | VH |  |  |  |  | 1.1209 | 1.0333 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200793 | 18L | Approved | P1 | 4 | 3INTL PAPER | VH |  |  |  |  | 1.1199 | 1.0328 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200794 | 18L | Approved | P1 | 4 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1192 | 1.0324 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200795 | 18L | Approved | P1 | 4 | 3NATCHEZ IND | VH |  |  |  |  | 1.1175 | 1.0315 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200796 | 18L | Approved | P1 | 4 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1152 | 1.032 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200797 | 18L | Approved | P1 | 4 | 3CROSBY+ | VH |  |  |  |  | 1.093 | 1.0276 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200798 | 18L | Approved | P1 | 4 | 3GLOSTER | VH |  |  |  |  | 1.0865 | 1.0265 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200799 | 18L | Approved | P1 | 4 | 3LIBERTY P/L | VH |  |  |  |  | 1.0564 | 1.0357 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200800 | 18L | Approved | P1 | 4 | 3WOODVILLE | VH |  |  |  |  | 1.0666 | 1.0052 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200801 | 18L | Approved | P1 | 4 | 3LIBERTY! | VH |  |  |  |  | 1.0565 | 1.0357 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200802 | 18L | Approved | P1 | 4 | 3INTRSTE P/L | VH |  |  |  |  | 1.0565 | 1.0357 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200803 | 18L | Approved | P1 | 4 | 3KINGSTON MS | VH |  |  |  |  | 1.114 | 1.0307 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200804 | 18L | Approved | P1 | 4 | 3CENTREVILLE | VH |  |  |  |  | 1.0723 | 1.0113 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200805 | 18L | Approved | P1 | 4 | 3WASHINGTON+ | VH |  |  |  |  | 1.1157 | 1.0329 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200806 | 18L | Approved | P1 | 4 | 3ROXIE | VH |  |  |  |  | 1.0909 | 1.0323 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200807 | 18L | Approved | P1 | 4 | 3MEADVILLE | VH |  |  |  |  | 1.0717 | 1.0338 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200808 | 18L | Approved | P1 | 4 | 3CRANFIELD+ | VH |  |  |  |  | 1.107 | 1.0322 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200809 | 18L | Approved | P1 | 4 | 3FAYETTE | VH |  |  |  |  | 1.1152 | 1.0326 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200810 | 18L | Approved | P1 | 4 | 3LORMAN+ | VH |  |  |  |  | 1.0962 | 1.0335 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200811 | 18L | Approved | P1 | 4 | 3LORMAN | VH |  |  |  |  | 1.0961 | 1.0334 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200812 | 18L | Approved | P1 | 4 | 3PORTGIBSON! | VH |  |  |  |  | 1.0835 | 1.0373 | 0.92 | 1.05 | 1339 | P1_2-1181 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200813 | 18L | Approved | P1 | 4 | 3GGNS | VH |  |  |  |  | 1.0825 | 1.0362 | 0.975 | 1.05 | 1339 | P1_2-1181 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200814 | 18L | Approved | P1 | 4 | 3BLACK_RIVER | VH |  |  |  |  | 1.09 | 0.9963 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200815 | 18L | Approved | P1 | 4 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1145 | 1.0233 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200816 | 18L | Approved | P1 | 4 | 3PLANTATION! | VH |  |  |  |  | 1.1097 | 1.0273 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200817 | 18L | Approved | P1 | 4 | 3VIDALIA_LA | VH |  |  |  |  | 1.1114 | 1.0276 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200818 | 18L | Approved | P1 | 4 | 3RED_GUM! | VH |  |  |  |  | 1.136 | 1.034 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200819 | 18L | Approved | P1 | 4 | 3METROPOLIS | VH |  |  |  |  | 1.214 | 1.0252 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200820 | 18L | Approved | P1 | 4 | 3WISNER | VH |  |  |  |  | 1.2195 | 1.0247 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200821 | 18L | Approved | P1 | 4 | 3WINNSBORO! | VH |  |  |  |  | 1.2413 | 1.0244 | 0.92 | 1.05 | 1339 | P1_2-1181 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200822 | 18L | Approved | P1 | 4 | JNESVIL3 | VH |  |  |  |  | 1.09 | 0.9963 | 0.92 | 1.05 | 1339 | P1_2-1181 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200823 | 18L | Approved | P1 | 4 | VIDALIA3 | VH |  |  |  |  | 1.1114 | 1.0276 | 0.92 | 1.05 | 1339 | P1_2-1181 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
200824 | 18L | Approved | P1 | 4 | 3DELHI_LA! | VH |  |  |  |  | 1.0543 | 1.0187 | 0.92 | 1.05 | 1415 | P1_2-1257 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! |  |  | VH
200825 | 18L | Approved | P1 | 4 | 3RICUSKEY! | VH |  |  |  |  | 1.0518 | 1.0394 | 0.92 | 1.05 | 1459 | P1_2-1301 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! |  |  | VH
200826 | 18L | Approved | P1 | 4 | 2DELUCE | VH |  |  |  |  | 1.0575 | 1.0466 | 0.92 | 1.05 | 1459 | P1_2-1301 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! |  |  | VH
200827 | 18L | Approved | P1 | 4 | 8ETTA% | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 1508 | P1_2-1350 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
200828 | 18L | Approved | P1 | 4 | 8DUKE HS-1! | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 1508 | P1_2-1350 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
200829 | 18L | Approved | P1 | 4 | 8DUKE HS-2! | VH |  |  |  |  | 1.0596 | 1.0341 | 0.92 | 1.05 | 1508 | P1_2-1350 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
200830 | 18L | Approved | P1 | 4 | 8HOLND BTM% | VH |  |  |  |  | 1.0532 | 1.0342 | 0.92 | 1.05 | 1600 | P1_2-1442 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
200831 | 18L | Approved | P1 | 4 | 8ISES-XF | VH |  |  |  |  | 1.0553 | 1.0439 | 0.92 | 1.05 | 1600 | P1_2-1442 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
200832 | 18L | Approved | P1 | 4 | 8ISES% | VH |  |  |  |  | 1.0554 | 1.0439 | 0.92 | 1.05 | 1600 | P1_2-1442 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
200833 | 18L | Approved | P1 | 4 | 2WARD | VH |  |  |  |  | 1.0624 | 1.0493 | 0.92 | 1.05 | 1600 | P1_2-1442 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
200834 | 18L | Approved | P1 | 4 | 3STUTGART.N+ | VH |  |  |  |  | 1.0503 | 1.0357 | 0.92 | 1.05 | 1604 | P1_2-1446 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
200835 | 18L | Approved | P1 | 4 | 3RICUSKEY! | VH |  |  |  |  | 1.0546 | 1.0394 | 0.92 | 1.05 | 1604 | P1_2-1446 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
200836 | 18L | Approved | P1 | 4 | 2DELUCE | VH |  |  |  |  | 1.0597 | 1.0466 | 0.92 | 1.05 | 1604 | P1_2-1446 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
200837 | 18L | Approved | P1 | 4 | 2WYNNE.E | VH |  |  |  |  | 1.0567 | 1.0451 | 0.92 | 1.05 | 1616 | P1_2-1458 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% |  |  | VH
200838 | 18L | Approved | P1 | 4 | 8ISES-XF | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 1649 | P1_2-1494 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% |  |  | VH
200839 | 18L | Approved | P1 | 4 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 1649 | P1_2-1494 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% |  |  | VH
200840 | 18L | Approved | P1 | 4 | 2BLACK ROCK | VH |  |  |  |  | 1.0585 | 1.0691 | 0.92 | 1.05 | 1650 | P1_2-1495 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1495_8ISES%,8DELL% |  |  | VH
200841 | 18L | Approved | P1 | 4 | 3SEDGWICK | VH |  |  |  |  | 1.0598 | 1.0484 | 0.92 | 1.05 | 1690 | P1_2-1535 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
200842 | 18L | Approved | P1 | 4 | 3T.E.P/S-7 | VH |  |  |  |  | 1.051 | 1.0396 | 0.92 | 1.05 | 1690 | P1_2-1535 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
200843 | 18L | Approved | P1 | 4 | 3WALNUT RDG! | VH |  |  |  |  | 1.0601 | 1.0461 | 0.92 | 1.05 | 1690 | P1_2-1535 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
200844 | 18L | Approved | P1 | 4 | 8LAG CRK CT | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 1715 | P1_2-1560 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% |  |  | VH
200845 | 18L | Approved | P1 | 4 | 8LAG CRK CC | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 1715 | P1_2-1560 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% |  |  | VH
200846 | 18L | Approved | P1 | 4 | 8WEAKLEY TN | VH |  |  |  |  | 1.0921 | 1.0777 | 0.92 | 1.05 | 1720 | P1_2-1565 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
200847 | 18L | Approved | P1 | 4 | 8LAG CRK CT | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 1720 | P1_2-1565 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
200848 | 18L | Approved | P1 | 4 | 8GLEASON CT | VH |  |  |  |  | 1.0922 | 1.0802 | 0.92 | 1.05 | 1720 | P1_2-1565 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
200849 | 18L | Approved | P1 | 4 | 8LAG CRK CC | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 1720 | P1_2-1565 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
200850 | 18L | Approved | P1 | 4 | 5HORN LAKE% | VH |  |  |  |  | 1.0518 | 1.0667 | 0.92 | 1.05 | 1722 | P1_2-1567 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! |  |  | VH
200851 | 18L | Approved | P1 | 4 | 8CHOCTAW CC | VH |  |  |  |  | 1.0529 | 1.0348 | 0.92 | 1.05 | 1746 | P1_2-1591 | 360627 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% |  |  | VH
200852 | 18L | Approved | P1 | 4 | 8CHOCTAW MS | VH |  |  |  |  | 1.0529 | 1.0348 | 0.92 | 1.05 | 1746 | P1_2-1591 | 360654 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% |  |  | VH
200853 | 18L | Approved | P1 | 4 | 8DANIEL | VH |  |  |  |  | 1.0812 | 1.0292 | 0.92 | 1.05 | 1762 | P1_2-1607 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! |  |  | VH
200854 | 18L | Approved | P1 | 4 | PNPRARIE 4 | VL |  |  |  |  | 0.9157 | 1.0028 | 0.92 | 1.05 | 1811 | P1_2-1656 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
200855 | 18L | Approved | P1 | 4 | TENRUSK7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 2021 | P1_2-1866 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
200856 | 18L | Approved | P1 | 4 | TENGEN 7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 2021 | P1_2-1866 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
200857 | 18L | Approved | P1 | 4 | FTSMITH7 | VH |  |  |  |  | 1.0537 | 1.0373 | 0.92 | 1.05 | 2047 | P1_2-1892 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | P1_2-1892_FTSMITH7%,FTSMITH8% |  |  | VH
200858 | 18S | Approved | P0 | 5 | 5HORN LAKE% | VH |  |  |  |  | 1.057 | 1.057 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
200859 | 18S | Approved | P0 | 5 | 7CLINTON | VH |  |  |  |  | 1.05 | 1.05 | 0.95 | 1.05 | 0 | ** Base Case ** | 348846 |  |  |  | 345 | 345 | 357 | AMIL |  |  | ** Base Case ** |  |  | VH
200860 | 18S | Approved | P0 | 5 | 8E POINT AL | VH |  |  |  |  | 1.0537 | 1.0537 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200861 | 18S | Approved | P0 | 5 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
200862 | 18S | Approved | P0 | 5 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
200863 | 18S | Approved | P1 | 5 | 3BLACK_RIV | VL |  |  |  |  | 0.9044 | 0.9835 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200864 | 18S | Approved | P1 | 5 | 3FAYETTE | VL |  |  |  |  | 0.886 | 1.0272 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200865 | 18S | Approved | P1 | 5 | 3LORMAN+ | VL |  |  |  |  | 0.8601 | 1.018 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200866 | 18S | Approved | P1 | 5 | 3LORMAN | VL |  |  |  |  | 0.8599 | 1.0178 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200867 | 18S | Approved | P1 | 5 | 3PORTGIBSON! | VL |  |  |  |  | 0.8465 | 1.0174 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200868 | 18S | Approved | P1 | 5 | 3GGNS | VL |  |  |  |  | 0.8452 | 1.0163 | 0.975 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200869 | 18S | Approved | P1 | 5 | 3S.VICKSBURG | VL |  |  |  |  | 0.8409 | 1.0201 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200870 | 18S | Approved | P1 | 5 | 3BLACK_RIVER | VL |  |  |  |  | 0.9044 | 0.9835 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200871 | 18S | Approved | P1 | 5 | JNESVIL3 | VL |  |  |  |  | 0.9044 | 0.9835 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
200873 | 18S | Approved | P1 | 5 | 3 34TH&MAIN | VL |  |  |  |  | 0.9157 | 0.9497 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200874 | 18S | Approved | P1 | 5 | 3PINEBLUF.E% | VL |  |  |  |  | 0.906 | 0.948 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200875 | 18S | Approved | P1 | 5 | 3MCCAMANT! | VL |  |  |  |  | 0.9037 | 0.9533 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200876 | 18S | Approved | P1 | 5 | 3PINEBLUF.W | VL |  |  |  |  | 0.9037 | 0.9565 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337626 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200877 | 18S | Approved | P1 | 5 | 3PB IP SS% | VL |  |  |  |  | 0.9031 | 0.9419 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200878 | 18S | Approved | P1 | 5 | 3PB IP! | VL |  |  |  |  | 0.9024 | 0.9413 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200879 | 18S | Approved | P1 | 5 | 3PB PORT | VL |  |  |  |  | 0.9026 | 0.9415 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200880 | 18S | Approved | P1 | 5 | 3PB ENERGY! | VL |  |  |  |  | 0.9025 | 0.9414 | 0.92 | 1.05 | 518 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200881 | 18S | Approved | P1 | 5 | 3PB IP SS% | VL |  |  |  |  | 0.9178 | 0.9419 | 0.92 | 1.05 | 529 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200882 | 18S | Approved | P1 | 5 | 3PB IP! | VL |  |  |  |  | 0.9172 | 0.9413 | 0.92 | 1.05 | 529 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200883 | 18S | Approved | P1 | 5 | 3PB PORT | VL |  |  |  |  | 0.9174 | 0.9415 | 0.92 | 1.05 | 529 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200884 | 18S | Approved | P1 | 5 | 3PB ENERGY! | VL |  |  |  |  | 0.9173 | 0.9414 | 0.92 | 1.05 | 529 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200885 | 18S | Approved | P1 | 5 | 3PB IP SS% | VL |  |  |  |  | 0.9143 | 0.9419 | 0.92 | 1.05 | 530 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200886 | 18S | Approved | P1 | 5 | 3PB IP! | VL |  |  |  |  | 0.9137 | 0.9413 | 0.92 | 1.05 | 530 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200887 | 18S | Approved | P1 | 5 | 3PB PORT | VL |  |  |  |  | 0.9138 | 0.9415 | 0.92 | 1.05 | 530 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200888 | 18S | Approved | P1 | 5 | 3PB ENERGY! | VL |  |  |  |  | 0.9138 | 0.9414 | 0.92 | 1.05 | 530 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200889 | 18S | Approved | P1 | 5 | 3 34TH&MAIN | VL |  |  |  |  | 0.9157 | 0.9497 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200890 | 18S | Approved | P1 | 5 | 3PINEBLUF.E% | VL |  |  |  |  | 0.906 | 0.948 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200891 | 18S | Approved | P1 | 5 | 3MCCAMANT! | VL |  |  |  |  | 0.9037 | 0.9533 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200892 | 18S | Approved | P1 | 5 | 3PB IP SS% | VL |  |  |  |  | 0.903 | 0.9419 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200893 | 18S | Approved | P1 | 5 | 3PB IP! | VL |  |  |  |  | 0.9024 | 0.9413 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200894 | 18S | Approved | P1 | 5 | 3PB PORT | VL |  |  |  |  | 0.9025 | 0.9415 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200895 | 18S | Approved | P1 | 5 | 3PB ENERGY! | VL |  |  |  |  | 0.9024 | 0.9414 | 0.92 | 1.05 | 531 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200896 | 18S | Approved | P1 | 5 | 3PB IP SS% | VL |  |  |  |  | 0.9166 | 0.9419 | 0.92 | 1.05 | 552 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200897 | 18S | Approved | P1 | 5 | 3PB IP! | VL |  |  |  |  | 0.916 | 0.9413 | 0.92 | 1.05 | 552 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200898 | 18S | Approved | P1 | 5 | 3PB PORT | VL |  |  |  |  | 0.9161 | 0.9415 | 0.92 | 1.05 | 552 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200899 | 18S | Approved | P1 | 5 | 3PB ENERGY! | VL |  |  |  |  | 0.916 | 0.9414 | 0.92 | 1.05 | 552 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200900 | 18S | Approved | P2 | 5 | 3MALVERN.S | VL |  |  |  |  | 0.9117 | 0.9711 | 0.92 | 1.05 | 603 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337746 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200901 | 18S | Approved | P2 | 5 | 3T.E.P/S-4+ | VL |  |  |  |  | 0.9131 | 0.97 | 0.92 | 1.05 | 603 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337747 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200902 | 18S | Approved | P2 | 5 | 3T.E.P/S-4 | VL |  |  |  |  | 0.9039 | 0.9618 | 0.92 | 1.05 | 603 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337748 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
200903 | 18S | Approved | P2 | 5 | 3BRYANT | VL |  |  |  |  | 0.916 | 0.9684 | 0.92 | 1.05 | 621 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337803 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
200904 | 18S | Approved | P2 | 5 | 3ALCOA RD | VL |  |  |  |  | 0.9191 | 0.9635 | 0.92 | 1.05 | 621 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 338433 |  |  |  | 115 | 115 | 336 | BUBA |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
200905 | 18S | Approved | P2 | 5 | 3BRYANT.S# | VL |  |  |  |  | 0.9172 | 0.9669 | 0.92 | 1.05 | 621 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 338757 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
200906 | 18S | Approved | P2 | 5 | 3BAUCUM | VL |  |  |  |  | 0.9123 | 0.9774 | 0.92 | 1.05 | 724 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 337956 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200907 | 18S | Approved | P2 | 5 | 3ENGLAND# | VL |  |  |  |  | 0.9179 | 0.9634 | 0.92 | 1.05 | 724 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 338753 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200908 | 18S | Approved | P2 | 5 | 3KEO# | VL |  |  |  |  | 0.9155 | 0.9669 | 0.92 | 1.05 | 724 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 338754 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200909 | 18S | Approved | P2 | 5 | 3STUTGART.N+ | VL |  |  |  |  | 0.918 | 0.9884 | 0.92 | 1.05 | 736 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200910 | 18S | Approved | P2 | 5 | 3STUTGART.N | VL |  |  |  |  | 0.9159 | 0.9865 | 0.92 | 1.05 | 736 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
200911 | 18S | Approved | P1 | 5 | 3STUTGART.N+ | VL |  |  |  |  | 0.9103 | 0.9884 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200912 | 18S | Approved | P1 | 5 | 3STUTGART.N | VL |  |  |  |  | 0.9082 | 0.9865 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200913 | 18S | Approved | P1 | 5 | 3RICUSKEY! | VL |  |  |  |  | 0.9105 | 0.9934 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200914 | 18S | Approved | P1 | 5 | 3STUTGART IN | VL |  |  |  |  | 0.9098 | 0.9883 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200915 | 18S | Approved | P1 | 5 | 3ULM | VL |  |  |  |  | 0.9172 | 0.9875 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200916 | 18S | Approved | P1 | 5 | 3ALMYRA | VL |  |  |  |  | 0.9082 | 0.977 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200917 | 18S | Approved | P1 | 5 | 3DEWITT | VL |  |  |  |  | 0.9098 | 0.9678 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200918 | 18S | Approved | P1 | 5 | 3HUMPHREY# | VL |  |  |  |  | 0.9151 | 0.9791 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200919 | 18S | Approved | P1 | 5 | 3DELUCE# | VL |  |  |  |  | 0.915 | 0.9648 | 0.92 | 1.05 | 738 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200920 | 18S | Approved | P2 | 5 | 3STUTGART IN | VL |  |  |  |  | 0.8957 | 0.9883 | 0.92 | 1.05 | 739 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
200921 | 18S | Approved | P2 | 5 | 3ULM | VL |  |  |  |  | 0.9042 | 0.9875 | 0.92 | 1.05 | 739 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
200922 | 18S | Approved | P2 | 5 | 3ALMYRA | VL |  |  |  |  | 0.7691 | 0.977 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200923 | 18S | Approved | P2 | 5 | 3DEWITT | VL |  |  |  |  | 0.7727 | 0.9678 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200924 | 18S | Approved | P2 | 5 | 3GILLETT! | VL |  |  |  |  | 0.7888 | 0.9663 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200925 | 18S | Approved | P2 | 5 | 3ELAINE | VL |  |  |  |  | 0.8349 | 0.9668 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200926 | 18S | Approved | P2 | 5 | 3MARVELL | VL |  |  |  |  | 0.8686 | 0.9689 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200927 | 18S | Approved | P2 | 5 | 3BARTON | VL |  |  |  |  | 0.8829 | 0.9695 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200928 | 18S | Approved | P2 | 5 | 3HELENA.W+ | VL |  |  |  |  | 0.9112 | 0.9707 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200929 | 18S | Approved | P2 | 5 | 2DELUCE | VL |  |  |  |  | 0.8011 | 0.9896 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200930 | 18S | Approved | P2 | 5 | 3DELUCE# | VL |  |  |  |  | 0.7811 | 0.9648 | 0.92 | 1.05 | 740 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200931 | 18S | Approved | P1 | 5 | 3DEWITT | VL |  |  |  |  | 0.8908 | 0.9678 | 0.92 | 1.05 | 745 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200932 | 18S | Approved | P1 | 5 | 3GILLETT! | VL |  |  |  |  | 0.8992 | 0.9663 | 0.92 | 1.05 | 745 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200933 | 18S | Approved | P1 | 5 | 3ELAINE | VL |  |  |  |  | 0.9188 | 0.9668 | 0.92 | 1.05 | 745 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200934 | 18S | Approved | P1 | 5 | 2DELUCE | VL |  |  |  |  | 0.9172 | 0.9896 | 0.92 | 1.05 | 745 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200935 | 18S | Approved | P1 | 5 | 3DELUCE# | VL |  |  |  |  | 0.8943 | 0.9648 | 0.92 | 1.05 | 745 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200936 | 18S | Approved | P1 | 5 | 3ELAINE | VL |  |  |  |  | 0.9066 | 0.9668 | 0.92 | 1.05 | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200937 | 18S | Approved | P1 | 5 | 3MARVELL | VL |  |  |  |  | 0.9002 | 0.9689 | 0.92 | 1.05 | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200938 | 18S | Approved | P1 | 5 | 3BARTON | VL |  |  |  |  | 0.8979 | 0.9695 | 0.92 | 1.05 | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200939 | 18S | Approved | P1 | 5 | 3HELENA.W+ | VL |  |  |  |  | 0.8941 | 0.9707 | 0.92 | 1.05 | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200940 | 18S | Approved | P1 | 5 | 3HELENA.C | VL |  |  |  |  | 0.8926 | 0.9711 | 0.92 | 1.05 | 753 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200941 | 18S | Approved | P1 | 5 | 3GILLETT! | VL |  |  |  |  | 0.9165 | 0.9663 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200942 | 18S | Approved | P1 | 5 | 3ELAINE | VL |  |  |  |  | 0.8909 | 0.9668 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200943 | 18S | Approved | P1 | 5 | 3MARVELL | VL |  |  |  |  | 0.8832 | 0.9689 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200944 | 18S | Approved | P1 | 5 | 3BARTON | VL |  |  |  |  | 0.8806 | 0.9695 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200945 | 18S | Approved | P1 | 5 | 3HELENA.W+ | VL |  |  |  |  | 0.8762 | 0.9707 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200946 | 18S | Approved | P1 | 5 | 3HELENA.C | VL |  |  |  |  | 0.8745 | 0.9711 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200947 | 18S | Approved | P1 | 5 | 3HELENA IN#! | VL |  |  |  |  | 0.8742 | 0.9734 | 0.92 | 1.05 | 756 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
200948 | 18S | Approved | P2 | 5 | 3CABOT | VL |  |  |  |  | 0.8542 | 0.9906 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338006 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200949 | 18S | Approved | P2 | 5 | 3BEEBE | VL |  |  |  |  | 0.8714 | 0.9845 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200950 | 18S | Approved | P2 | 5 | 3GARNER+ | VL |  |  |  |  | 0.8873 | 0.9892 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200951 | 18S | Approved | P2 | 5 | 3T.E.P/S-MC | VL |  |  |  |  | 0.8871 | 0.9891 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200952 | 18S | Approved | P2 | 5 | 3SRCY PRICE! | VL |  |  |  |  | 0.9152 | 0.9956 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200953 | 18S | Approved | P2 | 5 | 3T.E.P/S-6 | VL |  |  |  |  | 0.91 | 0.9632 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200954 | 18S | Approved | P2 | 5 | 2WARD | VL |  |  |  |  | 0.8749 | 1.009 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200955 | 18S | Approved | P2 | 5 | 3WARD# | VL |  |  |  |  | 0.853 | 0.9838 | 0.92 | 1.05 | 774 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200956 | 18S | Approved | P1 | 5 | 3BEEBE | VL |  |  |  |  | 0.9097 | 0.9845 | 0.92 | 1.05 | 775 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200957 | 18S | Approved | P1 | 5 | 2WARD | VL |  |  |  |  | 0.9143 | 1.009 | 0.92 | 1.05 | 775 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200958 | 18S | Approved | P1 | 5 | 3WARD# | VL |  |  |  |  | 0.8914 | 0.9838 | 0.92 | 1.05 | 775 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
200959 | 18S | Approved | P2 | 5 | 5WYNNE.E# | VL |  |  |  |  | 0.9199 | 0.9765 | 0.92 | 1.05 | 803 | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 | 338883 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 |  | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
200960 | 18S | Approved | P1 | 5 | 2HARRISON.S | VH |  |  |  |  | 1.0507 | 1.0346 | 0.92 | 1.05 | 817 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
200961 | 18S | Approved | P1 | 5 | 8SANS SOUCI% | VH |  |  |  |  | 1.0539 | 1.0373 | 0.92 | 1.05 | 889 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
200962 | 18S | Approved | P1 | 5 | 2THAYER.N | VL |  |  |  |  | 0.9103 | 1.0183 | 0.92 | 1.05 | 919 | 338216 2THAYER.S! 69.0 338217 2THAYER.N 69.0 1 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338216 2THAYER.S! 69.0 338217 2THAYER.N 69.0 1 |  | Turn on Switch shunt at Couch 69 kV sub
200963 | 18S | Approved | P1 | 5 | 5POCHNTAS.N | VL |  |  |  |  | 0.8503 | 0.9766 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200964 | 18S | Approved | P1 | 5 | 5DATTO | VL |  |  |  |  | 0.8446 | 0.969 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200965 | 18S | Approved | P1 | 5 | 3DATTO | VL |  |  |  |  | 0.8648 | 0.9921 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200966 | 18S | Approved | P1 | 5 | 3CORNING | VL |  |  |  |  | 0.8605 | 0.9836 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200967 | 18S | Approved | P1 | 5 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8498 | 0.9761 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200968 | 18S | Approved | P1 | 5 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8497 | 0.9756 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200969 | 18S | Approved | P1 | 5 | 3CORNING.N# | VL |  |  |  |  | 0.8609 | 0.9845 | 0.92 | 1.05 | 923 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200970 | 18S | Approved | P1 | 5 | 5DATTO | VL |  |  |  |  | 0.8786 | 0.969 | 0.92 | 1.05 | 924 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200971 | 18S | Approved | P1 | 5 | 3DATTO | VL |  |  |  |  | 0.9056 | 0.9921 | 0.92 | 1.05 | 924 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200972 | 18S | Approved | P1 | 5 | 3CORNING | VL |  |  |  |  | 0.9078 | 0.9836 | 0.92 | 1.05 | 924 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200973 | 18S | Approved | P1 | 5 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8766 | 0.9761 | 0.92 | 1.05 | 924 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200974 | 18S | Approved | P1 | 5 | 3CORNING.N# | VL |  |  |  |  | 0.9075 | 0.9845 | 0.92 | 1.05 | 924 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200975 | 18S | Approved | P1 | 5 | 2IMBODEN! | VL |  |  |  |  | 0.8557 | 0.9763 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338221 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200976 | 18S | Approved | P1 | 5 | 2WTR VALLEY! | VL |  |  |  |  | 0.8555 | 0.976 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338222 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200977 | 18S | Approved | P1 | 5 | 5WTR VALLEY+ | VL |  |  |  |  | 0.855 | 0.9755 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338223 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200978 | 18S | Approved | P1 | 5 | 5WTR VALLEY | VL |  |  |  |  | 0.855 | 0.9755 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338224 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200979 | 18S | Approved | P1 | 5 | 5POCHNTAS.N | VL |  |  |  |  | 0.8555 | 0.9766 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200980 | 18S | Approved | P1 | 5 | 5DATTO | VL |  |  |  |  | 0.8493 | 0.969 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200981 | 18S | Approved | P1 | 5 | 3DATTO | VL |  |  |  |  | 0.8693 | 0.9921 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200982 | 18S | Approved | P1 | 5 | 3CORNING | VL |  |  |  |  | 0.8644 | 0.9836 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200983 | 18S | Approved | P1 | 5 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8551 | 0.9761 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200984 | 18S | Approved | P1 | 5 | 5POCHNTAS.W# | VL |  |  |  |  | 0.855 | 0.9756 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200985 | 18S | Approved | P1 | 5 | 3CORNING.N# | VL |  |  |  |  | 0.8648 | 0.9845 | 0.92 | 1.05 | 1079 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
200986 | 18S | Approved | P1 | 5 | 2CALVERT! | VL |  |  |  |  | 0.8415 | 0.9805 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200987 | 18S | Approved | P1 | 5 | 2SINHERN | VL |  |  |  |  | 0.8747 | 1.0002 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200988 | 18S | Approved | P1 | 5 | 2HEARNE! | VL |  |  |  |  | 0.9068 | 1.0191 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200989 | 18S | Approved | P1 | 5 | 2TXHEARN | VL |  |  |  |  | 0.907 | 1.0196 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200990 | 18S | Approved | P1 | 5 | 2APLHERN | VL |  |  |  |  | 0.9076 | 1.0207 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200991 | 18S | Approved | P1 | 5 | 2BRYAN A! | VL |  |  |  |  | 0.9125 | 1.0257 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200992 | 18S | Approved | P1 | 5 | 2HUMBHRN | VL |  |  |  |  | 0.9138 | 1.0199 | 0.92 | 1.05 | 1093 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
200993 | 18S | Approved | P1 | 5 | 4NEWCANY! | VL |  |  |  |  | 0.9124 | 0.9714 | 0.92 | 1.05 | 1184 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
200994 | 18S | Approved | P1 | 5 | 4MILLCR! | VL |  |  |  |  | 0.9045 | 0.9951 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200995 | 18S | Approved | P1 | 5 | 4PINELND | VL |  |  |  |  | 0.8977 | 0.9785 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200996 | 18S | Approved | P1 | 5 | 4BROADUS | VL |  |  |  |  | 0.8935 | 0.9749 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200997 | 18S | Approved | P1 | 5 | 4ETOIL | VL |  |  |  |  | 0.8918 | 0.9734 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200998 | 18S | Approved | P1 | 5 | 4HRTNHIL | VL |  |  |  |  | 0.8999 | 0.9858 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
200999 | 18S | Approved | P1 | 5 | 2PINELND | VL |  |  |  |  | 0.913 | 0.9871 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201000 | 18S | Approved | P1 | 5 | 2TEMPL1* | VL |  |  |  |  | 0.9112 | 0.9855 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201001 | 18S | Approved | P1 | 5 | 2TEMPLE1 | VL |  |  |  |  | 0.9109 | 0.9852 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201002 | 18S | Approved | P1 | 5 | 2TEMPL2* | VL |  |  |  |  | 0.9109 | 0.9853 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201003 | 18S | Approved | P1 | 5 | 2TEMPLE2 | VL |  |  |  |  | 0.9108 | 0.9851 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201004 | 18S | Approved | P1 | 5 | 2TMPLSWC | VL |  |  |  |  | 0.9109 | 0.9852 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201005 | 18S | Approved | P1 | 5 | 2WEIRGAT | VL |  |  |  |  | 0.9004 | 0.9758 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201006 | 18S | Approved | P1 | 5 | 4PEACH! | VL |  |  |  |  | 0.9134 | 0.9937 | 0.92 | 1.05 | 1292 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201007 | 18S | Approved | P1 | 5 | 2SABRA | VL |  |  |  |  | 0.9116 | 0.9901 | 0.92 | 1.05 | 1551 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334704 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201008 | 18S | Approved | P1 | 5 | 2DEWEYVL! | VL |  |  |  |  | 0.9122 | 0.9816 | 0.92 | 1.05 | 1551 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201009 | 18S | Approved | P1 | 5 | 2SKBVREG | VL |  |  |  |  | 0.9139 | 0.9833 | 0.92 | 1.05 | 1551 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201010 | 18S | Approved | P1 | 5 | 2DEWEYVL! | VL |  |  |  |  | 0.9176 | 0.9816 | 0.92 | 1.05 | 1553 | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201011 | 18S | Approved | P1 | 5 | 2SKBVREG | VL |  |  |  |  | 0.9193 | 0.9833 | 0.92 | 1.05 | 1553 | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201012 | 18S | Approved | P1 | 5 | 4LEBLANC! | VL |  |  |  |  | 0.9048 | 0.9679 | 0.92 | 1.05 | 1791 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201013 | 18S | Approved | P1 | 5 | 4DELCAMBRE | VL |  |  |  |  | 0.9043 | 0.9729 | 0.92 | 1.05 | 1791 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201014 | 18S | Approved | P1 | 5 | 2LINE-625_OP | VL |  |  |  |  | 0.9195 | 0.9622 | 0.92 | 1.05 | 1803 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201015 | 18S | Approved | P1 | 5 | 2ST_MARTIN | VL |  |  |  |  | 0.9142 | 0.9571 | 0.92 | 1.05 | 1803 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201016 | 18S | Approved | P1 | 5 | LONGFL 2 | VL |  |  |  |  | 0.9142 | 0.9571 | 0.92 | 1.05 | 1803 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201017 | 18S | Approved | P1 | 5 | 2LINE-625_OP | VL |  |  |  |  | 0.9075 | 0.9622 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201017 | 18S | Approved | P1 | 5 | 2LINE-625_OP | VL |  |  |  |  | 0.9075 | 0.9622 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201018 | 18S | Approved | P1 | 5 | 2ST_MARTIN | VL |  |  |  |  | 0.9021 | 0.9571 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201018 | 18S | Approved | P1 | 5 | 2ST_MARTIN | VL |  |  |  |  | 0.9021 | 0.9571 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201019 | 18S | Approved | P1 | 5 | LONGFL 2 | VL |  |  |  |  | 0.9021 | 0.9571 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201019 | 18S | Approved | P1 | 5 | LONGFL 2 | VL |  |  |  |  | 0.9021 | 0.9571 | 0.92 | 1.05 | 1805 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201020 | 18S | Approved | P1 | 5 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9172 | 0.9643 | 0.92 | 1.05 | 1832 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201021 | 18S | Approved | P1 | 5 | 4BOBCAT | VL |  |  |  |  | 0.9136 | 0.9707 | 0.92 | 1.05 | 1832 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201022 | 18S | Approved | P1 | 5 | 4LINE-642_TP | VL |  |  |  |  | 0.9173 | 0.9644 | 0.92 | 1.05 | 1832 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201023 | 18S | Approved | P1 | 5 | 4COL_SPRINGS | VL |  |  |  |  | 0.9172 | 0.9643 | 0.92 | 1.05 | 1832 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201024 | 18S | Approved | P1 | 5 | 2NESSER_TP | VL |  |  |  |  | 0.8804 | 0.978 | 0.92 | 1.05 | 1968 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201025 | 18S | Approved | P1 | 5 | 2NESSER | VL |  |  |  |  | 0.8754 | 0.9735 | 0.92 | 1.05 | 1968 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201026 | 18S | Approved | P1 | 5 | 2LN-372A_TP | VL |  |  |  |  | 0.8959 | 0.9917 | 0.92 | 1.05 | 1968 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335710 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201027 | 18S | Approved | P1 | 5 | 2JONESCREEK! | VL |  |  |  |  | 0.8993 | 0.9882 | 0.92 | 1.05 | 1968 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201028 | 18S | Approved | P1 | 5 | 3ASHLAND | VH |  |  |  |  | 1.0612 | 1.0017 | 0.92 | 1.05 | 2085 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201029 | 18S | Approved | P1 | 5 | 3HOUMA! | VH |  |  |  |  | 1.0698 | 1.0062 | 0.92 | 1.05 | 2085 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201030 | 18S | Approved | P1 | 5 | 3CHAVIN! | VH |  |  |  |  | 1.0508 | 0.9994 | 0.92 | 1.05 | 2085 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201031 | 18S | Approved | P1 | 5 | HOUMA 3 | VH |  |  |  |  | 1.0698 | 1.0062 | 0.92 | 1.05 | 2085 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201032 | 18S | Approved | P2 | 5 | 3GMEADW! | VL |  |  |  |  | 0.9196 | 1.0067 | 0.92 | 1.05 | 2114 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  | None
201033 | 18S | Approved | P2 | 5 | 3LEEVLL | VL |  |  |  |  | 0.8853 | 0.9959 | 0.92 | 1.05 | 2114 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  | None
201034 | 18S | Approved | P2 | 5 | 3FOURCHN | VL |  |  |  |  | 0.8743 | 0.9861 | 0.92 | 1.05 | 2114 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  | None
201035 | 18S | Approved | P1 | 5 | 3CARLSL | VL |  |  |  |  | 0.8777 | 0.9832 | 0.92 | 1.05 | 2124 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
201036 | 18S | Approved | P1 | 5 | 3JNESBORO_LA | VL |  |  |  |  | 0.8677 | 1.0068 | 0.92 | 1.05 | 2275 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337346 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201037 | 18S | Approved | P1 | 5 | 3HODGE_LA! | VL |  |  |  |  | 0.8689 | 1.0058 | 0.92 | 1.05 | 2275 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201038 | 18S | Approved | P1 | 5 | 2TUPPER | VL |  |  |  |  | 0.9124 | 1.0111 | 0.92 | 1.05 | 2431 | 303014 4BAYOU_COVE% 138 335280 4JENNINGS! 138 1 | 335256 |  |  |  | 69 | 69 | 351 | EES |  |  | 303014 4BAYOU_COVE% 138 335280 4JENNINGS! 138 1 |  |  | Solution: Adjust caps
201039 | 18S | Approved | P1 | 5 | 2ELTON! | VL |  |  |  |  | 0.9136 | 1.0123 | 0.92 | 1.05 | 2431 | 303014 4BAYOU_COVE% 138 335280 4JENNINGS! 138 1 | 335257 |  |  |  | 69 | 69 | 351 | EES |  |  | 303014 4BAYOU_COVE% 138 335280 4JENNINGS! 138 1 |  |  | Solution: Adjust caps
201040 | 18S | Approved | P1 | 5 | 4LEBLANC! | VL |  |  |  |  | 0.9152 | 0.9679 | 0.92 | 1.05 | 2450 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201041 | 18S | Approved | P1 | 5 | 3MINDEN_LG | VL |  |  |  |  | 0.9078 | 0.9854 | 0.92 | 1.05 | 2471 | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 |  | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
201042 | 18S | Approved | P1 | 5 | 3TRUSSEL_CR | VL |  |  |  |  | 0.9199 | 0.9987 | 0.92 | 1.05 | 2474 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | 303310 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1
201043 | 18S | Approved | P1 | 5 | 3GILBERT | VL |  |  |  |  | 0.8991 | 1.0225 | 0.92 | 1.05 | 2488 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201044 | 18S | Approved | P1 | 5 | 3METROPOLIS | VL |  |  |  |  | 0.9128 | 1.0293 | 0.92 | 1.05 | 2488 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201045 | 18S | Approved | P1 | 5 | 3WISNER | VL |  |  |  |  | 0.9094 | 1.0298 | 0.92 | 1.05 | 2488 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201046 | 18S | Approved | P1 | 5 | 3WINNSBORO! | VL |  |  |  |  | 0.8839 | 1.0121 | 0.92 | 1.05 | 2488 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201047 | 18S | Approved | P1 | 5 | 3GILBERT | VH |  |  |  |  | 1.0949 | 1.0225 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | VH
201048 | 18S | Approved | P1 | 5 | 3BASKIN | VH |  |  |  |  | 1.0952 | 1.0032 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | VH
201049 | 18S | Approved | P1 | 5 | 3NATCHEZSES% | VH |  |  |  |  | 1.063 | 1.0273 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201050 | 18S | Approved | P1 | 5 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0624 | 1.027 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201051 | 18S | Approved | P1 | 5 | 3PINE RIDGE | VH |  |  |  |  | 1.0621 | 1.0266 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201052 | 18S | Approved | P1 | 5 | 3NATCHEZ! | VH |  |  |  |  | 1.0613 | 1.0267 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201053 | 18S | Approved | P1 | 5 | 3J.MANVILLE | VH |  |  |  |  | 1.0586 | 1.0244 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201054 | 18S | Approved | P1 | 5 | 3INTL PAPER | VH |  |  |  |  | 1.0578 | 1.0238 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201055 | 18S | Approved | P1 | 5 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0571 | 1.0233 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201056 | 18S | Approved | P1 | 5 | 3NATCHEZ IND | VH |  |  |  |  | 1.0556 | 1.0223 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201057 | 18S | Approved | P1 | 5 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0551 | 1.0231 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201058 | 18S | Approved | P1 | 5 | 3KINGSTON MS | VH |  |  |  |  | 1.0528 | 1.0207 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201059 | 18S | Approved | P1 | 5 | 3WASHINGTON+ | VH |  |  |  |  | 1.0562 | 1.0238 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201060 | 18S | Approved | P1 | 5 | 3FAYETTE | VH |  |  |  |  | 1.0502 | 1.0272 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201061 | 18S | Approved | P1 | 5 | 3VIDALIA_LA | VH |  |  |  |  | 1.0504 | 1.0182 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201062 | 18S | Approved | P1 | 5 | 3RED_GUM! | VH |  |  |  |  | 1.0615 | 1.0251 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201063 | 18S | Approved | P1 | 5 | 3METROPOLIS | VH |  |  |  |  | 1.0928 | 1.0293 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201064 | 18S | Approved | P1 | 5 | 3WISNER | VH |  |  |  |  | 1.0955 | 1.0298 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201065 | 18S | Approved | P1 | 5 | 3WINNSBORO! | VH |  |  |  |  | 1.0975 | 1.0121 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201066 | 18S | Approved | P1 | 5 | VIDALIA3 | VH |  |  |  |  | 1.0504 | 1.0182 | 0.92 | 1.05 | 2489 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Contingency: invalid, no breakers
201067 | 18S | Approved | P1 | 5 | 4CANEY | VL |  |  |  |  | 0.8727 | 0.995 | 0.92 | 1.05 | 2648 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201068 | 18S | Approved | P1 | 5 | OAKDALE4 | VL |  |  |  |  | 0.8747 | 0.9932 | 0.92 | 1.05 | 2648 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201069 | 18S | Approved | P1 | 5 | PNPRARIE 4 | VL |  |  |  |  | 0.8656 | 1.0072 | 0.92 | 1.05 | 2648 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201070 | 18S | Approved | P1 | 5 | WSTBAY 4 | VL |  |  |  |  | 0.8865 | 0.9918 | 0.92 | 1.05 | 2648 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201074 | 18S | Approved | P1 | 5 | ELKS 6 | VL |  |  |  |  | 0.9161 | 0.9827 | 0.92 | 1.05 | 2741 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  | turn on switch shunt at BEADLE 230kV sub
201075 | 18S | Approved | P1 | 5 | BEADLE 6 | VL |  |  |  |  | 0.9166 | 0.9844 | 0.92 | 1.05 | 2741 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1
201076 | 18S | Approved | P1 | 5 | ELKS 6 | VL |  |  |  |  | 0.9003 | 0.9827 | 0.92 | 1.05 | 2766 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
201077 | 18S | Approved | P1 | 5 | 8THALMANN | VH |  |  |  |  | 1.0514 | 1.04 | 0.92 | 1.05 | 2857 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201078 | 18S | Approved | P1 | 5 | 8MCCALL RD | VH |  |  |  |  | 1.0661 | 1.0334 | 0.92 | 1.05 | 2857 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201079 | 18S | Approved | P1 | 5 | 8DANIEL | VH |  |  |  |  | 1.0762 | 1.0432 | 0.92 | 1.05 | 3579 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
201080 | 18S | Approved | P2 | 5 | 5HIGHLAND | VL |  |  |  |  | 0.9077 | 0.9813 | 0.92 | 1.05 | 4363 | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 | 338220 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 |  | None
201081 | 18S | Approved | P1 | 5 | TENRUSK7 | VH |  |  |  |  | 1.0519 | 1.0182 | 0.92 | 1.05 | 4566 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201082 | 18S | Approved | P1 | 5 | TENGEN 7 | VH |  |  |  |  | 1.0519 | 1.0182 | 0.92 | 1.05 | 4566 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201083 | 18S | Approved | P1 | 5 | ELKCITY7 | VH |  |  |  |  | 1.0515 | 1.0271 | 0.92 | 1.05 | 4607 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
201084 | 18S | Approved | P0 | 6 | 5HORN LAKE% | VH |  |  |  |  | 1.057 | 1.057 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201085 | 18S | Approved | P0 | 6 | 7CLINTON | VH |  |  |  |  | 1.05 | 1.05 | 0.95 | 1.05 | 0 | ** Base Case ** | 348846 |  |  |  | 345 | 345 | 357 | AMIL |  |  | ** Base Case ** |  |  | VH
201086 | 18S | Approved | P0 | 6 | 8E POINT AL | VH |  |  |  |  | 1.0537 | 1.0537 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201087 | 18S | Approved | P0 | 6 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201088 | 18S | Approved | P0 | 6 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201089 | 18S | Approved | P1 | 6 | 2TUPPER | VL |  |  |  |  | 0.9113 | 1.0111 | 0.92 | 1.05 | 328 | P1_2-92 | 335256 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-92 |  |  | Solution: Adjust caps
201090 | 18S | Approved | P1 | 6 | 2ELTON! | VL |  |  |  |  | 0.9126 | 1.0123 | 0.92 | 1.05 | 328 | P1_2-92 | 335257 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-92 |  |  | Solution: Adjust caps
201091 | 18S | Approved | P1 | 6 | 4LEBLANC! | VL |  |  |  |  | 0.9154 | 0.9679 | 0.92 | 1.05 | 349 | P1_2-113 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201092 | 18S | Approved | P1 | 6 | 2CALVERT! | VH |  |  |  |  | 1.0559 | 0.9805 | 0.92 | 1.05 | 360 | P1_2-124 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201093 | 18S | Approved | P1 | 6 | 2SINHERN | VH |  |  |  |  | 1.0678 | 1.0002 | 0.92 | 1.05 | 360 | P1_2-124 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201094 | 18S | Approved | P1 | 6 | 2HEARNE! | VH |  |  |  |  | 1.0788 | 1.0191 | 0.92 | 1.05 | 360 | P1_2-124 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201095 | 18S | Approved | P1 | 6 | 2TXHEARN | VH |  |  |  |  | 1.0773 | 1.0196 | 0.92 | 1.05 | 360 | P1_2-124 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201096 | 18S | Approved | P1 | 6 | 2APLHERN | VH |  |  |  |  | 1.0732 | 1.0207 | 0.92 | 1.05 | 360 | P1_2-124 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201097 | 18S | Approved | P1 | 6 | 2CALVERT! | VL |  |  |  |  | 0.7882 | 0.9805 | 0.92 | 1.05 | 361 | P1_2-125 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201098 | 18S | Approved | P1 | 6 | 2SINHERN | VL |  |  |  |  | 0.829 | 1.0002 | 0.92 | 1.05 | 361 | P1_2-125 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201099 | 18S | Approved | P1 | 6 | 2HEARNE! | VL |  |  |  |  | 0.8662 | 1.0191 | 0.92 | 1.05 | 361 | P1_2-125 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201100 | 18S | Approved | P1 | 6 | 2TXHEARN | VL |  |  |  |  | 0.8661 | 1.0196 | 0.92 | 1.05 | 361 | P1_2-125 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201101 | 18S | Approved | P1 | 6 | 2APLHERN | VL |  |  |  |  | 0.8659 | 1.0207 | 0.92 | 1.05 | 361 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201102 | 18S | Approved | P1 | 6 | 2BRYAN A! | VL |  |  |  |  | 0.8661 | 1.0257 | 0.92 | 1.05 | 361 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201103 | 18S | Approved | P1 | 6 | 2HUMBHRN | VL |  |  |  |  | 0.8769 | 1.0199 | 0.92 | 1.05 | 361 | P1_2-125 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
201105 | 18S | Approved | P1 | 6 | 4MILLCR! | VL |  |  |  |  | 0.9043 | 0.9951 | 0.92 | 1.05 | 473 | P1_2-237 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201106 | 18S | Approved | P1 | 6 | 4PINELND | VL |  |  |  |  | 0.8975 | 0.9785 | 0.92 | 1.05 | 473 | P1_2-237 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201107 | 18S | Approved | P1 | 6 | 4BROADUS | VL |  |  |  |  | 0.8932 | 0.9749 | 0.92 | 1.05 | 473 | P1_2-237 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201108 | 18S | Approved | P1 | 6 | 4ETOIL | VL |  |  |  |  | 0.8916 | 0.9734 | 0.92 | 1.05 | 473 | P1_2-237 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201109 | 18S | Approved | P1 | 6 | 4HRTNHIL | VL |  |  |  |  | 0.8997 | 0.9858 | 0.92 | 1.05 | 473 | P1_2-237 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201110 | 18S | Approved | P1 | 6 | 2PINELND | VL |  |  |  |  | 0.9128 | 0.9871 | 0.92 | 1.05 | 473 | P1_2-237 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201111 | 18S | Approved | P1 | 6 | 2TEMPL1* | VL |  |  |  |  | 0.911 | 0.9855 | 0.92 | 1.05 | 473 | P1_2-237 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201112 | 18S | Approved | P1 | 6 | 2TEMPLE1 | VL |  |  |  |  | 0.9106 | 0.9852 | 0.92 | 1.05 | 473 | P1_2-237 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201113 | 18S | Approved | P1 | 6 | 2TEMPL2* | VL |  |  |  |  | 0.9107 | 0.9853 | 0.92 | 1.05 | 473 | P1_2-237 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201114 | 18S | Approved | P1 | 6 | 2TEMPLE2 | VL |  |  |  |  | 0.9105 | 0.9851 | 0.92 | 1.05 | 473 | P1_2-237 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201115 | 18S | Approved | P1 | 6 | 2TMPLSWC | VL |  |  |  |  | 0.9106 | 0.9852 | 0.92 | 1.05 | 473 | P1_2-237 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201116 | 18S | Approved | P1 | 6 | 2WEIRGAT | VL |  |  |  |  | 0.9002 | 0.9758 | 0.92 | 1.05 | 473 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201117 | 18S | Approved | P1 | 6 | 4PEACH! | VL |  |  |  |  | 0.9132 | 0.9937 | 0.92 | 1.05 | 473 | P1_2-237 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201118 | 18S | Approved | P1 | 6 | 2DEWEYVL! | VL |  |  |  |  | 0.918 | 0.9816 | 0.92 | 1.05 | 650 | P1_2-414 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201119 | 18S | Approved | P1 | 6 | 2SKBVREG | VL |  |  |  |  | 0.9196 | 0.9833 | 0.92 | 1.05 | 650 | P1_2-414 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201120 | 18S | Approved | P1 | 6 | 2LINE-625_OP | VL |  |  |  |  | 0.919 | 0.9622 | 0.92 | 1.05 | 815 | P1_2-579 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201121 | 18S | Approved | P1 | 6 | 2ST_MARTIN | VL |  |  |  |  | 0.9137 | 0.9571 | 0.92 | 1.05 | 815 | P1_2-579 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201122 | 18S | Approved | P1 | 6 | LONGFL 2 | VL |  |  |  |  | 0.9137 | 0.9571 | 0.92 | 1.05 | 815 | P1_2-579 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201123 | 18S | Approved | P1 | 6 | 3ASHLAND | VH |  |  |  |  | 1.0612 | 1.0017 | 0.92 | 1.05 | 1038 | P1_2-802 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201124 | 18S | Approved | P1 | 6 | 3HOUMA! | VH |  |  |  |  | 1.0698 | 1.0062 | 0.92 | 1.05 | 1038 | P1_2-802 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201125 | 18S | Approved | P1 | 6 | 3CHAVIN! | VH |  |  |  |  | 1.0508 | 0.9994 | 0.92 | 1.05 | 1038 | P1_2-802 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201126 | 18S | Approved | P1 | 6 | HOUMA 3 | VH |  |  |  |  | 1.0698 | 1.0062 | 0.92 | 1.05 | 1038 | P1_2-802 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201127 | 18S | Approved | P1 | 6 | 3GMEADW! | VL |  |  |  |  | 0.9196 | 1.0067 | 0.92 | 1.05 | 1043 | P1_2-807 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  | None
201128 | 18S | Approved | P1 | 6 | 3LEEVLL | VL |  |  |  |  | 0.8852 | 0.9959 | 0.92 | 1.05 | 1043 | P1_2-807 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  | None
201129 | 18S | Approved | P1 | 6 | 3FOURCHN | VL |  |  |  |  | 0.8743 | 0.9861 | 0.92 | 1.05 | 1043 | P1_2-807 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  | None
201130 | 18S | Approved | P1 | 6 | 8GGNS% | VL |  |  |  |  | 0.9816 | 1.0166 | 0.982 | 1.05 | 1269 | P1_2-1033 | 336820 |  |  |  | 500 | 500 | 326 | EES-EMI |  |  | P1_2-1033_8GGNS%,8BXTRWILSON% |  | None
201131 | 18S | Approved | P1 | 6 | 3GILBERT | VL |  |  |  |  | 0.8963 | 1.0225 | 0.92 | 1.05 | 1414 | P1_2-1178 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201132 | 18S | Approved | P1 | 6 | 3METROPOLIS | VL |  |  |  |  | 0.9101 | 1.0293 | 0.92 | 1.05 | 1414 | P1_2-1178 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201133 | 18S | Approved | P1 | 6 | 3WISNER | VL |  |  |  |  | 0.9067 | 1.0298 | 0.92 | 1.05 | 1414 | P1_2-1178 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201134 | 18S | Approved | P1 | 6 | 3WINNSBORO! | VL |  |  |  |  | 0.8811 | 1.0121 | 0.92 | 1.05 | 1414 | P1_2-1178 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201135 | 18S | Approved | P1 | 6 | 3 34TH&MAIN | VL |  |  |  |  | 0.9154 | 0.9497 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201136 | 18S | Approved | P1 | 6 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9056 | 0.948 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201137 | 18S | Approved | P1 | 6 | 3MCCAMANT! | VL |  |  |  |  | 0.9033 | 0.9533 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201138 | 18S | Approved | P1 | 6 | 3PB IP SS% | VL |  |  |  |  | 0.9026 | 0.9419 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201139 | 18S | Approved | P1 | 6 | 3PB IP! | VL |  |  |  |  | 0.902 | 0.9413 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201140 | 18S | Approved | P1 | 6 | 3PB PORT | VL |  |  |  |  | 0.9021 | 0.9415 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201141 | 18S | Approved | P1 | 6 | 3PB ENERGY! | VL |  |  |  |  | 0.9021 | 0.9414 | 0.92 | 1.05 | 1529 | P1_2-1293 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201142 | 18S | Approved | P1 | 6 | 3PINEBLUF.E% | VL |  |  |  |  | 0.92 | 0.948 | 0.92 | 1.05 | 1538 | P1_2-1302 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201143 | 18S | Approved | P1 | 6 | 3PB IP SS% | VL |  |  |  |  | 0.916 | 0.9419 | 0.92 | 1.05 | 1538 | P1_2-1302 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201144 | 18S | Approved | P1 | 6 | 3PB IP! | VL |  |  |  |  | 0.9154 | 0.9413 | 0.92 | 1.05 | 1538 | P1_2-1302 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201145 | 18S | Approved | P1 | 6 | 3PB PORT | VL |  |  |  |  | 0.9155 | 0.9415 | 0.92 | 1.05 | 1538 | P1_2-1302 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201146 | 18S | Approved | P1 | 6 | 3PB ENERGY! | VL |  |  |  |  | 0.9154 | 0.9414 | 0.92 | 1.05 | 1538 | P1_2-1302 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201147 | 18S | Approved | P1 | 6 | 3PB IP SS% | VL |  |  |  |  | 0.9142 | 0.9419 | 0.92 | 1.05 | 1539 | P1_2-1303 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201148 | 18S | Approved | P1 | 6 | 3PB IP! | VL |  |  |  |  | 0.9136 | 0.9413 | 0.92 | 1.05 | 1539 | P1_2-1303 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201149 | 18S | Approved | P1 | 6 | 3PB PORT | VL |  |  |  |  | 0.9137 | 0.9415 | 0.92 | 1.05 | 1539 | P1_2-1303 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201150 | 18S | Approved | P1 | 6 | 3PB ENERGY! | VL |  |  |  |  | 0.9137 | 0.9414 | 0.92 | 1.05 | 1539 | P1_2-1303 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201151 | 18S | Approved | P1 | 6 | 3PB IP SS% | VL |  |  |  |  | 0.9166 | 0.9419 | 0.92 | 1.05 | 1549 | P1_2-1313 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201152 | 18S | Approved | P1 | 6 | 3PB IP! | VL |  |  |  |  | 0.916 | 0.9413 | 0.92 | 1.05 | 1549 | P1_2-1313 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201153 | 18S | Approved | P1 | 6 | 3PB PORT | VL |  |  |  |  | 0.9161 | 0.9415 | 0.92 | 1.05 | 1549 | P1_2-1313 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201154 | 18S | Approved | P1 | 6 | 3PB ENERGY! | VL |  |  |  |  | 0.916 | 0.9414 | 0.92 | 1.05 | 1549 | P1_2-1313 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201155 | 18S | Approved | P1 | 6 | 3STUTGART.N+ | VL |  |  |  |  | 0.9109 | 0.9884 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201156 | 18S | Approved | P1 | 6 | 3STUTGART.N | VL |  |  |  |  | 0.9088 | 0.9865 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201157 | 18S | Approved | P1 | 6 | 3RICUSKEY! | VL |  |  |  |  | 0.9112 | 0.9934 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201158 | 18S | Approved | P1 | 6 | 3STUTGART IN | VL |  |  |  |  | 0.9105 | 0.9883 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201159 | 18S | Approved | P1 | 6 | 3ULM | VL |  |  |  |  | 0.9178 | 0.9875 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201160 | 18S | Approved | P1 | 6 | 3ALMYRA | VL |  |  |  |  | 0.9091 | 0.977 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201161 | 18S | Approved | P1 | 6 | 3DEWITT | VL |  |  |  |  | 0.9109 | 0.9678 | 0.92 | 1.05 | 1677 | P1_2-1441 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201162 | 18S | Approved | P1 | 6 | 3HUMPHREY# | VL |  |  |  |  | 0.9156 | 0.9791 | 0.92 | 1.05 | 1677 | P1_2-1441 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201163 | 18S | Approved | P1 | 6 | 3DELUCE# | VL |  |  |  |  | 0.9161 | 0.9648 | 0.92 | 1.05 | 1677 | P1_2-1441 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201164 | 18S | Approved | P1 | 6 | 3GILLETT! | VL |  |  |  |  | 0.9144 | 0.9663 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201165 | 18S | Approved | P1 | 6 | 3ELAINE | VL |  |  |  |  | 0.888 | 0.9668 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201166 | 18S | Approved | P1 | 6 | 3MARVELL | VL |  |  |  |  | 0.8799 | 0.9689 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201167 | 18S | Approved | P1 | 6 | 3BARTON | VL |  |  |  |  | 0.8772 | 0.9695 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201168 | 18S | Approved | P1 | 6 | 3HELENA.W+ | VL |  |  |  |  | 0.8727 | 0.9707 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201169 | 18S | Approved | P1 | 6 | 3HELENA.C | VL |  |  |  |  | 0.8709 | 0.9711 | 0.92 | 1.05 | 1684 | P1_2-1448 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201170 | 18S | Approved | P1 | 6 | 3DELUCE# | VL |  |  |  |  | 0.919 | 0.9648 | 0.92 | 1.05 | 1684 | P1_2-1448 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201171 | 18S | Approved | P1 | 6 | 3HELENA IN#! | VL |  |  |  |  | 0.8706 | 0.9734 | 0.92 | 1.05 | 1684 | P1_2-1448 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201172 | 18S | Approved | P1 | 6 | 8SANS SOUCI% | VH |  |  |  |  | 1.0539 | 1.0373 | 0.92 | 1.05 | 1752 | P1_2-1519 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1519 |  |  | VH
201173 | 18S | Approved | P1 | 6 | 8DANIEL | VH |  |  |  |  | 1.0762 | 1.0432 | 0.92 | 1.05 | 1837 | P1_2-1604 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! |  |  | VH
201174 | 18S | Approved | P1 | 6 | 4CANEY | VL |  |  |  |  | 0.8726 | 0.995 | 0.92 | 1.05 | 1886 | P1_2-1653 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201175 | 18S | Approved | P1 | 6 | OAKDALE4 | VL |  |  |  |  | 0.8745 | 0.9932 | 0.92 | 1.05 | 1886 | P1_2-1653 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201176 | 18S | Approved | P1 | 6 | PNPRARIE 4 | VL |  |  |  |  | 0.8654 | 1.0072 | 0.92 | 1.05 | 1886 | P1_2-1653 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201177 | 18S | Approved | P1 | 6 | WSTBAY 4 | VL |  |  |  |  | 0.8863 | 0.9918 | 0.92 | 1.05 | 1886 | P1_2-1653 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201178 | 18S | Approved | P1 | 6 | 4VEAZIE | VL |  |  |  |  | 0.889 | 0.9781 | 0.92 | 1.05 | 1887 | P1_2-1654 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201179 | 18S | Approved | P1 | 6 | GUIDRY 4 | VL |  |  |  |  | 0.8876 | 0.9769 | 0.92 | 1.05 | 1887 | P1_2-1654 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201180 | 18S | Approved | P1 | 6 | PLAISAN4 | VL |  |  |  |  | 0.9032 | 0.9908 | 0.92 | 1.05 | 1887 | P1_2-1654 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201181 | 18S | Approved | P1 | 6 | TENRUSK7 | VH |  |  |  |  | 1.0519 | 1.0182 | 0.92 | 1.05 | 2096 | P1_2-1863 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
201182 | 18S | Approved | P1 | 6 | TENGEN 7 | VH |  |  |  |  | 1.0519 | 1.0182 | 0.92 | 1.05 | 2096 | P1_2-1863 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
201183 | 18W | Approved | P0 | 7 | 5HORN LAKE% | VH |  |  |  |  | 1.0601 | 1.0601 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201184 | 18W | Approved | P0 | 7 | 8UNION MS | VH |  |  |  |  | 1.0502 | 1.0502 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201185 | 18W | Approved | P0 | 7 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201186 | 18W | Approved | P0 | 7 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201187 | 18W | Approved | P0 | 7 | 8PLEASANT HL | VH |  |  |  |  | 1.0508 | 1.0508 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201188 | 18W | Approved | P0 | 7 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201189 | 18W | Approved | P0 | 7 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201190 | 18W | Approved | P1 | 7 | 3BLACK_RIV | VH |  |  |  |  | 1.0785 | 0.9905 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201191 | 18W | Approved | P1 | 7 | 3GILBERT | VH |  |  |  |  | 1.1015 | 1.0076 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201192 | 18W | Approved | P1 | 7 | 3PERSIM_MIL | VH |  |  |  |  | 1.1028 | 1.0169 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201193 | 18W | Approved | P1 | 7 | 3BASKIN | VH |  |  |  |  | 1.0681 | 0.9995 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201194 | 18W | Approved | P1 | 7 | 3NATCHEZSES% | VH |  |  |  |  | 1.1299 | 1.0283 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201195 | 18W | Approved | P1 | 7 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1292 | 1.0286 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201196 | 18W | Approved | P1 | 7 | 3PINE RIDGE | VH |  |  |  |  | 1.1291 | 1.0285 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201197 | 18W | Approved | P1 | 7 | 3NATCHEZ! | VH |  |  |  |  | 1.1272 | 1.0295 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201198 | 18W | Approved | P1 | 7 | 3J.MANVILLE | VH |  |  |  |  | 1.1243 | 1.0278 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201199 | 18W | Approved | P1 | 7 | 3INTL PAPER | VH |  |  |  |  | 1.1223 | 1.0273 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201200 | 18W | Approved | P1 | 7 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1209 | 1.0268 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201201 | 18W | Approved | P1 | 7 | 3NATCHEZ IND | VH |  |  |  |  | 1.1176 | 1.026 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201202 | 18W | Approved | P1 | 7 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1206 | 1.0295 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201203 | 18W | Approved | P1 | 7 | 3CROSBY+ | VH |  |  |  |  | 1.1011 | 1.0344 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201204 | 18W | Approved | P1 | 7 | 3GLOSTER | VH |  |  |  |  | 1.0955 | 1.0363 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201205 | 18W | Approved | P1 | 7 | 3LIBERTY P/L | VH |  |  |  |  | 1.0708 | 1.036 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201206 | 18W | Approved | P1 | 7 | 3WOODVILLE | VH |  |  |  |  | 1.0691 | 1.008 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201207 | 18W | Approved | P1 | 7 | 3LIBERTY! | VH |  |  |  |  | 1.0709 | 1.036 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201208 | 18W | Approved | P1 | 7 | 3INTRSTE P/L | VH |  |  |  |  | 1.0709 | 1.036 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201209 | 18W | Approved | P1 | 7 | 3GILLSBURG+ | VH |  |  |  |  | 1.0504 | 1.0211 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336517 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201210 | 18W | Approved | P1 | 7 | 3KINGSTON MS | VH |  |  |  |  | 1.1195 | 1.0283 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201211 | 18W | Approved | P1 | 7 | 3CENTREVILLE | VH |  |  |  |  | 1.0763 | 1.0157 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201212 | 18W | Approved | P1 | 7 | 3SMITHDALE+ | VH |  |  |  |  | 1.0535 | 1.0322 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336525 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201213 | 18W | Approved | P1 | 7 | 3WASHINGTON+ | VH |  |  |  |  | 1.1205 | 1.0273 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201214 | 18W | Approved | P1 | 7 | 3ROXIE | VH |  |  |  |  | 1.0908 | 1.0263 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201215 | 18W | Approved | P1 | 7 | 3MEADVILLE | VH |  |  |  |  | 1.0694 | 1.0274 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201216 | 18W | Approved | P1 | 7 | 3CRANFIELD+ | VH |  |  |  |  | 1.11 | 1.0266 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201217 | 18W | Approved | P1 | 7 | 3FAYETTE | VH |  |  |  |  | 1.1952 | 1.0265 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201218 | 18W | Approved | P1 | 7 | 3LORMAN+ | VH |  |  |  |  | 1.2235 | 1.0277 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201219 | 18W | Approved | P1 | 7 | 3LORMAN | VH |  |  |  |  | 1.2234 | 1.0276 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201220 | 18W | Approved | P1 | 7 | 3PORTGIBSON! | VH |  |  |  |  | 1.2486 | 1.031 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201221 | 18W | Approved | P1 | 7 | 3GGNS | VH |  |  |  |  | 1.2478 | 1.0299 | 0.975 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201222 | 18W | Approved | P1 | 7 | 3S.VICKSBURG | VH |  |  |  |  | 1.2812 | 1.0267 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201223 | 18W | Approved | P1 | 7 | 3BLACK_RIVER | VH |  |  |  |  | 1.0785 | 0.9905 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201224 | 18W | Approved | P1 | 7 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1023 | 1.0166 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201225 | 18W | Approved | P1 | 7 | 3PLANTATION! | VH |  |  |  |  | 1.1041 | 1.0216 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201226 | 18W | Approved | P1 | 7 | 3VIDALIA_LA | VH |  |  |  |  | 1.1081 | 1.0221 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201227 | 18W | Approved | P1 | 7 | 3RED_GUM! | VH |  |  |  |  | 1.1137 | 1.0254 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201228 | 18W | Approved | P1 | 7 | 3METROPOLIS | VH |  |  |  |  | 1.1115 | 1.0108 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201229 | 18W | Approved | P1 | 7 | 3WISNER | VH |  |  |  |  | 1.1115 | 1.0099 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201230 | 18W | Approved | P1 | 7 | 3WINNSBORO! | VH |  |  |  |  | 1.0843 | 1.0051 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201231 | 18W | Approved | P1 | 7 | JNESVIL3 | VH |  |  |  |  | 1.0785 | 0.9905 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201232 | 18W | Approved | P1 | 7 | VIDALIA3 | VH |  |  |  |  | 1.1081 | 1.0221 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201233 | 18W | Approved | P1 | 7 | 3NITTA YUMA+ | VL |  |  |  |  | 0.9169 | 1.0048 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336970 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201234 | 18W | Approved | P1 | 7 | 3MURPHY+ | VL |  |  |  |  | 0.9045 | 1.0058 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336992 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201235 | 18W | Approved | P1 | 7 | 3GREENVILLE+ | VL |  |  |  |  | 0.8931 | 1.0176 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201236 | 18W | Approved | P1 | 7 | 3HOLLANDALE | VL |  |  |  |  | 0.9052 | 1.0064 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337048 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201237 | 18W | Approved | P1 | 7 | 3ARCOLA+ | VL |  |  |  |  | 0.8985 | 1.0116 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201238 | 18W | Approved | P1 | 7 | 3SWIFTWATER | VL |  |  |  |  | 0.8927 | 1.0172 | 0.92 | 1.05 | 265 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201239 | 18W | Approved | P1 | 7 | 3JNCTN CITY! | VH |  |  |  |  | 1.067 | 1.0327 | 0.92 | 1.05 | 456 | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 |  |  | VH
201240 | 18W | Approved | P1 | 7 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0296 | 0.92 | 1.05 | 865 | 338153 5SWIFTON 161 338705 5HOXIE.S# 161 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338153 5SWIFTON 161 338705 5HOXIE.S# 161 1 |  |  | VH
201241 | 18W | Approved | P1 | 7 | 8SANS SOUCI% | VH |  |  |  |  | 1.0617 | 1.0489 | 0.92 | 1.05 | 888 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
201242 | 18W | Approved | P1 | 7 | 2HEARNE! | VH |  |  |  |  | 1.0507 | 1.0144 | 0.92 | 1.05 | 1091 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201243 | 18W | Approved | P1 | 7 | 2TXHEARN | VH |  |  |  |  | 1.0529 | 1.0148 | 0.92 | 1.05 | 1091 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201244 | 18W | Approved | P1 | 7 | 2APLHERN | VH |  |  |  |  | 1.0587 | 1.0161 | 0.92 | 1.05 | 1091 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201245 | 18W | Approved | P1 | 7 | 2BRYAN A! | VH |  |  |  |  | 1.1015 | 1.0216 | 0.92 | 1.05 | 1091 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201246 | 18W | Approved | P1 | 7 | 4STOWELL! | VH |  |  |  |  | 1.0519 | 1.0243 | 0.92 | 1.05 | 1252 | 334219 4SHILOH! 138 334220 4BRKSCRK 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334219 4SHILOH! 138 334220 4BRKSCRK 138 1 |  |  | VH
201247 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0655 | 1.037 | 0.92 | 1.05 | 1252 | 334219 4SHILOH! 138 334220 4BRKSCRK 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334219 4SHILOH! 138 334220 4BRKSCRK 138 1 |  |  | VH
201248 | 18W | Approved | P1 | 7 | 4STOWELL! | VH |  |  |  |  | 1.0517 | 1.0243 | 0.92 | 1.05 | 1253 | 334220 4BRKSCRK 138 334221 4BAYSHOR 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334220 4BRKSCRK 138 334221 4BAYSHOR 138 1 |  |  | VH
201249 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0654 | 1.037 | 0.92 | 1.05 | 1253 | 334220 4BRKSCRK 138 334221 4BAYSHOR 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334220 4BRKSCRK 138 334221 4BAYSHOR 138 1 |  |  | VH
201250 | 18W | Approved | P1 | 7 | 4HANKAMR | VH |  |  |  |  | 1.0563 | 1.0082 | 0.92 | 1.05 | 1254 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334222 |  |  |  | 138 | 138 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
201251 | 18W | Approved | P1 | 7 | 4CROKBYU | VH |  |  |  |  | 1.0567 | 1.014 | 0.92 | 1.05 | 1254 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334223 |  |  |  | 138 | 138 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
201252 | 18W | Approved | P1 | 7 | 4TEPPCO | VH |  |  |  |  | 1.0566 | 1.0139 | 0.92 | 1.05 | 1254 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334224 |  |  |  | 138 | 138 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
201253 | 18W | Approved | P1 | 7 | 4STOWELL! | VH |  |  |  |  | 1.0578 | 1.0243 | 0.92 | 1.05 | 1254 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
201254 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0715 | 1.037 | 0.92 | 1.05 | 1254 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
201255 | 18W | Approved | P1 | 7 | 4STOWELL! | VH |  |  |  |  | 1.0514 | 1.0243 | 0.92 | 1.05 | 1258 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  |  | VH
201256 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0514 | 1.037 | 0.92 | 1.05 | 1258 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  |  | VH
201257 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0596 | 1.037 | 0.92 | 1.05 | 1259 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 |  |  | VH
201258 | 18W | Approved | P1 | 7 | 4STOWELL! | VH |  |  |  |  | 1.0513 | 1.0243 | 0.92 | 1.05 | 1261 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  |  | VH
201259 | 18W | Approved | P1 | 7 | 4BIGHILL! | VH |  |  |  |  | 1.0509 | 1.0131 | 0.92 | 1.05 | 1261 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334227 |  |  |  | 138 | 138 | 351 | EES |  |  | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  |  | VH
201260 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.051 | 1.037 | 0.92 | 1.05 | 1261 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  |  | VH
201261 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0619 | 1.037 | 0.92 | 1.05 | 1267 | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 |  |  | VH
201262 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1279 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 |  |  | VH
201263 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.055 | 1.037 | 0.92 | 1.05 | 1280 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 |  |  | VH
201264 | 18W | Approved | P1 | 7 | 2HIMEX | VH |  |  |  |  | 1.0545 | 1.037 | 0.92 | 1.05 | 1282 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 |  |  | VH
201265 | 18W | Approved | P1 | 7 | 4MILLCR! | VL |  |  |  |  | 0.9156 | 1.0012 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201266 | 18W | Approved | P1 | 7 | 4PINELND | VL |  |  |  |  | 0.914 | 0.9891 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201267 | 18W | Approved | P1 | 7 | 4BROADUS | VL |  |  |  |  | 0.9112 | 0.9868 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201268 | 18W | Approved | P1 | 7 | 4ETOIL | VL |  |  |  |  | 0.91 | 0.9858 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201269 | 18W | Approved | P1 | 7 | 4HRTNHIL | VL |  |  |  |  | 0.9139 | 0.9945 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201270 | 18W | Approved | P1 | 7 | 2WEIRGAT | VL |  |  |  |  | 0.9133 | 0.983 | 0.92 | 1.05 | 1290 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201271 | 18W | Approved | P1 | 7 | 2SABRA | VL |  |  |  |  | 0.8953 | 0.9937 | 0.92 | 1.05 | 1549 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334704 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201272 | 18W | Approved | P1 | 7 | 2DEWEYVL! | VL |  |  |  |  | 0.896 | 0.9827 | 0.92 | 1.05 | 1549 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201273 | 18W | Approved | P1 | 7 | 2SKBVREG | VL |  |  |  |  | 0.8975 | 0.9844 | 0.92 | 1.05 | 1549 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201274 | 18W | Approved | P1 | 7 | 2DEWEYVL! | VL |  |  |  |  | 0.9019 | 0.9827 | 0.92 | 1.05 | 1551 | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201275 | 18W | Approved | P1 | 7 | 2SKBVREG | VL |  |  |  |  | 0.9035 | 0.9844 | 0.92 | 1.05 | 1551 | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | 334704 2SABRA 69.0 334705 2DEWEYVL! 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201276 | 18W | Approved | P1 | 7 | 2SERPENT | VL |  |  |  |  | 0.9183 | 0.933 | 0.92 | 1.05 | 1636 | 335070 6CARLYSS% 230 335073 6BOUDOIN% 230 1 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | 335070 6CARLYSS% 230 335073 6BOUDOIN% 230 1 |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
201277 | 18W | Approved | P1 | 7 | 2NESSER_TP | VL |  |  |  |  | 0.9157 | 0.9812 | 0.92 | 1.05 | 1967 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201278 | 18W | Approved | P1 | 7 | 2NESSER | VL |  |  |  |  | 0.9118 | 0.9776 | 0.92 | 1.05 | 1967 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201279 | 18W | Approved | P1 | 7 | 3ASHLAND | VH |  |  |  |  | 1.0927 | 1.0073 | 0.92 | 1.05 | 2084 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201280 | 18W | Approved | P1 | 7 | 3HOUMA! | VH |  |  |  |  | 1.1028 | 1.0113 | 0.92 | 1.05 | 2084 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201281 | 18W | Approved | P1 | 7 | 3CHAVIN! | VH |  |  |  |  | 1.0761 | 1.0048 | 0.92 | 1.05 | 2084 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201282 | 18W | Approved | P1 | 7 | HOUMA 3 | VH |  |  |  |  | 1.1028 | 1.0113 | 0.92 | 1.05 | 2084 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201283 | 18W | Approved | P1 | 7 | 3GMEADW! | VH |  |  |  |  | 1.1753 | 1.0145 | 0.92 | 1.05 | 2113 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201284 | 18W | Approved | P1 | 7 | 3LEEVLL | VH |  |  |  |  | 1.1984 | 1.0053 | 0.92 | 1.05 | 2113 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201285 | 18W | Approved | P1 | 7 | 3FOURCHN | VH |  |  |  |  | 1.1982 | 0.9956 | 0.92 | 1.05 | 2113 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201286 | 18W | Approved | P1 | 7 | 3CARLSL | VL |  |  |  |  | 0.8819 | 0.9866 | 0.92 | 1.05 | 2123 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
201287 | 18W | Approved | P1 | 7 | 3GILBERT | VL |  |  |  |  | 0.9128 | 1.0076 | 0.92 | 1.05 | 2263 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  | None
201288 | 18W | Approved | P1 | 7 | 3METROPOLIS | VL |  |  |  |  | 0.9113 | 1.0108 | 0.92 | 1.05 | 2263 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201289 | 18W | Approved | P1 | 7 | 3WISNER | VL |  |  |  |  | 0.9114 | 1.0099 | 0.92 | 1.05 | 2263 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201290 | 18W | Approved | P1 | 7 | 3WINNSBORO! | VL |  |  |  |  | 0.9175 | 1.0051 | 0.92 | 1.05 | 2263 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201291 | 18W | Approved | P1 | 7 | 3WISNER | VL |  |  |  |  | 0.9196 | 1.0099 | 0.92 | 1.05 | 2265 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
201292 | 18W | Approved | P1 | 7 | 3JNESBORO_LA | VL |  |  |  |  | 0.9111 | 1.0133 | 0.92 | 1.05 | 2274 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337346 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201293 | 18W | Approved | P1 | 7 | 3HODGE_LA! | VL |  |  |  |  | 0.912 | 1.0128 | 0.92 | 1.05 | 2274 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201294 | 18W | Approved | P1 | 7 | 3LUCKY | VH |  |  |  |  | 1.0569 | 1.0248 | 0.92 | 1.05 | 2277 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 |  |  | VH
201295 | 18W | Approved | P1 | 7 | 2SERPENT | VL |  |  |  |  | 0.9182 | 0.933 | 0.92 | 1.05 | 2424 | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
201296 | 18W | Approved | P1 | 7 | 3GILBERT | VH |  |  |  |  | 1.1217 | 1.0076 | 0.92 | 1.05 | 2475 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201297 | 18W | Approved | P2 | 7 | 3RED_GUM! | VH |  |  |  |  | 1.0535 | 1.0254 | 0.92 | 1.05 | 2475 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201298 | 18W | Approved | P2 | 7 | 3METROPOLIS | VH |  |  |  |  | 1.1133 | 1.0108 | 0.92 | 1.05 | 2475 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201299 | 18W | Approved | P2 | 7 | 3WISNER | VH |  |  |  |  | 1.1177 | 1.0099 | 0.92 | 1.05 | 2475 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201300 | 18W | Approved | P2 | 7 | 3WINNSBORO! | VH |  |  |  |  | 1.1313 | 1.0051 | 0.92 | 1.05 | 2475 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201301 | 18W | Approved | P1 | 7 | CLARN 2 | VH |  |  |  |  | 1.07 | 1.0323 | 0.92 | 1.05 | 2619 | 500165 CLARN 2 69.0 500565 MAURICE2 69.0 1 | 500165 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 500165 CLARN 2 69.0 500565 MAURICE2 69.0 1 |  |  | VH
201302 | 18W | Approved | P1 | 7 | 4CANEY | VL |  |  |  |  | 0.8884 | 1 | 0.92 | 1.05 | 2635 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201303 | 18W | Approved | P1 | 7 | OAKDALE4 | VL |  |  |  |  | 0.8903 | 0.9986 | 0.92 | 1.05 | 2635 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201304 | 18W | Approved | P1 | 7 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 2635 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201305 | 18W | Approved | P1 | 7 | WSTBAY 4 | VL |  |  |  |  | 0.9 | 0.997 | 0.92 | 1.05 | 2635 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201306 | 18W | Approved | P1 | 7 | NATCH 2 | VH |  |  |  |  | 1.0741 | 1.0395 | 0.92 | 1.05 | 2672 | 500590 NATCH 4 138 500600 NATCH 2 69.0 1 | 500600 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 500590 NATCH 4 138 500600 NATCH 2 69.0 1 |  |  | VH
201307 | 18W | Approved | P1 | 7 | PRICE 4 | VH |  |  |  |  | 1.0527 | 1.0419 | 0.92 | 1.05 | 2674 | 500590 NATCH 4 138 500730 PRICE 4 138 1 | 500730 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500590 NATCH 4 138 500730 PRICE 4 138 1 |  |  | VH
201308 | 18W | Approved | P1 | 7 | 8THALMANN | VH |  |  |  |  | 1.0551 | 1.0425 | 0.92 | 1.05 | 2838 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201309 | 18W | Approved | P1 | 7 | 8MCCALL RD | VH |  |  |  |  | 1.0698 | 1.0325 | 0.92 | 1.05 | 2838 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201310 | 18W | Approved | P1 | 7 | 8THOMSON | VH |  |  |  |  | 1.0557 | 1.0384 | 0.92 | 1.05 | 3265 | 381413 6THOMSON 230 381490 8THOMSON 500 1 | 381490 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 381413 6THOMSON 230 381490 8THOMSON 500 1 |  |  | VH
201311 | 18W | Approved | P1 | 7 | 8DANIEL | VH |  |  |  |  | 1.0757 | 1.042 | 0.92 | 1.05 | 3561 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
201312 | 18W | Approved | P1 | 7 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 3910 | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 |  |  | VH
201313 | 18W | Approved | P1 | 7 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 4480 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201314 | 18W | Approved | P1 | 7 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 4480 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201315 | 18W | Approved | P1 | 7 | ELKCITY7 | VH |  |  |  |  | 1.0535 | 1.0294 | 0.92 | 1.05 | 4521 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
201316 | 18W | Approved | P0 | 8 | 5HORN LAKE% | VH |  |  |  |  | 1.0601 | 1.0601 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201317 | 18W | Approved | P0 | 8 | 8UNION MS | VH |  |  |  |  | 1.0502 | 1.0502 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201318 | 18W | Approved | P0 | 8 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201319 | 18W | Approved | P0 | 8 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201320 | 18W | Approved | P0 | 8 | 8PLEASANT HL | VH |  |  |  |  | 1.0508 | 1.0508 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201321 | 18W | Approved | P0 | 8 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201322 | 18W | Approved | P0 | 8 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201324 | 18W | Approved | P1 | 8 | 2HEARNE! | VH |  |  |  |  | 1.0507 | 1.0144 | 0.92 | 1.05 | 344 | P1_2-125 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
201325 | 18W | Approved | P1 | 8 | 2TXHEARN | VH |  |  |  |  | 1.0529 | 1.0148 | 0.92 | 1.05 | 344 | P1_2-125 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
201326 | 18W | Approved | P1 | 8 | 2APLHERN | VH |  |  |  |  | 1.0587 | 1.0161 | 0.92 | 1.05 | 344 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
201327 | 18W | Approved | P1 | 8 | 2BRYAN A! | VH |  |  |  |  | 1.1015 | 1.0216 | 0.92 | 1.05 | 344 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
201328 | 18W | Approved | P1 | 8 | 4STOWELL! | VH |  |  |  |  | 1.0514 | 1.0243 | 0.92 | 1.05 | 439 | P1_2-220 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! |  |  | VH
201329 | 18W | Approved | P1 | 8 | 2HIMEX | VH |  |  |  |  | 1.0514 | 1.037 | 0.92 | 1.05 | 439 | P1_2-220 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! |  |  | VH
201330 | 18W | Approved | P1 | 8 | 2HIMEX | VH |  |  |  |  | 1.0596 | 1.037 | 0.92 | 1.05 | 440 | P1_2-221 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! |  |  | VH
201331 | 18W | Approved | P1 | 8 | 4STOWELL! | VH |  |  |  |  | 1.0512 | 1.0243 | 0.92 | 1.05 | 442 | P1_2-223 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
201332 | 18W | Approved | P1 | 8 | 4BIGHILL! | VH |  |  |  |  | 1.0508 | 1.0131 | 0.92 | 1.05 | 442 | P1_2-223 | 334227 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
201333 | 18W | Approved | P1 | 8 | 2HIMEX | VH |  |  |  |  | 1.051 | 1.037 | 0.92 | 1.05 | 442 | P1_2-223 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
201334 | 18W | Approved | P1 | 8 | 2HIMEX | VH |  |  |  |  | 1.0619 | 1.037 | 0.92 | 1.05 | 448 | P1_2-229 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! |  |  | VH
201335 | 18W | Approved | P1 | 8 | 2HIMEX | VH |  |  |  |  | 1.057 | 1.037 | 0.92 | 1.05 | 452 | P1_2-233 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  |  | VH
201336 | 18W | Approved | P1 | 8 | 4MILLCR! | VL |  |  |  |  | 0.9156 | 1.0012 | 0.92 | 1.05 | 456 | P1_2-237 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201337 | 18W | Approved | P1 | 8 | 4PINELND | VL |  |  |  |  | 0.914 | 0.9891 | 0.92 | 1.05 | 456 | P1_2-237 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201338 | 18W | Approved | P1 | 8 | 4BROADUS | VL |  |  |  |  | 0.9112 | 0.9868 | 0.92 | 1.05 | 456 | P1_2-237 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201339 | 18W | Approved | P1 | 8 | 4ETOIL | VL |  |  |  |  | 0.91 | 0.9858 | 0.92 | 1.05 | 456 | P1_2-237 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201340 | 18W | Approved | P1 | 8 | 4HRTNHIL | VL |  |  |  |  | 0.9139 | 0.9945 | 0.92 | 1.05 | 456 | P1_2-237 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201341 | 18W | Approved | P1 | 8 | 2WEIRGAT | VL |  |  |  |  | 0.9133 | 0.983 | 0.92 | 1.05 | 456 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201342 | 18W | Approved | P1 | 8 | 2DEWEYVL! | VL |  |  |  |  | 0.9019 | 0.9827 | 0.92 | 1.05 | 633 | P1_2-414 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201343 | 18W | Approved | P1 | 8 | 2SKBVREG | VL |  |  |  |  | 0.9035 | 0.9844 | 0.92 | 1.05 | 633 | P1_2-414 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201344 | 18W | Approved | P1 | 8 | 2SERPENT | VL |  |  |  |  | 0.9183 | 0.933 | 0.92 | 1.05 | 676 | P1_2-457 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-457_6CARLYSS%,6BOUDOIN% |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
201345 | 18W | Approved | P1 | 8 | 3ASHLAND | VH |  |  |  |  | 1.0927 | 1.0073 | 0.92 | 1.05 | 1022 | P1_2-803 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
201346 | 18W | Approved | P1 | 8 | 3HOUMA! | VH |  |  |  |  | 1.1028 | 1.0113 | 0.92 | 1.05 | 1022 | P1_2-803 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
201347 | 18W | Approved | P1 | 8 | 3CHAVIN! | VH |  |  |  |  | 1.0761 | 1.0048 | 0.92 | 1.05 | 1022 | P1_2-803 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
201348 | 18W | Approved | P1 | 8 | HOUMA 3 | VH |  |  |  |  | 1.1028 | 1.0113 | 0.92 | 1.05 | 1022 | P1_2-803 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
201349 | 18W | Approved | P1 | 8 | 3GMEADW! | VH |  |  |  |  | 1.1753 | 1.0145 | 0.92 | 1.05 | 1027 | P1_2-808 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
201350 | 18W | Approved | P1 | 8 | 3LEEVLL | VH |  |  |  |  | 1.1984 | 1.0053 | 0.92 | 1.05 | 1027 | P1_2-808 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
201351 | 18W | Approved | P1 | 8 | 3FOURCHN | VH |  |  |  |  | 1.1981 | 0.9956 | 0.92 | 1.05 | 1027 | P1_2-808 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
201352 | 18W | Approved | P1 | 8 | 3GILBERT | VH |  |  |  |  | 1.1219 | 1.0076 | 0.92 | 1.05 | 1400 | P1_2-1181 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
201353 | 18W | Approved | P1 | 8 | 3RED_GUM! | VH |  |  |  |  | 1.0536 | 1.0254 | 0.92 | 1.05 | 1400 | P1_2-1181 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
201354 | 18W | Approved | P1 | 8 | 3METROPOLIS | VH |  |  |  |  | 1.1135 | 1.0108 | 0.92 | 1.05 | 1400 | P1_2-1181 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
201355 | 18W | Approved | P1 | 8 | 3WISNER | VH |  |  |  |  | 1.1179 | 1.0099 | 0.92 | 1.05 | 1400 | P1_2-1181 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
201356 | 18W | Approved | P1 | 8 | 3WINNSBORO! | VH |  |  |  |  | 1.1315 | 1.0051 | 0.92 | 1.05 | 1400 | P1_2-1181 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
201357 | 18W | Approved | P1 | 8 | 3JNCTN CITY! | VH |  |  |  |  | 1.0674 | 1.0327 | 0.92 | 1.05 | 1499 | P1_2-1280 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1280 |  |  | VH
201358 | 18W | Approved | P1 | 8 | 8SANS SOUCI% | VH |  |  |  |  | 1.0617 | 1.0489 | 0.92 | 1.05 | 1738 | P1_2-1522 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | VH
201359 | 18W | Approved | P1 | 8 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 1801 | P1_2-1585 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! |  |  | VH
201360 | 18W | Approved | P1 | 8 | 8DANIEL | VH |  |  |  |  | 1.0757 | 1.042 | 0.92 | 1.05 | 1823 | P1_2-1607 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! |  |  | VH
201361 | 18W | Approved | P1 | 8 | CLARN 2 | VH |  |  |  |  | 1.07 | 1.0323 | 0.92 | 1.05 | 1853 | P1_2-1637 | 500165 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1637 |  |  | VH
201362 | 18W | Approved | P1 | 8 | 4CANEY | VL |  |  |  |  | 0.8884 | 1 | 0.92 | 1.05 | 1872 | P1_2-1656 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
201363 | 18W | Approved | P1 | 8 | OAKDALE4 | VL |  |  |  |  | 0.8903 | 0.9986 | 0.92 | 1.05 | 1872 | P1_2-1656 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
201364 | 18W | Approved | P1 | 8 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 1872 | P1_2-1656 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
201365 | 18W | Approved | P1 | 8 | WSTBAY 4 | VL |  |  |  |  | 0.9 | 0.997 | 0.92 | 1.05 | 1872 | P1_2-1656 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
201366 | 18W | Approved | P1 | 8 | NATCH 2 | VH |  |  |  |  | 1.0741 | 1.0395 | 0.92 | 1.05 | 1910 | P1_2-1694 | 500600 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1694 |  |  | VH
201367 | 18W | Approved | P1 | 8 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 2082 | P1_2-1866 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
201368 | 18W | Approved | P1 | 8 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 2082 | P1_2-1866 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
201369 | 23S | Approved | P0 | 9 | 5HORN LAKE% | VH |  |  |  |  | 1.0564 | 1.0564 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201370 | 23S | Approved | P0 | 9 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201371 | 23S | Approved | P0 | 9 | 8CENTRLAL | VH |  |  |  |  | 1.05 | 1.05 | 0.92 | 1.05 | 0 | ** Base Case ** | 385337 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201372 | 23S | Approved | P1 | 9 | 3WOODVILLE | VL |  |  |  |  | 0.9086 | 0.9685 | 0.92 | 1.05 | 16 | 336512 3GLOSTER 115 336515 3LIBERTY! 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336512 3GLOSTER 115 336515 3LIBERTY! 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201373 | 23S | Approved | P2 | 9 | 3WOODVILLE | VL |  |  |  |  | 0.919 | 0.9685 | 0.92 | 1.05 | 25 | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336526 3ARLINGTON+ 115 336559 3FRANKLIN! 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
201375 | 23S | Approved | P1 | 9 | 6CHARITY CH | VL |  |  |  |  | 0.9113 | 0.9955 | 0.92 | 1.05 | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336860 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
201376 | 23S | Approved | P1 | 9 | 6HOY RD | VL |  |  |  |  | 0.9121 | 0.9925 | 0.92 | 1.05 | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336861 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
201377 | 23S | Approved | P1 | 9 | 6YANDELL RD! | VL |  |  |  |  | 0.9135 | 0.9891 | 0.92 | 1.05 | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336862 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
201378 | 23S | Approved | P1 | 9 | 6BOZEMAN RD | VL |  |  |  |  | 0.9124 | 0.9881 | 0.92 | 1.05 | 135 | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 | 336863 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 336848 6LAKEOVER% 230 336860 6CHARITY CH 230 1 |  | Project Proposed |  | 14-EMI-002-CP | 2017-06-01 | Construct line Bozeman Road 230 kV to new Tinnin Rd 230 kV switching station on R Braswell-G Andrus
201379 | 23S | Approved | P2 | 9 | 3SE.GREENVL | VL |  |  |  |  | 0.9002 | 1.0145 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337045 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201380 | 23S | Approved | P2 | 9 | 3GREENVILLE+ | VL |  |  |  |  | 0.9023 | 1.0127 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201381 | 23S | Approved | P2 | 9 | 3ARCOLA+ | VL |  |  |  |  | 0.9158 | 1.0128 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201382 | 23S | Approved | P2 | 9 | 3SWIFTWATER | VL |  |  |  |  | 0.9015 | 1.012 | 0.92 | 1.05 | 261 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed |  | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
201383 | 23S | Approved | P2 | 9 | 3GLENDALE# | VL |  |  |  |  | 0.9191 | 0.9642 | 0.92 | 1.05 | 482 | 337579 3MONTCELO.E! 115 338662 3MONTONGO# 115 1 | 338657 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337579 3MONTCELO.E! 115 338662 3MONTONGO# 115 1 |  | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201384 | 23S | Approved | P2 | 9 | 3MONTONGO# | VL |  |  |  |  | 0.9184 | 0.9787 | 0.92 | 1.05 | 482 | 337579 3MONTCELO.E! 115 338662 3MONTONGO# 115 1 | 338662 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337579 3MONTCELO.E! 115 338662 3MONTONGO# 115 1 |  | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201385 | 23S | Approved | P2 | 9 | 3GLENDALE# | VL |  |  |  |  | 0.9124 | 0.9642 | 0.92 | 1.05 | 520 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 338657 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  | Project Approved |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201385 | 23S | Approved | P2 | 9 | 3GLENDALE# | VL |  |  |  |  | 0.9124 | 0.9642 | 0.92 | 1.05 | 520 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 338657 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201386 | 23S | Approved | P2 | 9 | 3PINEBERGEN# | VL |  |  |  |  | 0.9087 | 0.9618 | 0.92 | 1.05 | 520 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 338660 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  | Project Approved |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201386 | 23S | Approved | P2 | 9 | 3PINEBERGEN# | VL |  |  |  |  | 0.9087 | 0.9618 | 0.92 | 1.05 | 520 | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 | 338660 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337619 3WOODWARD-S! 115 338660 3PINEBERGEN# 115 1 |  | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
201387 | 23S | Approved | P1 | 9 | 3 34TH&MAIN | VL |  |  |  |  | 0.9177 | 0.9512 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201388 | 23S | Approved | P1 | 9 | 3PINEBLUF.E% | VL |  |  |  |  | 0.908 | 0.9495 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201389 | 23S | Approved | P1 | 9 | 3MCCAMANT! | VL |  |  |  |  | 0.9057 | 0.9547 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201390 | 23S | Approved | P1 | 9 | 3PINEBLUF.W | VL |  |  |  |  | 0.9057 | 0.9578 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337626 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201391 | 23S | Approved | P1 | 9 | 3PB IP SS% | VL |  |  |  |  | 0.905 | 0.9434 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201392 | 23S | Approved | P1 | 9 | 3PB IP! | VL |  |  |  |  | 0.9044 | 0.9428 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201393 | 23S | Approved | P1 | 9 | 3PB PORT | VL |  |  |  |  | 0.9045 | 0.9429 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201394 | 23S | Approved | P1 | 9 | 3PB ENERGY! | VL |  |  |  |  | 0.9044 | 0.9429 | 0.92 | 1.05 | 521 | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337620 3WOODWARD-N! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201395 | 23S | Approved | P1 | 9 | 3PB IP SS% | VL |  |  |  |  | 0.9179 | 0.9434 | 0.92 | 1.05 | 532 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201396 | 23S | Approved | P1 | 9 | 3PB IP! | VL |  |  |  |  | 0.9173 | 0.9428 | 0.92 | 1.05 | 532 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201397 | 23S | Approved | P1 | 9 | 3PB PORT | VL |  |  |  |  | 0.9174 | 0.9429 | 0.92 | 1.05 | 532 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201398 | 23S | Approved | P1 | 9 | 3PB ENERGY! | VL |  |  |  |  | 0.9174 | 0.9429 | 0.92 | 1.05 | 532 | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337625 3MCCAMANT! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201399 | 23S | Approved | P1 | 9 | 3PB IP SS% | VL |  |  |  |  | 0.9159 | 0.9434 | 0.92 | 1.05 | 533 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201400 | 23S | Approved | P1 | 9 | 3PB IP! | VL |  |  |  |  | 0.9153 | 0.9428 | 0.92 | 1.05 | 533 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201401 | 23S | Approved | P1 | 9 | 3PB PORT | VL |  |  |  |  | 0.9154 | 0.9429 | 0.92 | 1.05 | 533 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201402 | 23S | Approved | P1 | 9 | 3PB ENERGY! | VL |  |  |  |  | 0.9153 | 0.9429 | 0.92 | 1.05 | 533 | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337624 3PINEBLUF.E% 115 337627 3PB IP SS% 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201403 | 23S | Approved | P1 | 9 | 3 34TH&MAIN | VL |  |  |  |  | 0.9176 | 0.9512 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201404 | 23S | Approved | P1 | 9 | 3PINEBLUF.E% | VL |  |  |  |  | 0.908 | 0.9495 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201405 | 23S | Approved | P1 | 9 | 3MCCAMANT! | VL |  |  |  |  | 0.9057 | 0.9547 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201406 | 23S | Approved | P1 | 9 | 3PB IP SS% | VL |  |  |  |  | 0.905 | 0.9434 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201407 | 23S | Approved | P1 | 9 | 3PB IP! | VL |  |  |  |  | 0.9044 | 0.9428 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201408 | 23S | Approved | P1 | 9 | 3PB PORT | VL |  |  |  |  | 0.9045 | 0.9429 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201409 | 23S | Approved | P1 | 9 | 3PB ENERGY! | VL |  |  |  |  | 0.9044 | 0.9429 | 0.92 | 1.05 | 534 | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337625 3MCCAMANT! 115 337626 3PINEBLUF.W 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201410 | 23S | Approved | P1 | 9 | 3PB IP SS% | VL |  |  |  |  | 0.9164 | 0.9434 | 0.92 | 1.05 | 555 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201411 | 23S | Approved | P1 | 9 | 3PB IP! | VL |  |  |  |  | 0.9158 | 0.9428 | 0.92 | 1.05 | 555 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201412 | 23S | Approved | P1 | 9 | 3PB PORT | VL |  |  |  |  | 0.9159 | 0.9429 | 0.92 | 1.05 | 555 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201413 | 23S | Approved | P1 | 9 | 3PB ENERGY! | VL |  |  |  |  | 0.9158 | 0.9429 | 0.92 | 1.05 | 555 | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337650 8WHT BLUF-XF 500 337651 8WHT BLUFF% 500 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201414 | 23S | Approved | P2 | 9 | 3MALVERN.S | VL |  |  |  |  | 0.9103 | 0.9683 | 0.92 | 1.05 | 606 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337746 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
201415 | 23S | Approved | P2 | 9 | 3T.E.P/S-4+ | VL |  |  |  |  | 0.9118 | 0.9673 | 0.92 | 1.05 | 606 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337747 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
201416 | 23S | Approved | P2 | 9 | 3T.E.P/S-4 | VL |  |  |  |  | 0.9026 | 0.959 | 0.92 | 1.05 | 606 | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 | 337748 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337718 3CARPENTER! 115 337746 3MALVERN.S 115 1 |  | Project Proposed |  | 12-EAI-027-CP | 2017-06-01 | Install 10.2 Mvar capacitor bank at Malvern South 115 kV
201417 | 23S | Approved | P2 | 9 | 3BAUXITE | VL |  |  |  |  | 0.8946 | 0.9598 | 0.92 | 1.05 | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337802 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
201418 | 23S | Approved | P2 | 9 | 3BRYANT | VL |  |  |  |  | 0.8865 | 0.9632 | 0.92 | 1.05 | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337803 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
201419 | 23S | Approved | P2 | 9 | 3ALCOA RD | VL |  |  |  |  | 0.8915 | 0.9568 | 0.92 | 1.05 | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 338433 |  |  |  | 115 | 115 | 336 | BUBA |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
201420 | 23S | Approved | P2 | 9 | 3BRYANT.S# | VL |  |  |  |  | 0.8881 | 0.961 | 0.92 | 1.05 | 624 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 338757 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
201421 | 23S | Approved | P2 | 9 | 3BAUCUM | VL |  |  |  |  | 0.9109 | 0.9936 | 0.92 | 1.05 | 727 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 337956 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201422 | 23S | Approved | P2 | 9 | 3ENGLAND# | VL |  |  |  |  | 0.9166 | 0.9744 | 0.92 | 1.05 | 727 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 338753 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201423 | 23S | Approved | P2 | 9 | 3KEO# | VL |  |  |  |  | 0.9141 | 0.9794 | 0.92 | 1.05 | 727 | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 | 338754 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 337956 3BAUCUM 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201424 | 23S | Approved | P2 | 9 | 3STUTGART.N+ | VL |  |  |  |  | 0.9167 | 0.9876 | 0.92 | 1.05 | 739 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201425 | 23S | Approved | P2 | 9 | 3STUTGART.N | VL |  |  |  |  | 0.9146 | 0.9856 | 0.92 | 1.05 | 739 | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337965 3STUTGART.N+ 115 337967 3RICUSKEY! 115 1 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201426 | 23S | Approved | P1 | 9 | 3STUTGART.N+ | VL |  |  |  |  | 0.9058 | 0.9876 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201427 | 23S | Approved | P1 | 9 | 3STUTGART.N | VL |  |  |  |  | 0.9036 | 0.9856 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201428 | 23S | Approved | P1 | 9 | 3RICUSKEY! | VL |  |  |  |  | 0.9059 | 0.9926 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201429 | 23S | Approved | P1 | 9 | 3STUTGART IN | VL |  |  |  |  | 0.9054 | 0.9874 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201430 | 23S | Approved | P1 | 9 | 3ULM | VL |  |  |  |  | 0.913 | 0.9865 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201431 | 23S | Approved | P1 | 9 | 3ALMYRA | VL |  |  |  |  | 0.903 | 0.9753 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201432 | 23S | Approved | P1 | 9 | 3DEWITT | VL |  |  |  |  | 0.9045 | 0.9658 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201433 | 23S | Approved | P1 | 9 | 3GILLETT! | VL |  |  |  |  | 0.9154 | 0.964 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201434 | 23S | Approved | P1 | 9 | 3HUMPHREY# | VL |  |  |  |  | 0.911 | 0.9782 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201435 | 23S | Approved | P1 | 9 | 3DELUCE# | VL |  |  |  |  | 0.9098 | 0.9626 | 0.92 | 1.05 | 741 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201436 | 23S | Approved | P2 | 9 | 3STUTGART IN | VL |  |  |  |  | 0.8929 | 0.9874 | 0.92 | 1.05 | 742 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
201437 | 23S | Approved | P2 | 9 | 3ULM | VL |  |  |  |  | 0.9015 | 0.9865 | 0.92 | 1.05 | 742 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
201438 | 23S | Approved | P2 | 9 | 3ALMYRA | VL |  |  |  |  | 0.5297 | 0.9753 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201439 | 23S | Approved | P2 | 9 | 3DEWITT | VL |  |  |  |  | 0.5348 | 0.9658 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201440 | 23S | Approved | P2 | 9 | 3GILLETT! | VL |  |  |  |  | 0.5641 | 0.964 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201441 | 23S | Approved | P2 | 9 | 3ELAINE | VL |  |  |  |  | 0.6706 | 0.965 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201442 | 23S | Approved | P2 | 9 | 3MARVELL | VL |  |  |  |  | 0.7422 | 0.9673 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201443 | 23S | Approved | P2 | 9 | 3BARTON | VL |  |  |  |  | 0.7716 | 0.968 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201444 | 23S | Approved | P2 | 9 | 3HELENA.W+ | VL |  |  |  |  | 0.827 | 0.9694 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201445 | 23S | Approved | P2 | 9 | 3HELENA.C | VL |  |  |  |  | 0.8482 | 0.9699 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201446 | 23S | Approved | P2 | 9 | 3RITCHIE! | VL |  |  |  |  | 0.8795 | 0.9725 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337986 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201447 | 23S | Approved | P2 | 9 | 3HELENA.S | VL |  |  |  |  | 0.882 | 0.9707 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337987 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201448 | 23S | Approved | P2 | 9 | 3HELENA.W! | VL |  |  |  |  | 0.8882 | 0.9702 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337988 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201449 | 23S | Approved | P2 | 9 | 2DELUCE | VL |  |  |  |  | 0.5651 | 0.9873 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201450 | 23S | Approved | P2 | 9 | 3DELUCE# | VL |  |  |  |  | 0.551 | 0.9626 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201451 | 23S | Approved | P2 | 9 | 3HELENA IN#! | VL |  |  |  |  | 0.877 | 0.9722 | 0.92 | 1.05 | 743 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201452 | 23S | Approved | P1 | 9 | 3DEWITT | VL |  |  |  |  | 0.8478 | 0.9658 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201453 | 23S | Approved | P1 | 9 | 3GILLETT! | VL |  |  |  |  | 0.8588 | 0.964 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201454 | 23S | Approved | P1 | 9 | 3ELAINE | VL |  |  |  |  | 0.8887 | 0.965 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201455 | 23S | Approved | P1 | 9 | 3MARVELL | VL |  |  |  |  | 0.9121 | 0.9673 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201456 | 23S | Approved | P1 | 9 | 2DELUCE | VL |  |  |  |  | 0.8747 | 0.9873 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201457 | 23S | Approved | P1 | 9 | 3DELUCE# | VL |  |  |  |  | 0.8528 | 0.9626 | 0.92 | 1.05 | 748 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201458 | 23S | Approved | P1 | 9 | 3ELAINE | VL |  |  |  |  | 0.8989 | 0.965 | 0.92 | 1.05 | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201459 | 23S | Approved | P1 | 9 | 3MARVELL | VL |  |  |  |  | 0.892 | 0.9673 | 0.92 | 1.05 | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201460 | 23S | Approved | P1 | 9 | 3BARTON | VL |  |  |  |  | 0.8895 | 0.968 | 0.92 | 1.05 | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201461 | 23S | Approved | P1 | 9 | 3HELENA.W+ | VL |  |  |  |  | 0.8856 | 0.9694 | 0.92 | 1.05 | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201462 | 23S | Approved | P1 | 9 | 3HELENA.C | VL |  |  |  |  | 0.8841 | 0.9699 | 0.92 | 1.05 | 756 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201463 | 23S | Approved | P1 | 9 | 3GILLETT! | VL |  |  |  |  | 0.9064 | 0.964 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201464 | 23S | Approved | P1 | 9 | 3ELAINE | VL |  |  |  |  | 0.8777 | 0.965 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201465 | 23S | Approved | P1 | 9 | 3MARVELL | VL |  |  |  |  | 0.869 | 0.9673 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201466 | 23S | Approved | P1 | 9 | 3BARTON | VL |  |  |  |  | 0.866 | 0.968 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201467 | 23S | Approved | P1 | 9 | 3HELENA.W+ | VL |  |  |  |  | 0.8613 | 0.9694 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201468 | 23S | Approved | P1 | 9 | 3HELENA.C | VL |  |  |  |  | 0.8595 | 0.9699 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201469 | 23S | Approved | P1 | 9 | 3DELUCE# | VL |  |  |  |  | 0.9116 | 0.9626 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201470 | 23S | Approved | P1 | 9 | 3HELENA IN#! | VL |  |  |  |  | 0.8591 | 0.9722 | 0.92 | 1.05 | 759 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201471 | 23S | Approved | P2 | 9 | 3CABOT | VL |  |  |  |  | 0.7097 | 0.9902 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338006 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201472 | 23S | Approved | P2 | 9 | 3BEEBE | VL |  |  |  |  | 0.7445 | 0.9812 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201473 | 23S | Approved | P2 | 9 | 3GARNER+ | VL |  |  |  |  | 0.7777 | 0.9856 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201474 | 23S | Approved | P2 | 9 | 3T.E.P/S-MC | VL |  |  |  |  | 0.7775 | 0.9854 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201475 | 23S | Approved | P2 | 9 | 3SRCY PRICE! | VL |  |  |  |  | 0.8349 | 0.9915 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201476 | 23S | Approved | P2 | 9 | 3GRIFFITHVLE | VL |  |  |  |  | 0.8563 | 0.9893 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338011 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201477 | 23S | Approved | P2 | 9 | 3DES ARC | VL |  |  |  |  | 0.8885 | 0.9892 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338012 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201478 | 23S | Approved | P2 | 9 | 5SRCY PRICE! | VL |  |  |  |  | 0.8579 | 0.984 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201479 | 23S | Approved | P2 | 9 | 5SEARCY.S | VL |  |  |  |  | 0.8617 | 0.9832 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201480 | 23S | Approved | P2 | 9 | 5BALD KNOB | VL |  |  |  |  | 0.881 | 0.9838 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201481 | 23S | Approved | P2 | 9 | 5T.E.P/S-6 | VL |  |  |  |  | 0.886 | 0.9843 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201482 | 23S | Approved | P2 | 9 | 3T.E.P/S-6 | VL |  |  |  |  | 0.8632 | 0.96 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201483 | 23S | Approved | P2 | 9 | 2WARD | VL |  |  |  |  | 0.7287 | 1.0067 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201484 | 23S | Approved | P2 | 9 | 5COPPERSPRG# | VL |  |  |  |  | 0.8812 | 0.9883 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201485 | 23S | Approved | P2 | 9 | 3WARD# | VL |  |  |  |  | 0.7105 | 0.9815 | 0.92 | 1.05 | 777 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201486 | 23S | Approved | P1 | 9 | 3BEEBE | VL |  |  |  |  | 0.8645 | 0.9812 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201487 | 23S | Approved | P1 | 9 | 3GARNER+ | VL |  |  |  |  | 0.8827 | 0.9856 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201488 | 23S | Approved | P1 | 9 | 3T.E.P/S-MC | VL |  |  |  |  | 0.8826 | 0.9854 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201489 | 23S | Approved | P1 | 9 | 3SRCY PRICE! | VL |  |  |  |  | 0.9122 | 0.9915 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201490 | 23S | Approved | P1 | 9 | 5SRCY PRICE! | VL |  |  |  |  | 0.918 | 0.984 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201491 | 23S | Approved | P1 | 9 | 5SEARCY.S | VL |  |  |  |  | 0.9195 | 0.9832 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201492 | 23S | Approved | P1 | 9 | 3T.E.P/S-6 | VL |  |  |  |  | 0.9085 | 0.96 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201493 | 23S | Approved | P1 | 9 | 2WARD | VL |  |  |  |  | 0.8629 | 1.0067 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201494 | 23S | Approved | P1 | 9 | 3WARD# | VL |  |  |  |  | 0.8413 | 0.9815 | 0.92 | 1.05 | 778 | 338006 3CABOT 115 338756 3WARD# 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338756 3WARD# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
201495 | 23S | Approved | P2 | 9 | 5WYNNE.S | VL |  |  |  |  | 0.9148 | 0.9735 | 0.92 | 1.05 | 806 | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 | 338031 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 |  | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
201496 | 23S | Approved | P2 | 9 | 5WYNNE IND | VL |  |  |  |  | 0.9137 | 0.9725 | 0.92 | 1.05 | 806 | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 | 338032 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 |  | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
201497 | 23S | Approved | P2 | 9 | 5WYNNE.E# | VL |  |  |  |  | 0.9114 | 0.9769 | 0.92 | 1.05 | 806 | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 | 338883 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338033 5PARKIN! 161 338883 5WYNNE.E# 161 1 |  | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
201498 | 23S | Approved | P1 | 9 | 2HARRISON.S | VH |  |  |  |  | 1.0501 | 1.0343 | 0.92 | 1.05 | 820 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
201499 | 23S | Approved | P1 | 9 | 8SANS SOUCI% | VH |  |  |  |  | 1.0522 | 1.0342 | 0.92 | 1.05 | 892 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
201500 | 23S | Approved | P1 | 9 | 5POCHNTAS.N | VL |  |  |  |  | 0.8266 | 0.9845 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201501 | 23S | Approved | P1 | 9 | 5DATTO | VL |  |  |  |  | 0.8222 | 0.9756 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201502 | 23S | Approved | P1 | 9 | 3DATTO | VL |  |  |  |  | 0.8426 | 0.9981 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201503 | 23S | Approved | P1 | 9 | 3CORNING | VL |  |  |  |  | 0.8401 | 0.9883 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201504 | 23S | Approved | P1 | 9 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8262 | 0.984 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201505 | 23S | Approved | P1 | 9 | 5POCHNTAS.W# | VL |  |  |  |  | 0.826 | 0.9838 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201506 | 23S | Approved | P1 | 9 | 3CORNING.N# | VL |  |  |  |  | 0.8402 | 0.9894 | 0.92 | 1.05 | 926 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201507 | 23S | Approved | P1 | 9 | 5DATTO | VL |  |  |  |  | 0.8746 | 0.9756 | 0.92 | 1.05 | 927 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201508 | 23S | Approved | P1 | 9 | 3DATTO | VL |  |  |  |  | 0.9016 | 0.9981 | 0.92 | 1.05 | 927 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201509 | 23S | Approved | P1 | 9 | 3CORNING | VL |  |  |  |  | 0.9041 | 0.9883 | 0.92 | 1.05 | 927 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201510 | 23S | Approved | P1 | 9 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8724 | 0.984 | 0.92 | 1.05 | 927 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201511 | 23S | Approved | P1 | 9 | 3CORNING.N# | VL |  |  |  |  | 0.9037 | 0.9894 | 0.92 | 1.05 | 927 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201512 | 23S | Approved | P1 | 9 | 5DATTO | VL |  |  |  |  | 0.9172 | 0.9756 | 0.92 | 1.05 | 928 | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201513 | 23S | Approved | P2 | 9 | 3LONOKE.E | VL |  |  |  |  | 0.9167 | 0.9826 | 0.92 | 1.05 | 1060 | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 | 338004 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 |  | voltage issue will be gone after White Bluff-woodward 230kV, stuttgart Ricuskey cap banck and Stuttgart industrial cap bank
201514 | 23S | Approved | P2 | 9 | 3NLR GALLOWY | VL |  |  |  |  | 0.9141 | 0.9957 | 0.92 | 1.05 | 1060 | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 | 338489 |  |  |  | 115 | 115 | 339 | NLR |  |  | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 |  | voltage issue will be gone after White Bluff-woodward 230kV, stuttgart Ricuskey cap banck and Stuttgart industrial cap bank
201515 | 23S | Approved | P2 | 9 | 3REMINGTON# | VL |  |  |  |  | 0.914 | 0.9883 | 0.92 | 1.05 | 1060 | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 | 338755 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337949 3LYNCH-W! 115 338489 3NLR GALLOWY 115 1 |  | voltage issue will be gone after White Bluff-woodward 230kV, stuttgart Ricuskey cap banck and Stuttgart industrial cap bank
201516 | 23S | Approved | P1 | 9 | 2IMBODEN! | VL |  |  |  |  | 0.8297 | 0.9846 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338221 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201517 | 23S | Approved | P1 | 9 | 2WTR VALLEY! | VL |  |  |  |  | 0.8294 | 0.9843 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338222 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201518 | 23S | Approved | P1 | 9 | 5WTR VALLEY+ | VL |  |  |  |  | 0.829 | 0.9838 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338223 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201519 | 23S | Approved | P1 | 9 | 5WTR VALLEY | VL |  |  |  |  | 0.829 | 0.9838 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338224 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201520 | 23S | Approved | P1 | 9 | 5POCHNTAS.N | VL |  |  |  |  | 0.8295 | 0.9845 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201521 | 23S | Approved | P1 | 9 | 5DATTO | VL |  |  |  |  | 0.8248 | 0.9756 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201522 | 23S | Approved | P1 | 9 | 3DATTO | VL |  |  |  |  | 0.845 | 0.9981 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201523 | 23S | Approved | P1 | 9 | 3CORNING | VL |  |  |  |  | 0.8422 | 0.9883 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201524 | 23S | Approved | P1 | 9 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8291 | 0.984 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201525 | 23S | Approved | P1 | 9 | 5POCHNTAS.W# | VL |  |  |  |  | 0.829 | 0.9838 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201526 | 23S | Approved | P1 | 9 | 3CORNING.N# | VL |  |  |  |  | 0.8423 | 0.9894 | 0.92 | 1.05 | 1088 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201527 | 23S | Approved | P1 | 9 | 3LONOKE.E | VL |  |  |  |  | 0.915 | 0.9826 | 0.92 | 1.05 | 1089 | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 | 338004 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201527 | 23S | Approved | P1 | 9 | 3LONOKE.E | VL |  |  |  |  | 0.915 | 0.9826 | 0.92 | 1.05 | 1089 | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 | 338004 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 |  | Project Approved | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201528 | 23S | Approved | P1 | 9 | 3REMINGTON# | VL |  |  |  |  | 0.912 | 0.9883 | 0.92 | 1.05 | 1089 | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 | 338755 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 |  | Project Approved | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201528 | 23S | Approved | P1 | 9 | 3REMINGTON# | VL |  |  |  |  | 0.912 | 0.9883 | 0.92 | 1.05 | 1089 | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 | 338755 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338489 3NLR GALLOWY 115 338755 3REMINGTON# 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201529 | 23S | Approved | P1 | 9 | 4NEWCANY! | VL |  |  |  |  | 0.865 | 0.964 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201530 | 23S | Approved | P1 | 9 | 4HICKORY | VL |  |  |  |  | 0.8783 | 0.9639 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201531 | 23S | Approved | P1 | 9 | 4EASTGAT | VL |  |  |  |  | 0.8943 | 0.9665 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201531 | 23S | Approved | P1 | 9 | 4EASTGAT | VL |  |  |  |  | 0.8943 | 0.9665 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201532 | 23S | Approved | P1 | 9 | 4HUFFMAN | VL |  |  |  |  | 0.8924 | 0.9648 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201532 | 23S | Approved | P1 | 9 | 4HUFFMAN | VL |  |  |  |  | 0.8924 | 0.9648 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201533 | 23S | Approved | P1 | 9 | 46L533TP8 | VL |  |  |  |  | 0.9151 | 0.9718 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201533 | 23S | Approved | P1 | 9 | 46L533TP8 | VL |  |  |  |  | 0.9151 | 0.9718 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201534 | 23S | Approved | P1 | 9 | 4KLMP-EX | VL |  |  |  |  | 0.9151 | 0.9718 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201534 | 23S | Approved | P1 | 9 | 4KLMP-EX | VL |  |  |  |  | 0.9151 | 0.9718 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201535 | 23S | Approved | P1 | 9 | 4ROLKERD | VL |  |  |  |  | 0.9188 | 0.9727 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201535 | 23S | Approved | P1 | 9 | 4ROLKERD | VL |  |  |  |  | 0.9188 | 0.9727 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201536 | 23S | Approved | P1 | 9 | 4ADAYTON! | VL |  |  |  |  | 0.9186 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201536 | 23S | Approved | P1 | 9 | 4ADAYTON! | VL |  |  |  |  | 0.9186 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201537 | 23S | Approved | P1 | 9 | 4BDAYTON! | VL |  |  |  |  | 0.9187 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201537 | 23S | Approved | P1 | 9 | 4BDAYTON! | VL |  |  |  |  | 0.9187 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201538 | 23S | Approved | P1 | 9 | 4LIBERTY-SR | VL |  |  |  |  | 0.9191 | 0.966 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201538 | 23S | Approved | P1 | 9 | 4LIBERTY-SR | VL |  |  |  |  | 0.9191 | 0.966 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201539 | 23S | Approved | P1 | 9 | 4GORDON | VL |  |  |  |  | 0.9186 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
201539 | 23S | Approved | P1 | 9 | 4GORDON | VL |  |  |  |  | 0.9186 | 0.9726 | 0.92 | 1.05 | 1193 | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | 334100 4PORTER% 138 334111 4NEWCANY! 138 1 |  | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
201540 | 23S | Approved | P1 | 9 | 4CHINA% | VL |  |  |  |  | 0.9187 | 1.0009 | 0.92 | 1.05 | 1242 | 334204 6CHINA% 230 334215 4CHINA% 138 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | 334204 6CHINA% 230 334215 4CHINA% 138 1 |  | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
201541 | 23S | Approved | P1 | 9 | 4MILLCR! | VL |  |  |  |  | 0.8811 | 0.9945 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201542 | 23S | Approved | P1 | 9 | 4PINELND | VL |  |  |  |  | 0.871 | 0.9762 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201543 | 23S | Approved | P1 | 9 | 4BROADUS | VL |  |  |  |  | 0.8661 | 0.9722 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201544 | 23S | Approved | P1 | 9 | 4ETOIL | VL |  |  |  |  | 0.8641 | 0.9705 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201545 | 23S | Approved | P1 | 9 | 4HRTNHIL | VL |  |  |  |  | 0.8746 | 0.9842 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201546 | 23S | Approved | P1 | 9 | 2PINELND | VL |  |  |  |  | 0.8849 | 0.9844 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201547 | 23S | Approved | P1 | 9 | 2TEMPL1* | VL |  |  |  |  | 0.8829 | 0.9827 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201548 | 23S | Approved | P1 | 9 | 2TEMPLE1 | VL |  |  |  |  | 0.8826 | 0.9823 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201549 | 23S | Approved | P1 | 9 | 2TEMPL2* | VL |  |  |  |  | 0.8826 | 0.9824 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201550 | 23S | Approved | P1 | 9 | 2TEMPLE2 | VL |  |  |  |  | 0.8825 | 0.9823 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201551 | 23S | Approved | P1 | 9 | 2TMPLSWC | VL |  |  |  |  | 0.8826 | 0.9824 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201552 | 23S | Approved | P1 | 9 | 2WEIRGAT | VL |  |  |  |  | 0.8709 | 0.9724 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201553 | 23S | Approved | P1 | 9 | 4PEACH! | VL |  |  |  |  | 0.8921 | 0.9928 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201554 | 23S | Approved | P1 | 9 | 4UNONGSU! | VL |  |  |  |  | 0.9078 | 0.9916 | 0.92 | 1.05 | 1301 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201555 | 23S | Approved | P1 | 9 | 4JNE EVA | VL |  |  |  |  | 0.9199 | 1.0043 | 0.92 | 1.05 | 1324 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334308 |  |  |  | 138 | 138 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201556 | 23S | Approved | P1 | 9 | 2SABRA | VL |  |  |  |  | 0.9187 | 0.9914 | 0.92 | 1.05 | 1560 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334704 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201557 | 23S | Approved | P1 | 9 | 2DEWEYVL! | VL |  |  |  |  | 0.9192 | 0.9831 | 0.92 | 1.05 | 1560 | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | 334703 2ECHO! 69.0 334704 2SABRA 69.0 1 |  | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
201558 | 23S | Approved | P1 | 9 | 4LEBLANC! | VL |  |  |  |  | 0.8802 | 0.959 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201558 | 23S | Approved | P1 | 9 | 4LEBLANC! | VL |  |  |  |  | 0.8802 | 0.959 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201559 | 23S | Approved | P1 | 9 | 4ABBEVILLE | VL |  |  |  |  | 0.9142 | 0.9635 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335386 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201559 | 23S | Approved | P1 | 9 | 4ABBEVILLE | VL |  |  |  |  | 0.9142 | 0.9635 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335386 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201560 | 23S | Approved | P1 | 9 | 4DELCAMBRE | VL |  |  |  |  | 0.8797 | 0.9647 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201560 | 23S | Approved | P1 | 9 | 4DELCAMBRE | VL |  |  |  |  | 0.8797 | 0.9647 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201561 | 23S | Approved | P1 | 9 | ABBEVL 4 | VL |  |  |  |  | 0.9142 | 0.9635 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 500010 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201561 | 23S | Approved | P1 | 9 | ABBEVL 4 | VL |  |  |  |  | 0.9142 | 0.9635 | 0.92 | 1.05 | 1800 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 500010 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201562 | 23S | Approved | P1 | 9 | 2ST_MARTIN | VL |  |  |  |  | 0.9169 | 0.9556 | 0.92 | 1.05 | 1803 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201563 | 23S | Approved | P1 | 9 | LONGFL 2 | VL |  |  |  |  | 0.9169 | 0.9556 | 0.92 | 1.05 | 1803 | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335388 4MORIL! 138 335405 2MORIL! 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201564 | 23S | Approved | P1 | 9 | 2LINE-625_OP | VL |  |  |  |  | 0.9117 | 0.9609 | 0.92 | 1.05 | 1812 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201565 | 23S | Approved | P1 | 9 | 2ST_MARTIN | VL |  |  |  |  | 0.9061 | 0.9556 | 0.92 | 1.05 | 1812 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201566 | 23S | Approved | P1 | 9 | LONGFL 2 | VL |  |  |  |  | 0.9061 | 0.9556 | 0.92 | 1.05 | 1812 | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335405 2MORIL! 69.0 335408 2NEW_IBERIA!69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201567 | 23S | Approved | P1 | 9 | 2LINE-625_OP | VL |  |  |  |  | 0.8994 | 0.9609 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201567 | 23S | Approved | P1 | 9 | 2LINE-625_OP | VL |  |  |  |  | 0.8994 | 0.9609 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201568 | 23S | Approved | P1 | 9 | 2ST_MARTIN | VL |  |  |  |  | 0.8937 | 0.9556 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201568 | 23S | Approved | P1 | 9 | 2ST_MARTIN | VL |  |  |  |  | 0.8937 | 0.9556 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201569 | 23S | Approved | P1 | 9 | LONGFL 2 | VL |  |  |  |  | 0.8937 | 0.9556 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Proposed |  | 14-EGL-001-CP | 2015-06-01 | Move Longfellow to Cade Switch 69 kV Normally Open Point
201569 | 23S | Approved | P1 | 9 | LONGFL 2 | VL |  |  |  |  | 0.8937 | 0.9556 | 0.92 | 1.05 | 1814 | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335409 2CADE_SW_STA69.0 1 |  | Project Horizon |  | 14-EGL-011-HZ | 2022-06-01 | Longfellow to Cade Switch - Construct new 69kV parallel line from New Iberia to Line 625A Tap Point.
201570 | 23S | Approved | P1 | 9 | 2PARKS | VL |  |  |  |  | 0.9107 | 0.9923 | 0.92 | 1.05 | 1825 | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 | 335425 |  |  |  | 69 | 69 | 351 | EES |  |  | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201571 | 23S | Approved | P1 | 9 | 2ST_JOHN | VL |  |  |  |  | 0.9111 | 0.9845 | 0.92 | 1.05 | 1825 | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 | 335426 |  |  |  | 69 | 69 | 351 | EES |  |  | 335424 2CECELIA! 69.0 335425 2PARKS 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201572 | 23S | Approved | P1 | 9 | 2ST_JOHN | VL |  |  |  |  | 0.9128 | 0.9845 | 0.92 | 1.05 | 1826 | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 | 335426 |  |  |  | 69 | 69 | 351 | EES |  |  | 335425 2PARKS 69.0 335426 2ST_JOHN 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201573 | 23S | Approved | P1 | 9 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9059 | 0.9588 | 0.92 | 1.05 | 1841 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201574 | 23S | Approved | P1 | 9 | 4BOBCAT | VL |  |  |  |  | 0.9022 | 0.9657 | 0.92 | 1.05 | 1841 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201575 | 23S | Approved | P1 | 9 | 4LINE-642_TP | VL |  |  |  |  | 0.906 | 0.9588 | 0.92 | 1.05 | 1841 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201576 | 23S | Approved | P1 | 9 | 4COL_SPRINGS | VL |  |  |  |  | 0.9059 | 0.9587 | 0.92 | 1.05 | 1841 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201577 | 23S | Approved | P1 | 9 | 2NESSER_TP | VL |  |  |  |  | 0.8694 | 0.9755 | 0.92 | 1.05 | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201578 | 23S | Approved | P1 | 9 | 2NESSER | VL |  |  |  |  | 0.8641 | 0.9708 | 0.92 | 1.05 | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201579 | 23S | Approved | P1 | 9 | 2LN-372A_TP | VL |  |  |  |  | 0.8855 | 0.9897 | 0.92 | 1.05 | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335710 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201580 | 23S | Approved | P1 | 9 | 2JONESCREEK! | VL |  |  |  |  | 0.8891 | 0.986 | 0.92 | 1.05 | 1977 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201581 | 23S | Approved | P1 | 9 | 3CARLSL | VL |  |  |  |  | 0.8703 | 0.9815 | 0.92 | 1.05 | 2133 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
201582 | 23S | Approved | P1 | 9 | 3CLAYTN! | VL |  |  |  |  | 0.9162 | 0.9847 | 0.92 | 1.05 | 2186 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | 336230 |  |  |  | 115 | 115 | 351 | EES |  |  | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 |  | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
201583 | 23S | Approved | P1 | 9 | 3NORCO% | VL |  |  |  |  | 0.917 | 0.9819 | 0.92 | 1.05 | 2186 | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 | 336231 |  |  |  | 115 | 115 | 351 | EES |  |  | 336220 3GYPSY% 115 336230 3CLAYTN! 115 1 |  | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
201584 | 23S | Approved | P1 | 9 | 3JNESBORO_LA | VL |  |  |  |  | 0.8631 | 1.0047 | 0.92 | 1.05 | 2284 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337346 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201585 | 23S | Approved | P1 | 9 | 3HODGE_LA! | VL |  |  |  |  | 0.8642 | 1.0033 | 0.92 | 1.05 | 2284 | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | 337345 3DANVILE_LA! 115 337346 3JNESBORO_LA 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201586 | 23S | Approved | P1 | 9 | 3HODGE_LA! | VL |  |  |  |  | 0.9183 | 1.0033 | 0.92 | 1.05 | 2286 | 337346 3JNESBORO_LA 115 337347 3HODGE_LA! 115 1 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | 337346 3JNESBORO_LA 115 337347 3HODGE_LA! 115 1 |  | Project Distribution |  | 13-ELL-008-LD
201587 | 23S | Approved | P1 | 9 | 3MINDEN_LG | VL |  |  |  |  | 0.9195 | 0.9833 | 0.92 | 1.05 | 2296 | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 |  | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
201588 | 23S | Approved | P1 | 9 | 4LEBLANC! | VL |  |  |  |  | 0.8916 | 0.959 | 0.92 | 1.05 | 2456 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201588 | 23S | Approved | P1 | 9 | 4LEBLANC! | VL |  |  |  |  | 0.8916 | 0.959 | 0.92 | 1.05 | 2456 | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303150 4LEBLANC! 138 335387 4DELCAMBRE 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201589 | 23S | Approved | P1 | 9 | 3MINDEN_LG | VL |  |  |  |  | 0.8913 | 0.9833 | 0.92 | 1.05 | 2477 | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303302 3MINDEN_LG 115 337361 3MINDEN_LA! 115 1 |  | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
201590 | 23S | Approved | P1 | 9 | 3TRUSSEL_CR | VL |  |  |  |  | 0.9117 | 0.996 | 0.92 | 1.05 | 2480 | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1 | 303310 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303310 3TRUSSEL_CR 115 337371 3VIENNA_LA! 115 1
201591 | 23S | Approved | P1 | 9 | 4CANEY | VL |  |  |  |  | 0.9145 | 0.9933 | 0.92 | 1.05 | 2594 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
201592 | 23S | Approved | P1 | 9 | OAKDALE4 | VL |  |  |  |  | 0.9151 | 0.9913 | 0.92 | 1.05 | 2594 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
201593 | 23S | Approved | P1 | 9 | 4CANEY | VL |  |  |  |  | 0.8641 | 0.9933 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201594 | 23S | Approved | P1 | 9 | CENTNL 4 | VL |  |  |  |  | 0.9127 | 0.99 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201595 | 23S | Approved | P1 | 9 | OAKDALE4 | VL |  |  |  |  | 0.8661 | 0.9913 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201596 | 23S | Approved | P1 | 9 | PNPRARIE 4 | VL |  |  |  |  | 0.8569 | 1.0061 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201597 | 23S | Approved | P1 | 9 | WSTBAY 4 | VL |  |  |  |  | 0.878 | 0.9896 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201606 | 23S | Approved | P1 | 9 | ELKS 6 | VL |  |  |  |  | 0.9155 | 0.9801 | 0.92 | 1.05 | 2747 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  | turn on switch shunt at BEADLE 230kV sub
201607 | 23S | Approved | P1 | 9 | BEADLE 6 | VL |  |  |  |  | 0.916 | 0.9818 | 0.92 | 1.05 | 2747 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1
201608 | 23S | Approved | P1 | 9 | ELKS 6 | VL |  |  |  |  | 0.9008 | 0.9801 | 0.92 | 1.05 | 2772 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
201609 | 23S | Approved | P1 | 9 | 8THALMANN | VH |  |  |  |  | 1.0561 | 1.042 | 0.92 | 1.05 | 2866 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201610 | 23S | Approved | P1 | 9 | 8MCCALL RD | VH |  |  |  |  | 1.0709 | 1.0283 | 0.92 | 1.05 | 2866 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201611 | 23S | Approved | P1 | 9 | 8N TIFTON | VH |  |  |  |  | 1.0517 | 1.0386 | 0.92 | 1.05 | 2898 | 380024 8N TIFTON 500 380222 6N TIFTON 230 1 | 380024 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380024 8N TIFTON 500 380222 6N TIFTON 230 1 |  |  | VH
201612 | 23S | Approved | P1 | 9 | 8DANIEL | VH |  |  |  |  | 1.0753 | 1.0432 | 0.92 | 1.05 | 3605 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
201613 | 23S | Approved | P1 | 9 | 7SHAWNEE FP | VH |  |  |  |  | 1.0513 | 1.0388 | 0.92 | 1.05 | 3946 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
201614 | 23S | Approved | P1 | 9 | 8RUTHERFORD | VL |  |  |  |  | 0.8873 | 0.9664 | 0.92 | 1.05 | 3948 | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1 | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1
201615 | 23S | Approved | P2 | 9 | 5HIGHLAND | VL |  |  |  |  | 0.9166 | 0.9846 | 0.92 | 1.05 | 4450 | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 | 338220 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 |  | None
201616 | 23S | Approved | P1 | 9 | TENRUSK7 | VH |  |  |  |  | 1.0501 | 1.015 | 0.92 | 1.05 | 4656 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201617 | 23S | Approved | P1 | 9 | TENGEN 7 | VH |  |  |  |  | 1.0501 | 1.015 | 0.92 | 1.05 | 4656 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201618 | 23S | Approved | P1 | 9 | ELKCITY7 | VH |  |  |  |  | 1.0513 | 1.0246 | 0.92 | 1.05 | 4697 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
201619 | 23S | Approved | P0 | 10 | 5HORN LAKE% | VH |  |  |  |  | 1.0564 | 1.0564 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201620 | 23S | Approved | P0 | 10 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201621 | 23S | Approved | P0 | 10 | 8CENTRLAL | VH |  |  |  |  | 1.05 | 1.05 | 0.92 | 1.05 | 0 | ** Base Case ** | 385337 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201622 | 23S | Approved | P1 | 10 | 4LEBLANC! | VL |  |  |  |  | 0.8924 | 0.959 | 0.92 | 1.05 | 365 | P1_2-113 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201622 | 23S | Approved | P1 | 10 | 4LEBLANC! | VL |  |  |  |  | 0.8924 | 0.959 | 0.92 | 1.05 | 365 | P1_2-113 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201635 | 23S | Approved | P1 | 10 | 4MILLCR! | VL |  |  |  |  | 0.8811 | 0.9945 | 0.92 | 1.05 | 489 | P1_2-237 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201636 | 23S | Approved | P1 | 10 | 4PINELND | VL |  |  |  |  | 0.871 | 0.9762 | 0.92 | 1.05 | 489 | P1_2-237 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201637 | 23S | Approved | P1 | 10 | 4BROADUS | VL |  |  |  |  | 0.8661 | 0.9722 | 0.92 | 1.05 | 489 | P1_2-237 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201638 | 23S | Approved | P1 | 10 | 4ETOIL | VL |  |  |  |  | 0.8641 | 0.9705 | 0.92 | 1.05 | 489 | P1_2-237 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201639 | 23S | Approved | P1 | 10 | 4HRTNHIL | VL |  |  |  |  | 0.8746 | 0.9842 | 0.92 | 1.05 | 489 | P1_2-237 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201640 | 23S | Approved | P1 | 10 | 2PINELND | VL |  |  |  |  | 0.8849 | 0.9844 | 0.92 | 1.05 | 489 | P1_2-237 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201641 | 23S | Approved | P1 | 10 | 2TEMPL1* | VL |  |  |  |  | 0.8829 | 0.9827 | 0.92 | 1.05 | 489 | P1_2-237 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201642 | 23S | Approved | P1 | 10 | 2TEMPLE1 | VL |  |  |  |  | 0.8826 | 0.9823 | 0.92 | 1.05 | 489 | P1_2-237 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201643 | 23S | Approved | P1 | 10 | 2TEMPL2* | VL |  |  |  |  | 0.8826 | 0.9824 | 0.92 | 1.05 | 489 | P1_2-237 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201644 | 23S | Approved | P1 | 10 | 2TEMPLE2 | VL |  |  |  |  | 0.8825 | 0.9823 | 0.92 | 1.05 | 489 | P1_2-237 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201645 | 23S | Approved | P1 | 10 | 2TMPLSWC | VL |  |  |  |  | 0.8826 | 0.9824 | 0.92 | 1.05 | 489 | P1_2-237 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201646 | 23S | Approved | P1 | 10 | 2WEIRGAT | VL |  |  |  |  | 0.8709 | 0.9724 | 0.92 | 1.05 | 489 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201647 | 23S | Approved | P1 | 10 | 4PEACH! | VL |  |  |  |  | 0.8921 | 0.9928 | 0.92 | 1.05 | 489 | P1_2-237 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201648 | 23S | Approved | P1 | 10 | 4UNONGSU! | VL |  |  |  |  | 0.9078 | 0.9916 | 0.92 | 1.05 | 489 | P1_2-237 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201649 | 23S | Approved | P1 | 10 | 2ST_MARTIN | VL |  |  |  |  | 0.9169 | 0.9556 | 0.92 | 1.05 | 821 | P1_2-569 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201650 | 23S | Approved | P1 | 10 | LONGFL 2 | VL |  |  |  |  | 0.9169 | 0.9556 | 0.92 | 1.05 | 821 | P1_2-569 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-569_4MORIL!,2MORIL! |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201651 | 23S | Approved | P1 | 10 | 2LINE-625_OP | VL |  |  |  |  | 0.9117 | 0.9609 | 0.92 | 1.05 | 831 | P1_2-579 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201652 | 23S | Approved | P1 | 10 | 2ST_MARTIN | VL |  |  |  |  | 0.9061 | 0.9556 | 0.92 | 1.05 | 831 | P1_2-579 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201653 | 23S | Approved | P1 | 10 | LONGFL 2 | VL |  |  |  |  | 0.9061 | 0.9556 | 0.92 | 1.05 | 831 | P1_2-579 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-579 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201654 | 23S | Approved | P1 | 10 | 3CLAYTN! | VL |  |  |  |  | 0.9162 | 0.9847 | 0.92 | 1.05 | 1176 | P1_2-924 | 336230 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! |  | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
201655 | 23S | Approved | P1 | 10 | 3NORCO% | VL |  |  |  |  | 0.917 | 0.9819 | 0.92 | 1.05 | 1176 | P1_2-924 | 336231 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! |  | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
201656 | 23S | Approved | P1 | 10 | 8GGNS% | VL |  |  |  |  | 0.9802 | 1.0162 | 0.982 | 1.05 | 1285 | P1_2-1033 | 336820 |  |  |  | 500 | 500 | 326 | EES-EMI |  |  | P1_2-1033_8GGNS%,8BXTRWILSON% |  | None
201657 | 23S | Approved | P1 | 10 | 3HODGE_LA! | VL |  |  |  |  | 0.9186 | 1.0033 | 0.92 | 1.05 | 1436 | P1_2-1184 | 337347 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1184 |  | Project Distribution |  | 13-ELL-008-LD
201658 | 23S | Approved | P1 | 10 | 3MINDEN_LG | VL |  |  |  |  | 0.9195 | 0.9833 | 0.92 | 1.05 | 1444 | P1_2-1192 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! |  | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
201659 | 23S | Approved | P1 | 10 | 3 34TH&MAIN | VL |  |  |  |  | 0.9176 | 0.9512 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337623 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201660 | 23S | Approved | P1 | 10 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9079 | 0.9495 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201661 | 23S | Approved | P1 | 10 | 3MCCAMANT! | VL |  |  |  |  | 0.9056 | 0.9547 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337625 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201662 | 23S | Approved | P1 | 10 | 3PB IP SS% | VL |  |  |  |  | 0.9049 | 0.9434 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201663 | 23S | Approved | P1 | 10 | 3PB IP! | VL |  |  |  |  | 0.9043 | 0.9428 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201664 | 23S | Approved | P1 | 10 | 3PB PORT | VL |  |  |  |  | 0.9044 | 0.9429 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201665 | 23S | Approved | P1 | 10 | 3PB ENERGY! | VL |  |  |  |  | 0.9044 | 0.9429 | 0.92 | 1.05 | 1545 | P1_2-1293 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1293_3WOODWARD-N!,3MCCAMANT! |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201666 | 23S | Approved | P1 | 10 | 3PB IP SS% | VL |  |  |  |  | 0.9179 | 0.9434 | 0.92 | 1.05 | 1554 | P1_2-1302 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201667 | 23S | Approved | P1 | 10 | 3PB IP! | VL |  |  |  |  | 0.9173 | 0.9428 | 0.92 | 1.05 | 1554 | P1_2-1302 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201668 | 23S | Approved | P1 | 10 | 3PB PORT | VL |  |  |  |  | 0.9174 | 0.9429 | 0.92 | 1.05 | 1554 | P1_2-1302 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201669 | 23S | Approved | P1 | 10 | 3PB ENERGY! | VL |  |  |  |  | 0.9174 | 0.9429 | 0.92 | 1.05 | 1554 | P1_2-1302 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1302 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201670 | 23S | Approved | P1 | 10 | 3PB IP SS% | VL |  |  |  |  | 0.9159 | 0.9434 | 0.92 | 1.05 | 1555 | P1_2-1303 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201671 | 23S | Approved | P1 | 10 | 3PB IP! | VL |  |  |  |  | 0.9153 | 0.9428 | 0.92 | 1.05 | 1555 | P1_2-1303 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201672 | 23S | Approved | P1 | 10 | 3PB PORT | VL |  |  |  |  | 0.9154 | 0.9429 | 0.92 | 1.05 | 1555 | P1_2-1303 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201673 | 23S | Approved | P1 | 10 | 3PB ENERGY! | VL |  |  |  |  | 0.9153 | 0.9429 | 0.92 | 1.05 | 1555 | P1_2-1303 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1303 |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201674 | 23S | Approved | P1 | 10 | 3PB IP SS% | VL |  |  |  |  | 0.9164 | 0.9434 | 0.92 | 1.05 | 1565 | P1_2-1313 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201675 | 23S | Approved | P1 | 10 | 3PB IP! | VL |  |  |  |  | 0.9158 | 0.9428 | 0.92 | 1.05 | 1565 | P1_2-1313 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201676 | 23S | Approved | P1 | 10 | 3PB PORT | VL |  |  |  |  | 0.9159 | 0.9429 | 0.92 | 1.05 | 1565 | P1_2-1313 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201677 | 23S | Approved | P1 | 10 | 3PB ENERGY! | VL |  |  |  |  | 0.9158 | 0.9429 | 0.92 | 1.05 | 1565 | P1_2-1313 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% |  | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
201678 | 23S | Approved | P1 | 10 | 3STUTGART.N+ | VL |  |  |  |  | 0.9058 | 0.9876 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201679 | 23S | Approved | P1 | 10 | 3STUTGART.N | VL |  |  |  |  | 0.9036 | 0.9856 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201680 | 23S | Approved | P1 | 10 | 3RICUSKEY! | VL |  |  |  |  | 0.9059 | 0.9926 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201681 | 23S | Approved | P1 | 10 | 3STUTGART IN | VL |  |  |  |  | 0.9054 | 0.9874 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201682 | 23S | Approved | P1 | 10 | 3ULM | VL |  |  |  |  | 0.913 | 0.9865 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201683 | 23S | Approved | P1 | 10 | 3ALMYRA | VL |  |  |  |  | 0.903 | 0.9753 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201684 | 23S | Approved | P1 | 10 | 3DEWITT | VL |  |  |  |  | 0.9045 | 0.9658 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201685 | 23S | Approved | P1 | 10 | 3GILLETT! | VL |  |  |  |  | 0.9154 | 0.964 | 0.92 | 1.05 | 1693 | P1_2-1441 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201686 | 23S | Approved | P1 | 10 | 3HUMPHREY# | VL |  |  |  |  | 0.911 | 0.9782 | 0.92 | 1.05 | 1693 | P1_2-1441 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201687 | 23S | Approved | P1 | 10 | 3DELUCE# | VL |  |  |  |  | 0.9098 | 0.9626 | 0.92 | 1.05 | 1693 | P1_2-1441 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201688 | 23S | Approved | P1 | 10 | 3GILLETT! | VL |  |  |  |  | 0.9064 | 0.964 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201689 | 23S | Approved | P1 | 10 | 3ELAINE | VL |  |  |  |  | 0.8777 | 0.965 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201690 | 23S | Approved | P1 | 10 | 3MARVELL | VL |  |  |  |  | 0.869 | 0.9673 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201691 | 23S | Approved | P1 | 10 | 3BARTON | VL |  |  |  |  | 0.866 | 0.968 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201692 | 23S | Approved | P1 | 10 | 3HELENA.W+ | VL |  |  |  |  | 0.8613 | 0.9694 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201693 | 23S | Approved | P1 | 10 | 3HELENA.C | VL |  |  |  |  | 0.8595 | 0.9699 | 0.92 | 1.05 | 1700 | P1_2-1448 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201694 | 23S | Approved | P1 | 10 | 3DELUCE# | VL |  |  |  |  | 0.9116 | 0.9626 | 0.92 | 1.05 | 1700 | P1_2-1448 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201695 | 23S | Approved | P1 | 10 | 3HELENA IN#! | VL |  |  |  |  | 0.8591 | 0.9722 | 0.92 | 1.05 | 1700 | P1_2-1448 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201696 | 23S | Approved | P1 | 10 | 8SANS SOUCI% | VH |  |  |  |  | 1.0522 | 1.0342 | 0.92 | 1.05 | 1768 | P1_2-1519 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1519 |  |  | VH
201697 | 23S | Approved | P1 | 10 | 8DANIEL | VH |  |  |  |  | 1.0753 | 1.0432 | 0.92 | 1.05 | 1853 | P1_2-1604 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! |  |  | VH
201698 | 23S | Approved | P1 | 10 | 4CANEY | VL |  |  |  |  | 0.8641 | 0.9933 | 0.92 | 1.05 | 1902 | P1_2-1653 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201699 | 23S | Approved | P1 | 10 | CENTNL 4 | VL |  |  |  |  | 0.9127 | 0.99 | 0.92 | 1.05 | 1902 | P1_2-1653 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201700 | 23S | Approved | P1 | 10 | OAKDALE4 | VL |  |  |  |  | 0.8661 | 0.9913 | 0.92 | 1.05 | 1902 | P1_2-1653 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201701 | 23S | Approved | P1 | 10 | PNPRARIE 4 | VL |  |  |  |  | 0.8569 | 1.0061 | 0.92 | 1.05 | 1902 | P1_2-1653 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201702 | 23S | Approved | P1 | 10 | WSTBAY 4 | VL |  |  |  |  | 0.878 | 0.9896 | 0.92 | 1.05 | 1902 | P1_2-1653 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
201703 | 23S | Approved | P1 | 10 | 4VEAZIE | VL |  |  |  |  | 0.8811 | 0.9741 | 0.92 | 1.05 | 1903 | P1_2-1654 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201704 | 23S | Approved | P1 | 10 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9161 | 0.9588 | 0.92 | 1.05 | 1903 | P1_2-1654 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201705 | 23S | Approved | P1 | 10 | 4BOBCAT | VL |  |  |  |  | 0.9144 | 0.9657 | 0.92 | 1.05 | 1903 | P1_2-1654 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201706 | 23S | Approved | P1 | 10 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9152 | 0.9696 | 0.92 | 1.05 | 1903 | P1_2-1654 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201707 | 23S | Approved | P1 | 10 | 4LINE-642_TP | VL |  |  |  |  | 0.9162 | 0.9588 | 0.92 | 1.05 | 1903 | P1_2-1654 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201708 | 23S | Approved | P1 | 10 | 4COL_SPRINGS | VL |  |  |  |  | 0.9161 | 0.9587 | 0.92 | 1.05 | 1903 | P1_2-1654 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201709 | 23S | Approved | P1 | 10 | GUIDRY 4 | VL |  |  |  |  | 0.8798 | 0.9729 | 0.92 | 1.05 | 1903 | P1_2-1654 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201710 | 23S | Approved | P1 | 10 | PLAISAN4 | VL |  |  |  |  | 0.8958 | 0.9872 | 0.92 | 1.05 | 1903 | P1_2-1654 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201711 | 23S | Approved | P1 | 10 | TENRUSK7 | VH |  |  |  |  | 1.0501 | 1.015 | 0.92 | 1.05 | 2112 | P1_2-1863 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
201712 | 23S | Approved | P1 | 10 | TENGEN 7 | VH |  |  |  |  | 1.0501 | 1.015 | 0.92 | 1.05 | 2112 | P1_2-1863 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
201713 | 15S | Proposed | P0 | 11 | 5HORN LAKE% | VH |  |  |  |  | 1.0575 | 1.0575 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201714 | 15S | Proposed | P0 | 11 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201715 | 15S | Proposed | P0 | 11 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201716 | 15S | Proposed | P0 | 11 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201717 | 15S | Proposed | P1 | 11 | 2WEIRGAT | VL |  |  |  |  | 0.9121 | 0.9234 | 0.92 | 1.05 | 25 | G-334282-1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201718 | 15S | Proposed | P1 | 11 | 3GILBERT | VH |  |  |  |  | 1.058 | 1.0251 | 0.92 | 1.05 | 343 | P1_2-116 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201719 | 15S | Proposed | P1 | 11 | 3NATCHEZSES% | VH |  |  |  |  | 1.0577 | 1.0297 | 0.92 | 1.05 | 343 | P1_2-116 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201720 | 15S | Proposed | P1 | 11 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0571 | 1.0294 | 0.92 | 1.05 | 343 | P1_2-116 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201721 | 15S | Proposed | P1 | 11 | 3PINE RIDGE | VH |  |  |  |  | 1.0568 | 1.0291 | 0.92 | 1.05 | 343 | P1_2-116 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201722 | 15S | Proposed | P1 | 11 | 3NATCHEZ! | VH |  |  |  |  | 1.0564 | 1.0292 | 0.92 | 1.05 | 343 | P1_2-116 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201723 | 15S | Proposed | P1 | 11 | 3J.MANVILLE | VH |  |  |  |  | 1.0541 | 1.0269 | 0.92 | 1.05 | 343 | P1_2-116 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201724 | 15S | Proposed | P1 | 11 | 3INTL PAPER | VH |  |  |  |  | 1.053 | 1.0263 | 0.92 | 1.05 | 343 | P1_2-116 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201725 | 15S | Proposed | P1 | 11 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0523 | 1.0259 | 0.92 | 1.05 | 343 | P1_2-116 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201726 | 15S | Proposed | P1 | 11 | 3NATCHEZ IND | VH |  |  |  |  | 1.0508 | 1.025 | 0.92 | 1.05 | 343 | P1_2-116 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201727 | 15S | Proposed | P1 | 11 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0503 | 1.0253 | 0.92 | 1.05 | 343 | P1_2-116 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201728 | 15S | Proposed | P1 | 11 | 3WASHINGTON+ | VH |  |  |  |  | 1.0526 | 1.0261 | 0.92 | 1.05 | 343 | P1_2-116 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201729 | 15S | Proposed | P1 | 11 | 3FAYETTE | VH |  |  |  |  | 1.0523 | 1.0285 | 0.92 | 1.05 | 343 | P1_2-116 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201730 | 15S | Proposed | P1 | 11 | 3RED_GUM! | VH |  |  |  |  | 1.0661 | 1.0281 | 0.92 | 1.05 | 343 | P1_2-116 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201731 | 15S | Proposed | P1 | 11 | 3METROPOLIS | VH |  |  |  |  | 1.0663 | 1.032 | 0.92 | 1.05 | 343 | P1_2-116 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201732 | 15S | Proposed | P1 | 11 | 3WISNER | VH |  |  |  |  | 1.0666 | 1.0325 | 0.92 | 1.05 | 343 | P1_2-116 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
201733 | 15S | Proposed | P1 | 11 | 2CALVERT! | VH |  |  |  |  | 1.0528 | 1.0061 | 0.92 | 1.05 | 351 | P1_2-124 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201734 | 15S | Proposed | P1 | 11 | 2SINHERN | VH |  |  |  |  | 1.0637 | 1.0192 | 0.92 | 1.05 | 351 | P1_2-124 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201735 | 15S | Proposed | P1 | 11 | 2HEARNE! | VH |  |  |  |  | 1.0753 | 1.0323 | 0.92 | 1.05 | 351 | P1_2-124 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201736 | 15S | Proposed | P1 | 11 | 2TXHEARN | VH |  |  |  |  | 1.0738 | 1.0322 | 0.92 | 1.05 | 351 | P1_2-124 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201737 | 15S | Proposed | P1 | 11 | 2APLHERN | VH |  |  |  |  | 1.07 | 1.032 | 0.92 | 1.05 | 351 | P1_2-124 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
201738 | 15S | Proposed | P1 | 11 | 2HEARNE! | VH |  |  |  |  | 1.0525 | 1.0323 | 0.92 | 1.05 | 354 | P1_2-127 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-127 |  |  | VH
201739 | 15S | Proposed | P1 | 11 | 2TXHEARN | VH |  |  |  |  | 1.0516 | 1.0322 | 0.92 | 1.05 | 354 | P1_2-127 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-127 |  |  | VH
201740 | 15S | Proposed | P1 | 11 | 2HUMBHRN | VH |  |  |  |  | 1.0516 | 1.0319 | 0.92 | 1.05 | 354 | P1_2-127 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-127 |  |  | VH
201741 | 15S | Proposed | P1 | 11 | 4STOWELL! | VH |  |  |  |  | 1.0552 | 1.0184 | 0.92 | 1.05 | 440 | P1_2-213 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-213 |  |  | VH
201742 | 15S | Proposed | P1 | 11 | 2HIMEX | VH |  |  |  |  | 1.0665 | 1.0276 | 0.92 | 1.05 | 440 | P1_2-213 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-213 |  |  | VH
201743 | 15S | Proposed | P1 | 11 | 2HIMEX | VH |  |  |  |  | 1.0515 | 1.0276 | 0.92 | 1.05 | 450 | P1_2-223 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
201744 | 15S | Proposed | P1 | 11 | 2PINELND | VL |  |  |  |  | 0.898 | 0.9365 | 0.92 | 1.05 | 458 | P1_2-231 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201745 | 15S | Proposed | P1 | 11 | 2TEMPL1* | VL |  |  |  |  | 0.8961 | 0.9347 | 0.92 | 1.05 | 458 | P1_2-231 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201746 | 15S | Proposed | P1 | 11 | 2TEMPLE1 | VL |  |  |  |  | 0.8957 | 0.9344 | 0.92 | 1.05 | 458 | P1_2-231 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201747 | 15S | Proposed | P1 | 11 | 2TEMPL2* | VL |  |  |  |  | 0.8958 | 0.9344 | 0.92 | 1.05 | 458 | P1_2-231 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201748 | 15S | Proposed | P1 | 11 | 2TEMPLE2 | VL |  |  |  |  | 0.8956 | 0.9342 | 0.92 | 1.05 | 458 | P1_2-231 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201749 | 15S | Proposed | P1 | 11 | 2TMPLSWC | VL |  |  |  |  | 0.8957 | 0.9343 | 0.92 | 1.05 | 458 | P1_2-231 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201750 | 15S | Proposed | P1 | 11 | 2WEIRGAT | VL |  |  |  |  | 0.8843 | 0.9234 | 0.92 | 1.05 | 458 | P1_2-231 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201751 | 15S | Proposed | P1 | 11 | 2PINELND | VL |  |  |  |  | 0.8819 | 0.9365 | 0.92 | 1.05 | 460 | P1_2-233 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201752 | 15S | Proposed | P1 | 11 | 2TEMPL1* | VL |  |  |  |  | 0.88 | 0.9347 | 0.92 | 1.05 | 460 | P1_2-233 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201753 | 15S | Proposed | P1 | 11 | 2TEMPLE1 | VL |  |  |  |  | 0.8796 | 0.9344 | 0.92 | 1.05 | 460 | P1_2-233 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201754 | 15S | Proposed | P1 | 11 | 2TEMPL2* | VL |  |  |  |  | 0.8797 | 0.9344 | 0.92 | 1.05 | 460 | P1_2-233 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201755 | 15S | Proposed | P1 | 11 | 2TEMPLE2 | VL |  |  |  |  | 0.8795 | 0.9342 | 0.92 | 1.05 | 460 | P1_2-233 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201756 | 15S | Proposed | P1 | 11 | 2TMPLSWC | VL |  |  |  |  | 0.8796 | 0.9343 | 0.92 | 1.05 | 460 | P1_2-233 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201757 | 15S | Proposed | P1 | 11 | 2WEIRGAT | VL |  |  |  |  | 0.868 | 0.9234 | 0.92 | 1.05 | 460 | P1_2-233 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201758 | 15S | Proposed | P1 | 11 | 3MCCALL! | VH |  |  |  |  | 1.0517 | 1.0205 | 0.92 | 1.05 | 1014 | P1_2-788 | 336016 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-788 |  |  | VH
201759 | 15S | Proposed | P1 | 11 | 3PVILLE! | VH |  |  |  |  | 1.0544 | 1.0163 | 0.92 | 1.05 | 1014 | P1_2-788 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-788 |  |  | VH
201760 | 15S | Proposed | P1 | 11 | 3ASHLAND | VH |  |  |  |  | 1.0874 | 1.0052 | 0.92 | 1.05 | 1023 | P1_2-797 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-797 |  |  | VH
201761 | 15S | Proposed | P1 | 11 | 3HOUMA! | VH |  |  |  |  | 1.0974 | 1.0095 | 0.92 | 1.05 | 1023 | P1_2-797 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-797 |  |  | VH
201762 | 15S | Proposed | P1 | 11 | 3CHAVIN! | VH |  |  |  |  | 1.0713 | 1.0025 | 0.92 | 1.05 | 1023 | P1_2-797 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-797 |  |  | VH
201763 | 15S | Proposed | P1 | 11 | HOUMA 3 | VH |  |  |  |  | 1.0974 | 1.0095 | 0.92 | 1.05 | 1023 | P1_2-797 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-797 |  |  | VH
201764 | 15S | Proposed | P1 | 11 | 3GMEADW! | VH |  |  |  |  | 1.1637 | 1.0165 | 0.92 | 1.05 | 1028 | P1_2-802 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201765 | 15S | Proposed | P1 | 11 | 3LEEVLL | VH |  |  |  |  | 1.186 | 1.0075 | 0.92 | 1.05 | 1028 | P1_2-802 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201766 | 15S | Proposed | P1 | 11 | 3FOURCHN | VH |  |  |  |  | 1.1858 | 0.9982 | 0.92 | 1.05 | 1028 | P1_2-802 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
201767 | 15S | Proposed | P1 | 11 | 8GGNS% | VL |  |  |  |  | 0.9794 | 1.0157 | 0.982 | 1.05 | 1254 | P1_2-1028 | 336820 |  |  |  | 500 | 500 | 326 | EES-EMI |  |  | P1_2-1028_8GGNS%,8BXTRWILSON% |  | None
201768 | 15S | Proposed | P1 | 11 | 3GILBERT | VH |  |  |  |  | 1.1049 | 1.0251 | 0.92 | 1.05 | 1399 | P1_2-1173 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | VH
201769 | 15S | Proposed | P1 | 11 | 3RED_GUM! | VH |  |  |  |  | 1.053 | 1.0281 | 0.92 | 1.05 | 1399 | P1_2-1173 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | VH
201770 | 15S | Proposed | P1 | 11 | 3METROPOLIS | VH |  |  |  |  | 1.0992 | 1.032 | 0.92 | 1.05 | 1399 | P1_2-1173 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | VH
201771 | 15S | Proposed | P1 | 11 | 3WISNER | VH |  |  |  |  | 1.1029 | 1.0325 | 0.92 | 1.05 | 1399 | P1_2-1173 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | VH
201772 | 15S | Proposed | P1 | 11 | 3WINNSBORO! | VH |  |  |  |  | 1.112 | 1.0141 | 0.92 | 1.05 | 1399 | P1_2-1173 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! |  |  | VH
201773 | 15S | Proposed | P1 | 11 | 3JNCTN CITY! | VH |  |  |  |  | 1.0625 | 1.0256 | 0.92 | 1.05 | 1498 | P1_2-1272 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1272 |  |  | VH
201774 | 15S | Proposed | P1 | 11 | 3MT PINE.S% | VL |  |  |  |  | 0.8517 | 0.9938 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201775 | 15S | Proposed | P1 | 11 | 3ROYAL | VL |  |  |  |  | 0.8617 | 0.9913 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201776 | 15S | Proposed | P1 | 11 | 3MILTON | VL |  |  |  |  | 0.8855 | 0.9886 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201777 | 15S | Proposed | P1 | 11 | 3HS.W | VL |  |  |  |  | 0.8398 | 0.9904 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201778 | 15S | Proposed | P1 | 11 | 3HS.S | VL |  |  |  |  | 0.8329 | 0.9899 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201779 | 15S | Proposed | P1 | 11 | 3ALBRIGHT | VL |  |  |  |  | 0.9162 | 0.9894 | 0.92 | 1.05 | 1561 | P1_2-1336 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336 |  |  | Contingency: invalid after Albright
201780 | 15S | Proposed | P1 | 11 | 3STUTGART.N+ | VL |  |  |  |  | 0.9185 | 1.0132 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201781 | 15S | Proposed | P1 | 11 | 3STUTGART.N | VL |  |  |  |  | 0.9164 | 1.0113 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201782 | 15S | Proposed | P1 | 11 | 3RICUSKEY! | VL |  |  |  |  | 0.9179 | 1.0179 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201783 | 15S | Proposed | P1 | 11 | 3STUTGART IN | VL |  |  |  |  | 0.917 | 1.012 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201784 | 15S | Proposed | P1 | 11 | 3ALMYRA | VL |  |  |  |  | 0.9128 | 1.0007 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201785 | 15S | Proposed | P1 | 11 | 3DEWITT | VL |  |  |  |  | 0.9122 | 0.9909 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201786 | 15S | Proposed | P1 | 11 | 3GILLETT! | VL |  |  |  |  | 0.9184 | 0.9877 | 0.92 | 1.05 | 1661 | P1_2-1436 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201787 | 15S | Proposed | P1 | 11 | 3DELUCE# | VL |  |  |  |  | 0.9144 | 0.9868 | 0.92 | 1.05 | 1661 | P1_2-1436 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201788 | 15S | Proposed | P1 | 11 | 3ELAINE | VL |  |  |  |  | 0.9105 | 0.9844 | 0.92 | 1.05 | 1668 | P1_2-1443 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201789 | 15S | Proposed | P1 | 11 | 3MARVELL | VL |  |  |  |  | 0.9032 | 0.9846 | 0.92 | 1.05 | 1668 | P1_2-1443 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201790 | 15S | Proposed | P1 | 11 | 3BARTON | VL |  |  |  |  | 0.9006 | 0.9844 | 0.92 | 1.05 | 1668 | P1_2-1443 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201791 | 15S | Proposed | P1 | 11 | 3HELENA.W+ | VL |  |  |  |  | 0.8964 | 0.9841 | 0.92 | 1.05 | 1668 | P1_2-1443 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201792 | 15S | Proposed | P1 | 11 | 3HELENA.C | VL |  |  |  |  | 0.8947 | 0.984 | 0.92 | 1.05 | 1668 | P1_2-1443 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201793 | 15S | Proposed | P1 | 11 | 3HELENA IN#! | VL |  |  |  |  | 0.8944 | 0.9855 | 0.92 | 1.05 | 1668 | P1_2-1443 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201794 | 15S | Proposed | P1 | 11 | 8SANS SOUCI% | VH |  |  |  |  | 1.0547 | 1.037 | 0.92 | 1.05 | 1736 | P1_2-1514 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1514 |  |  | VH
201795 | 15S | Proposed | P1 | 11 | 8DANIEL | VH |  |  |  |  | 1.0741 | 1.0443 | 0.92 | 1.05 | 1821 | P1_2-1599 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1599 |  |  | VH
201796 | 15S | Proposed | P1 | 11 | 4CANEY | VL |  |  |  |  | 0.8758 | 0.9956 | 0.92 | 1.05 | 1870 | P1_2-1648 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648
201797 | 15S | Proposed | P1 | 11 | OAKDALE4 | VL |  |  |  |  | 0.8777 | 0.9939 | 0.92 | 1.05 | 1870 | P1_2-1648 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
201798 | 15S | Proposed | P1 | 11 | PNPRARIE 4 | VL |  |  |  |  | 0.8686 | 1.0073 | 0.92 | 1.05 | 1870 | P1_2-1648 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
201799 | 15S | Proposed | P1 | 11 | WSTBAY 4 | VL |  |  |  |  | 0.8894 | 0.9929 | 0.92 | 1.05 | 1870 | P1_2-1648 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648
201800 | 15S | Proposed | P1 | 11 | 4VEAZIE | VL |  |  |  |  | 0.8949 | 0.979 | 0.92 | 1.05 | 1871 | P1_2-1649 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201801 | 15S | Proposed | P1 | 11 | GUIDRY 4 | VL |  |  |  |  | 0.8935 | 0.9778 | 0.92 | 1.05 | 1871 | P1_2-1649 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201802 | 15S | Proposed | P1 | 11 | PLAISAN4 | VL |  |  |  |  | 0.9085 | 0.9914 | 0.92 | 1.05 | 1871 | P1_2-1649 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201803 | 15S | Proposed | P1 | 11 | TENRUSK7 | VH |  |  |  |  | 1.0525 | 1.0189 | 0.92 | 1.05 | 2080 | P1_2-1858 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1858 |  |  | VH
201804 | 15S | Proposed | P1 | 11 | TENGEN 7 | VH |  |  |  |  | 1.0525 | 1.0189 | 0.92 | 1.05 | 2080 | P1_2-1858 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1858 |  |  | VH
201805 | 15S | Proposed | P0 | 12 | 5HORN LAKE% | VH |  |  |  |  | 1.0575 | 1.0575 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201806 | 15S | Proposed | P0 | 12 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201807 | 15S | Proposed | P0 | 12 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201808 | 15S | Proposed | P0 | 12 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201809 | 15S | Proposed | P1 | 12 | 3JNCTN CITY! | VH |  |  |  |  | 1.0621 | 1.0256 | 0.92 | 1.05 | 50 | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 |  |  | VH
201810 | 15S | Proposed | P1 | 12 | 3STUTGART.N+ | VL |  |  |  |  | 0.9185 | 1.0132 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201811 | 15S | Proposed | P1 | 12 | 3STUTGART.N | VL |  |  |  |  | 0.9164 | 1.0113 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201812 | 15S | Proposed | P1 | 12 | 3RICUSKEY! | VL |  |  |  |  | 0.9179 | 1.0179 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201813 | 15S | Proposed | P1 | 12 | 3STUTGART IN | VL |  |  |  |  | 0.917 | 1.012 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201814 | 15S | Proposed | P1 | 12 | 3ALMYRA | VL |  |  |  |  | 0.9128 | 1.0007 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201815 | 15S | Proposed | P1 | 12 | 3DEWITT | VL |  |  |  |  | 0.9122 | 0.9909 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201816 | 15S | Proposed | P1 | 12 | 3GILLETT! | VL |  |  |  |  | 0.9184 | 0.9877 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201817 | 15S | Proposed | P1 | 12 | 3DELUCE# | VL |  |  |  |  | 0.9144 | 0.9868 | 0.92 | 1.05 | 336 | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337968 6RICUSKEY% 230 1 |  | Project Approved |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201818 | 15S | Proposed | P2 | 12 | 3STUTGART IN | VL |  |  |  |  | 0.9058 | 1.012 | 0.92 | 1.05 | 337 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
201819 | 15S | Proposed | P2 | 12 | 3ULM | VL |  |  |  |  | 0.9142 | 1.0096 | 0.92 | 1.05 | 337 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
201820 | 15S | Proposed | P2 | 12 | 3ALMYRA | VL |  |  |  |  | 0.7938 | 1.0007 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201821 | 15S | Proposed | P2 | 12 | 3DEWITT | VL |  |  |  |  | 0.7972 | 0.9909 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201822 | 15S | Proposed | P2 | 12 | 3GILLETT! | VL |  |  |  |  | 0.8133 | 0.9877 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201823 | 15S | Proposed | P2 | 12 | 3ELAINE | VL |  |  |  |  | 0.8568 | 0.9844 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201824 | 15S | Proposed | P2 | 12 | 3MARVELL | VL |  |  |  |  | 0.8888 | 0.9846 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201825 | 15S | Proposed | P2 | 12 | 3BARTON | VL |  |  |  |  | 0.9023 | 0.9844 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201826 | 15S | Proposed | P2 | 12 | 2DELUCE | VL |  |  |  |  | 0.8264 | 1.0121 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201827 | 15S | Proposed | P2 | 12 | 3DELUCE# | VL |  |  |  |  | 0.8057 | 0.9868 | 0.92 | 1.05 | 338 | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337972 3ALMYRA 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201828 | 15S | Proposed | P1 | 12 | 3DEWITT | VL |  |  |  |  | 0.9181 | 0.9909 | 0.92 | 1.05 | 343 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201829 | 15S | Proposed | P1 | 12 | 3MARVELL | VL |  |  |  |  | 0.9197 | 0.9846 | 0.92 | 1.05 | 351 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201830 | 15S | Proposed | P1 | 12 | 3BARTON | VL |  |  |  |  | 0.9175 | 0.9844 | 0.92 | 1.05 | 351 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201831 | 15S | Proposed | P1 | 12 | 3HELENA.W+ | VL |  |  |  |  | 0.9138 | 0.9841 | 0.92 | 1.05 | 351 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201832 | 15S | Proposed | P1 | 12 | 3HELENA.C | VL |  |  |  |  | 0.9123 | 0.984 | 0.92 | 1.05 | 351 | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337984 3HELENA.C 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201833 | 15S | Proposed | P1 | 12 | 3ELAINE | VL |  |  |  |  | 0.9105 | 0.9844 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201834 | 15S | Proposed | P1 | 12 | 3MARVELL | VL |  |  |  |  | 0.9032 | 0.9846 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201835 | 15S | Proposed | P1 | 12 | 3BARTON | VL |  |  |  |  | 0.9006 | 0.9844 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201836 | 15S | Proposed | P1 | 12 | 3HELENA.W+ | VL |  |  |  |  | 0.8964 | 0.9841 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201837 | 15S | Proposed | P1 | 12 | 3HELENA.C | VL |  |  |  |  | 0.8947 | 0.984 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201838 | 15S | Proposed | P1 | 12 | 3HELENA IN#! | VL |  |  |  |  | 0.8944 | 0.9855 | 0.92 | 1.05 | 354 | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337986 3RITCHIE! 115 338880 3HELENA IN#! 115 1 |  | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
201839 | 15S | Proposed | P1 | 12 | 2HARRISON.S | VH |  |  |  |  | 1.0562 | 1.0407 | 0.92 | 1.05 | 416 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
201840 | 15S | Proposed | P1 | 12 | 8SANS SOUCI% | VH |  |  |  |  | 1.0547 | 1.037 | 0.92 | 1.05 | 488 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
201841 | 15S | Proposed | P1 | 12 | 5POCHNTAS.N | VL |  |  |  |  | 0.8795 | 0.9981 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201842 | 15S | Proposed | P1 | 12 | 5DATTO | VL |  |  |  |  | 0.8728 | 0.9892 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201843 | 15S | Proposed | P1 | 12 | 3DATTO | VL |  |  |  |  | 0.893 | 1.0121 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201844 | 15S | Proposed | P1 | 12 | 3CORNING | VL |  |  |  |  | 0.8872 | 1.0022 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201845 | 15S | Proposed | P1 | 12 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8791 | 0.9976 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201846 | 15S | Proposed | P1 | 12 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8791 | 0.9973 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201847 | 15S | Proposed | P1 | 12 | 3CORNING.N# | VL |  |  |  |  | 0.8877 | 1.0033 | 0.92 | 1.05 | 522 | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 338690 5POCHNTAS.W# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201848 | 15S | Proposed | P1 | 12 | 5DATTO | VL |  |  |  |  | 0.8909 | 0.9892 | 0.92 | 1.05 | 523 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201849 | 15S | Proposed | P1 | 12 | 3DATTO | VL |  |  |  |  | 0.9181 | 1.0121 | 0.92 | 1.05 | 523 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201850 | 15S | Proposed | P1 | 12 | 5POCHNTAS.E# | VL |  |  |  |  | 0.889 | 0.9976 | 0.92 | 1.05 | 523 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201851 | 15S | Proposed | P1 | 12 | 3CORNING.N# | VL |  |  |  |  | 0.9198 | 1.0033 | 0.92 | 1.05 | 523 | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338225 5POCHNTAS.N 161 338688 5POCHNTAS.E# 161 1 |  | Project Horizon | Contingency: invalid, no breakers | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201852 | 15S | Proposed | P1 | 12 | 2IMBODEN! | VL |  |  |  |  | 0.8825 | 0.998 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338221 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201853 | 15S | Proposed | P1 | 12 | 2WTR VALLEY! | VL |  |  |  |  | 0.8822 | 0.9977 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338222 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201854 | 15S | Proposed | P1 | 12 | 5WTR VALLEY+ | VL |  |  |  |  | 0.8818 | 0.9972 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338223 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201855 | 15S | Proposed | P1 | 12 | 5WTR VALLEY | VL |  |  |  |  | 0.8818 | 0.9972 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338224 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201856 | 15S | Proposed | P1 | 12 | 5POCHNTAS.N | VL |  |  |  |  | 0.8822 | 0.9981 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338225 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201857 | 15S | Proposed | P1 | 12 | 5DATTO | VL |  |  |  |  | 0.8751 | 0.9892 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338226 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201858 | 15S | Proposed | P1 | 12 | 3DATTO | VL |  |  |  |  | 0.8952 | 1.0121 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201859 | 15S | Proposed | P1 | 12 | 3CORNING | VL |  |  |  |  | 0.8891 | 1.0022 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201860 | 15S | Proposed | P1 | 12 | 5POCHNTAS.E# | VL |  |  |  |  | 0.8817 | 0.9976 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338688 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201861 | 15S | Proposed | P1 | 12 | 5POCHNTAS.W# | VL |  |  |  |  | 0.8818 | 0.9973 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338690 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201862 | 15S | Proposed | P1 | 12 | 3CORNING.N# | VL |  |  |  |  | 0.8896 | 1.0033 | 0.92 | 1.05 | 682 | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338223 5WTR VALLEY+ 161 505442 WATER V5 161 1 |  | Project Horizon |  | 11-EAI-015-HZ | 2020-06-01 | Construct Doniphan-Datto 161 kV (Jim Hill Area Upgrades)
201863 | 15S | Proposed | P1 | 12 | 2CALVERT! | VH |  |  |  |  | 1.0532 | 1.0061 | 0.92 | 1.05 | 693 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
201864 | 15S | Proposed | P1 | 12 | 2SINHERN | VH |  |  |  |  | 1.0641 | 1.0192 | 0.92 | 1.05 | 693 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
201865 | 15S | Proposed | P1 | 12 | 2HEARNE! | VH |  |  |  |  | 1.0757 | 1.0323 | 0.92 | 1.05 | 693 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
201866 | 15S | Proposed | P1 | 12 | 2TXHEARN | VH |  |  |  |  | 1.0742 | 1.0322 | 0.92 | 1.05 | 693 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
201867 | 15S | Proposed | P1 | 12 | 2APLHERN | VH |  |  |  |  | 1.0703 | 1.032 | 0.92 | 1.05 | 693 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
201868 | 15S | Proposed | P1 | 12 | 2CALVERT! | VH |  |  |  |  | 1.0536 | 1.0061 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201869 | 15S | Proposed | P1 | 12 | 2SINHERN | VH |  |  |  |  | 1.0644 | 1.0192 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201870 | 15S | Proposed | P1 | 12 | 2HEARNE! | VH |  |  |  |  | 1.076 | 1.0323 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201871 | 15S | Proposed | P1 | 12 | 2TXHEARN | VH |  |  |  |  | 1.0745 | 1.0322 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201872 | 15S | Proposed | P1 | 12 | 2APLHERN | VH |  |  |  |  | 1.0706 | 1.032 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201873 | 15S | Proposed | P1 | 12 | 2HUMBHRN | VH |  |  |  |  | 1.076 | 1.0319 | 0.92 | 1.05 | 697 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
201874 | 15S | Proposed | P1 | 12 | 2CALVERT! | VH |  |  |  |  | 1.0559 | 1.0061 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201875 | 15S | Proposed | P1 | 12 | 2SINHERN | VH |  |  |  |  | 1.0666 | 1.0192 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201876 | 15S | Proposed | P1 | 12 | 2HEARNE! | VH |  |  |  |  | 1.0781 | 1.0323 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201877 | 15S | Proposed | P1 | 12 | 2TXHEARN | VH |  |  |  |  | 1.0765 | 1.0322 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201878 | 15S | Proposed | P1 | 12 | 2APLHERN | VH |  |  |  |  | 1.0724 | 1.032 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201879 | 15S | Proposed | P1 | 12 | 2HUMBHRN | VH |  |  |  |  | 1.0781 | 1.0319 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201880 | 15S | Proposed | P1 | 12 | 2TESCO | VH |  |  |  |  | 1.0783 | 1.0305 | 0.92 | 1.05 | 698 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334007 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
201881 | 15S | Proposed | P1 | 12 | 2HEARNE! | VH |  |  |  |  | 1.0525 | 1.0323 | 0.92 | 1.05 | 700 | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201882 | 15S | Proposed | P1 | 12 | 2TXHEARN | VH |  |  |  |  | 1.0516 | 1.0322 | 0.92 | 1.05 | 700 | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201883 | 15S | Proposed | P1 | 12 | 2HUMBHRN | VH |  |  |  |  | 1.0516 | 1.0319 | 0.92 | 1.05 | 700 | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334008 2BRYAN B! 69.0 334020 4BRYAN! 138 1 |  |  | VH
201884 | 15S | Proposed | P1 | 12 | 4MAGROVE | VH |  |  |  |  | 1.0933 | 1.0172 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201885 | 15S | Proposed | P1 | 12 | 4L111T411 | VH |  |  |  |  | 1.0821 | 1.0147 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201886 | 15S | Proposed | P1 | 12 | 4KICKAPO | VH |  |  |  |  | 1.0819 | 1.0145 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201887 | 15S | Proposed | P1 | 12 | 4CORIGAN! | VH |  |  |  |  | 1.0713 | 1.014 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201888 | 15S | Proposed | P1 | 12 | 4SHECORR | VH |  |  |  |  | 1.0698 | 1.0135 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201889 | 15S | Proposed | P1 | 12 | 4CAMDEN | VH |  |  |  |  | 1.0633 | 1.0118 | 0.92 | 1.05 | 803 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
201890 | 15S | Proposed | P1 | 12 | 4CROKBYU | VH |  |  |  |  | 1.0534 | 1.0086 | 0.92 | 1.05 | 857 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334223 |  |  |  | 138 | 138 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
201891 | 15S | Proposed | P1 | 12 | 4TEPPCO | VH |  |  |  |  | 1.0534 | 1.0085 | 0.92 | 1.05 | 857 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334224 |  |  |  | 138 | 138 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
201892 | 15S | Proposed | P1 | 12 | 4STOWELL! | VH |  |  |  |  | 1.054 | 1.0184 | 0.92 | 1.05 | 857 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
201893 | 15S | Proposed | P1 | 12 | 2HIMEX | VH |  |  |  |  | 1.0651 | 1.0276 | 0.92 | 1.05 | 857 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
201894 | 15S | Proposed | P1 | 12 | 4STOWELL! | VH |  |  |  |  | 1.055 | 1.0184 | 0.92 | 1.05 | 859 | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 | 334225 |  |  |  | 138 | 138 | 351 | EES |  |  | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 |  |  | VH
201895 | 15S | Proposed | P1 | 12 | 2HIMEX | VH |  |  |  |  | 1.0663 | 1.0276 | 0.92 | 1.05 | 859 | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 |  |  | VH
201896 | 15S | Proposed | P1 | 12 | 2HIMEX | VH |  |  |  |  | 1.0515 | 1.0276 | 0.92 | 1.05 | 869 | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 |  |  | VH
201897 | 15S | Proposed | P1 | 12 | 2PINELND | VL |  |  |  |  | 0.898 | 0.9365 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201898 | 15S | Proposed | P1 | 12 | 2TEMPL1* | VL |  |  |  |  | 0.8961 | 0.9347 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201899 | 15S | Proposed | P1 | 12 | 2TEMPLE1 | VL |  |  |  |  | 0.8957 | 0.9344 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201900 | 15S | Proposed | P1 | 12 | 2TEMPL2* | VL |  |  |  |  | 0.8958 | 0.9344 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201901 | 15S | Proposed | P1 | 12 | 2TEMPLE2 | VL |  |  |  |  | 0.8956 | 0.9342 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201902 | 15S | Proposed | P1 | 12 | 2TMPLSWC | VL |  |  |  |  | 0.8957 | 0.9343 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201903 | 15S | Proposed | P1 | 12 | 2WEIRGAT | VL |  |  |  |  | 0.8843 | 0.9234 | 0.92 | 1.05 | 892 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201904 | 15S | Proposed | P1 | 12 | 2PINELND | VL |  |  |  |  | 0.8819 | 0.9365 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201905 | 15S | Proposed | P1 | 12 | 2TEMPL1* | VL |  |  |  |  | 0.88 | 0.9347 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201906 | 15S | Proposed | P1 | 12 | 2TEMPLE1 | VL |  |  |  |  | 0.8796 | 0.9344 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201907 | 15S | Proposed | P1 | 12 | 2TEMPL2* | VL |  |  |  |  | 0.8797 | 0.9344 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201908 | 15S | Proposed | P1 | 12 | 2TEMPLE2 | VL |  |  |  |  | 0.8795 | 0.9342 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201909 | 15S | Proposed | P1 | 12 | 2TMPLSWC | VL |  |  |  |  | 0.8796 | 0.9343 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201910 | 15S | Proposed | P1 | 12 | 2WEIRGAT | VL |  |  |  |  | 0.868 | 0.9234 | 0.92 | 1.05 | 894 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201911 | 15S | Proposed | P1 | 12 | 2PINELND | VL |  |  |  |  | 0.9027 | 0.9365 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201912 | 15S | Proposed | P1 | 12 | 2TEMPL1* | VL |  |  |  |  | 0.9008 | 0.9347 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201913 | 15S | Proposed | P1 | 12 | 2TEMPLE1 | VL |  |  |  |  | 0.9005 | 0.9344 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201914 | 15S | Proposed | P1 | 12 | 2TEMPL2* | VL |  |  |  |  | 0.9005 | 0.9344 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201915 | 15S | Proposed | P1 | 12 | 2TEMPLE2 | VL |  |  |  |  | 0.9004 | 0.9342 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201916 | 15S | Proposed | P1 | 12 | 2TMPLSWC | VL |  |  |  |  | 0.9004 | 0.9343 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201917 | 15S | Proposed | P1 | 12 | 2WEIRGAT | VL |  |  |  |  | 0.8892 | 0.9234 | 0.92 | 1.05 | 897 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201918 | 15S | Proposed | P1 | 12 | 4LEBLANC! | VL |  |  |  |  | 0.9195 | 0.9712 | 0.92 | 1.05 | 1394 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201918 | 15S | Proposed | P1 | 12 | 4LEBLANC! | VL |  |  |  |  | 0.9195 | 0.9712 | 0.92 | 1.05 | 1394 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201919 | 15S | Proposed | P1 | 12 | 4DELCAMBRE | VL |  |  |  |  | 0.919 | 0.9757 | 0.92 | 1.05 | 1394 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
201919 | 15S | Proposed | P1 | 12 | 4DELCAMBRE | VL |  |  |  |  | 0.919 | 0.9757 | 0.92 | 1.05 | 1394 | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 | 335387 |  |  |  | 138 | 138 | 351 | EES |  |  | 335387 4DELCAMBRE 138 335388 4MORIL! 138 1 |  | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
201920 | 15S | Proposed | P1 | 12 | 2ST_MARTIN | VL |  |  |  |  | 0.9198 | 0.986 | 0.92 | 1.05 | 1411 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
201921 | 15S | Proposed | P1 | 12 | LONGFL 2 | VL |  |  |  |  | 0.9198 | 0.986 | 0.92 | 1.05 | 1411 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1
201922 | 15S | Proposed | P1 | 12 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9124 | 0.9634 | 0.92 | 1.05 | 1438 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201923 | 15S | Proposed | P1 | 12 | 4BOBCAT | VL |  |  |  |  | 0.9088 | 0.9709 | 0.92 | 1.05 | 1438 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201924 | 15S | Proposed | P1 | 12 | 4LINE-642_TP | VL |  |  |  |  | 0.9125 | 0.9635 | 0.92 | 1.05 | 1438 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201925 | 15S | Proposed | P1 | 12 | 4COL_SPRINGS | VL |  |  |  |  | 0.9124 | 0.9634 | 0.92 | 1.05 | 1438 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
201926 | 15S | Proposed | P1 | 12 | 2NESSER_TP | VL |  |  |  |  | 0.8857 | 0.9718 | 0.92 | 1.05 | 1576 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201927 | 15S | Proposed | P1 | 12 | 2NESSER | VL |  |  |  |  | 0.8808 | 0.9674 | 0.92 | 1.05 | 1576 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201928 | 15S | Proposed | P1 | 12 | 2LN-372A_TP | VL |  |  |  |  | 0.9007 | 0.9853 | 0.92 | 1.05 | 1576 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335710 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201929 | 15S | Proposed | P1 | 12 | 2JONESCREEK! | VL |  |  |  |  | 0.904 | 0.9823 | 0.92 | 1.05 | 1576 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
201930 | 15S | Proposed | P1 | 12 | 2ANGOLA | VL |  |  |  |  | 0.8913 | 0.9914 | 0.92 | 1.05 | 1648 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  | None
201931 | 15S | Proposed | P1 | 12 | 3MCCALL! | VH |  |  |  |  | 1.0517 | 1.0205 | 0.92 | 1.05 | 1684 | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 | 336016 |  |  |  | 115 | 115 | 351 | EES |  |  | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 |  |  | VH
201932 | 15S | Proposed | P1 | 12 | 3PVILLE! | VH |  |  |  |  | 1.0544 | 1.0163 | 0.92 | 1.05 | 1684 | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 |  |  | VH
201933 | 15S | Proposed | P1 | 12 | 3ASHLAND | VH |  |  |  |  | 1.0874 | 1.0052 | 0.92 | 1.05 | 1694 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201934 | 15S | Proposed | P1 | 12 | 3HOUMA! | VH |  |  |  |  | 1.0974 | 1.0095 | 0.92 | 1.05 | 1694 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201935 | 15S | Proposed | P1 | 12 | 3CHAVIN! | VH |  |  |  |  | 1.0713 | 1.0025 | 0.92 | 1.05 | 1694 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201936 | 15S | Proposed | P1 | 12 | HOUMA 3 | VH |  |  |  |  | 1.0974 | 1.0095 | 0.92 | 1.05 | 1694 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
201937 | 15S | Proposed | P1 | 12 | 3GMEADW! | VH |  |  |  |  | 1.1638 | 1.0165 | 0.92 | 1.05 | 1723 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201938 | 15S | Proposed | P1 | 12 | 3LEEVLL | VH |  |  |  |  | 1.186 | 1.0075 | 0.92 | 1.05 | 1723 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201939 | 15S | Proposed | P1 | 12 | 3FOURCHN | VH |  |  |  |  | 1.1859 | 0.9982 | 0.92 | 1.05 | 1723 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
201940 | 15S | Proposed | P1 | 12 | 3CARLSL | VL |  |  |  |  | 0.8883 | 0.9847 | 0.92 | 1.05 | 1733 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
201941 | 15S | Proposed | P1 | 12 | 3NATCHEZSES% | VH |  |  |  |  | 1.0675 | 1.0297 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201942 | 15S | Proposed | P1 | 12 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0666 | 1.0294 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201943 | 15S | Proposed | P1 | 12 | 3PINE RIDGE | VH |  |  |  |  | 1.0662 | 1.0291 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201944 | 15S | Proposed | P1 | 12 | 3NATCHEZ! | VH |  |  |  |  | 1.0645 | 1.0292 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201945 | 15S | Proposed | P1 | 12 | 3J.MANVILLE | VH |  |  |  |  | 1.0617 | 1.0269 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201946 | 15S | Proposed | P1 | 12 | 3INTL PAPER | VH |  |  |  |  | 1.0602 | 1.0263 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201947 | 15S | Proposed | P1 | 12 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0592 | 1.0259 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201948 | 15S | Proposed | P1 | 12 | 3NATCHEZ IND | VH |  |  |  |  | 1.057 | 1.025 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201949 | 15S | Proposed | P1 | 12 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0576 | 1.0253 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201950 | 15S | Proposed | P1 | 12 | 3KINGSTON MS | VH |  |  |  |  | 1.0553 | 1.023 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201951 | 15S | Proposed | P1 | 12 | 3WASHINGTON+ | VH |  |  |  |  | 1.0589 | 1.0261 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201952 | 15S | Proposed | P1 | 12 | 3CRANFIELD+ | VH |  |  |  |  | 1.0501 | 1.0231 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201953 | 15S | Proposed | P1 | 12 | 3FAYETTE | VH |  |  |  |  | 1.1052 | 1.0285 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201954 | 15S | Proposed | P1 | 12 | 3LORMAN+ | VH |  |  |  |  | 1.1195 | 1.0188 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201955 | 15S | Proposed | P1 | 12 | 3LORMAN | VH |  |  |  |  | 1.1193 | 1.0186 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201956 | 15S | Proposed | P1 | 12 | 3PORTGIBSON! | VH |  |  |  |  | 1.1369 | 1.0177 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201957 | 15S | Proposed | P1 | 12 | 3GGNS | VH |  |  |  |  | 1.1359 | 1.0166 | 0.975 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201958 | 15S | Proposed | P1 | 12 | 3S.VICKSBURG | VH |  |  |  |  | 1.1648 | 1.0193 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201959 | 15S | Proposed | P1 | 12 | 3RED_GUM! | VH |  |  |  |  | 1.0528 | 1.0281 | 0.92 | 1.05 | 1957 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
201961 | 15S | Proposed | P1 | 12 | 3GILBERT | VH |  |  |  |  | 1.0591 | 1.0251 | 0.92 | 1.05 | 2245 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | VH
201962 | 15S | Proposed | P1 | 12 | 3WISNER | VH |  |  |  |  | 1.0684 | 1.0325 | 0.92 | 1.05 | 2245 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | VH
201963 | 15S | Proposed | P1 | 12 | 3LUCKY | VH |  |  |  |  | 1.0556 | 1.0234 | 0.92 | 1.05 | 2257 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 |  |  | VH
201964 | 15S | Proposed | P1 | 12 | 2WEIRGAT | VL |  |  |  |  | 0.9121 | 0.9234 | 0.92 | 1.05 | 2330 | Unit:334282 4RAYBURN% 138 Id:1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
201965 | 15S | Proposed | P1 | 12 | 3NATCHEZSES% | VH |  |  |  |  | 1.0515 | 1.0297 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
201966 | 15S | Proposed | P1 | 12 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0511 | 1.0294 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
201967 | 15S | Proposed | P1 | 12 | 3PINE RIDGE | VH |  |  |  |  | 1.0508 | 1.0291 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
201968 | 15S | Proposed | P1 | 12 | 3NATCHEZ! | VH |  |  |  |  | 1.0508 | 1.0292 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
201969 | 15S | Proposed | P1 | 12 | 3RED_GUM! | VH |  |  |  |  | 1.0591 | 1.0281 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
201970 | 15S | Proposed | P1 | 12 | 3METROPOLIS | VH |  |  |  |  | 1.1006 | 1.032 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
201971 | 15S | Proposed | P1 | 12 | 3WISNER | VH |  |  |  |  | 1.1036 | 1.0325 | 0.92 | 1.05 | 2473 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
201972 | 15S | Proposed | P1 | 12 | 3GILBERT | VH |  |  |  |  | 1.1084 | 1.0251 | 0.92 | 1.05 | 2478 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201973 | 15S | Proposed | P2 | 12 | 3RED_GUM! | VH |  |  |  |  | 1.0559 | 1.0281 | 0.92 | 1.05 | 2478 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201974 | 15S | Proposed | P2 | 12 | 3METROPOLIS | VH |  |  |  |  | 1.1026 | 1.032 | 0.92 | 1.05 | 2478 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201975 | 15S | Proposed | P2 | 12 | 3WISNER | VH |  |  |  |  | 1.1063 | 1.0325 | 0.92 | 1.05 | 2478 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201976 | 15S | Proposed | P2 | 12 | 3WINNSBORO! | VH |  |  |  |  | 1.1156 | 1.0141 | 0.92 | 1.05 | 2478 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
201977 | 15S | Proposed | P1 | 12 | 4CANEY | VL |  |  |  |  | 0.8758 | 0.9956 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201978 | 15S | Proposed | P1 | 12 | OAKDALE4 | VL |  |  |  |  | 0.8777 | 0.9939 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201979 | 15S | Proposed | P1 | 12 | PNPRARIE 4 | VL |  |  |  |  | 0.8686 | 1.0073 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201980 | 15S | Proposed | P1 | 12 | WSTBAY 4 | VL |  |  |  |  | 0.8894 | 0.9929 | 0.92 | 1.05 | 2654 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
201984 | 15S | Proposed | P1 | 12 | ELKS 6 | VL |  |  |  |  | 0.9189 | 0.9876 | 0.92 | 1.05 | 2747 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  | turn on switch shunt at BEADLE 230kV sub
201985 | 15S | Proposed | P1 | 12 | BEADLE 6 | VL |  |  |  |  | 0.9194 | 0.9887 | 0.92 | 1.05 | 2747 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1
201986 | 15S | Proposed | P1 | 12 | ELKS 6 | VL |  |  |  |  | 0.9033 | 0.9876 | 0.92 | 1.05 | 2771 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
201987 | 15S | Proposed | P1 | 12 | 8MCCALL RD | VH |  |  |  |  | 1.0677 | 1.0372 | 0.92 | 1.05 | 2863 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
201988 | 15S | Proposed | P1 | 12 | 8DANIEL | VH |  |  |  |  | 1.0741 | 1.0443 | 0.92 | 1.05 | 3576 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
201989 | 15S | Proposed | P1 | 12 | 7SHAWNEE FP | VH |  |  |  |  | 1.051 | 1.0386 | 0.92 | 1.05 | 3876 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
201990 | 15S | Proposed | P1 | 12 | TENRUSK7 | VH |  |  |  |  | 1.0525 | 1.0189 | 0.92 | 1.05 | 4554 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201991 | 15S | Proposed | P1 | 12 | TENGEN 7 | VH |  |  |  |  | 1.0525 | 1.0189 | 0.92 | 1.05 | 4554 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
201992 | 15S | Proposed | P0 | 13 | 5HORN LAKE% | VH |  |  |  |  | 1.0575 | 1.0575 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
201993 | 15S | Proposed | P0 | 13 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201994 | 15S | Proposed | P0 | 13 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
201995 | 15S | Proposed | P0 | 13 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
201996 | 15S | Proposed | P1 | 13 | 4NEW_IBERIA! | VL |  |  |  |  | 0.9057 | 0.9926 | 0.92 | 1.05 | 5 | P1_2-562-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-562-a |  |  | Contingency: Trip bus as result of con
201997 | 15S | Proposed | P1 | 13 | 4NEW_IBERIA! | VL |  |  |  |  | 0.9057 | 0.9926 | 0.92 | 1.05 | 6 | P1_2-568-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-568-a |  |  | Contingency: Trip bus as result of con
201998 | 18L | Proposed | P0 | 14 | 8GPDELL | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
201999 | 18L | Proposed | P0 | 14 | 7GOBKNOB | VH |  |  |  |  | 1.0515 | 1.0515 | 0.92 | 1.05 | 0 | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
202000 | 18L | Proposed | P0 | 14 | 2BATSON! | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
202001 | 18L | Proposed | P0 | 14 | 5HORN LAKE% | VH |  |  |  |  | 1.0684 | 1.0684 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202002 | 18L | Proposed | P0 | 14 | 8DELL% | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202003 | 18L | Proposed | P0 | 14 | 8SANS SOUCI% | VH |  |  |  |  | 1.0625 | 1.0625 | 0.92 | 1.05 | 0 | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202004 | 18L | Proposed | P0 | 14 | 3PARAGOULD! | VH |  |  |  |  | 1.061 | 1.061 | 0.92 | 1.05 | 0 | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202005 | 18L | Proposed | P0 | 14 | 3SEDGWICK | VH |  |  |  |  | 1.0506 | 1.0506 | 0.92 | 1.05 | 0 | ** Base Case ** | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202006 | 18L | Proposed | P0 | 14 | 3DATTO | VH |  |  |  |  | 1.0518 | 1.0518 | 0.92 | 1.05 | 0 | ** Base Case ** | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202007 | 18L | Proposed | P0 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0714 | 1.0714 | 0.92 | 1.05 | 0 | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202008 | 18L | Proposed | P0 | 14 | 2OPPELLO | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202009 | 18L | Proposed | P0 | 14 | 2WARD | VH |  |  |  |  | 1.0603 | 1.0603 | 0.92 | 1.05 | 0 | ** Base Case ** | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202010 | 18L | Proposed | P0 | 14 | 5DELL# | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202011 | 18L | Proposed | P0 | 14 | 3LIGHT# | VH |  |  |  |  | 1.0539 | 1.0539 | 0.92 | 1.05 | 0 | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202012 | 18L | Proposed | P0 | 14 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0571 | 1.0571 | 0.92 | 1.05 | 0 | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202013 | 18L | Proposed | P0 | 14 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 | 0 | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202014 | 18L | Proposed | P0 | 14 | 7SHAWNEE FP | VH |  |  |  |  | 1.0766 | 1.0766 | 0.92 | 1.05 | 0 | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202015 | 18L | Proposed | P0 | 14 | 8RUTHERFORD | VH |  |  |  |  | 1.0689 | 1.0689 | 0.92 | 1.05 | 0 | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202016 | 18L | Proposed | P0 | 14 | 8MARSHALL KY | VH |  |  |  |  | 1.0819 | 1.0819 | 0.92 | 1.05 | 0 | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202017 | 18L | Proposed | P0 | 14 | 8WEAKLEY TN | VH |  |  |  |  | 1.0785 | 1.0785 | 0.92 | 1.05 | 0 | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202018 | 18L | Proposed | P0 | 14 | 8JACKSON TN | VH |  |  |  |  | 1.0673 | 1.0673 | 0.92 | 1.05 | 0 | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202019 | 18L | Proposed | P0 | 14 | 8SHELBY TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202020 | 18L | Proposed | P0 | 14 | 8CORDOVA TN | VH |  |  |  |  | 1.0568 | 1.0568 | 0.92 | 1.05 | 0 | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202021 | 18L | Proposed | P0 | 14 | 8UNION MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202022 | 18L | Proposed | P0 | 14 | 8JVILLE FP | VH |  |  |  |  | 1.0829 | 1.0829 | 0.92 | 1.05 | 0 | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202023 | 18L | Proposed | P0 | 14 | 8CUMBERLAND | VH |  |  |  |  | 1.0876 | 1.0876 | 0.92 | 1.05 | 0 | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202024 | 18L | Proposed | P0 | 14 | 8PARADISE FP | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 | 0 | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202025 | 18L | Proposed | P0 | 14 | 8MONTGOMERY | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202026 | 18L | Proposed | P0 | 14 | 8DAVIDSON TN | VH |  |  |  |  | 1.0799 | 1.0799 | 0.92 | 1.05 | 0 | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202027 | 18L | Proposed | P0 | 14 | 8MAURY TN | VH |  |  |  |  | 1.0682 | 1.0682 | 0.92 | 1.05 | 0 | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202028 | 18L | Proposed | P0 | 14 | 8FRANKLIN TN | VH |  |  |  |  | 1.0523 | 1.0523 | 0.92 | 1.05 | 0 | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202029 | 18L | Proposed | P0 | 14 | 8WILSON TN | VH |  |  |  |  | 1.077 | 1.077 | 0.92 | 1.05 | 0 | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202030 | 18L | Proposed | P0 | 14 | 8PLATEAU TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202031 | 18L | Proposed | P0 | 14 | 8BULL RUN FP | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 | 0 | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202032 | 18L | Proposed | P0 | 14 | 8VOLUNTEER | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202033 | 18L | Proposed | P0 | 14 | 8PHIPPS B NP | VH |  |  |  |  | 1.0678 | 1.0678 | 0.92 | 1.05 | 0 | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202034 | 18L | Proposed | P0 | 14 | 8SULLIVAN TN | VH |  |  |  |  | 1.0612 | 1.0612 | 0.92 | 1.05 | 0 | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202035 | 18L | Proposed | P0 | 14 | 8PLEASANT HL | VH |  |  |  |  | 1.053 | 1.053 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202036 | 18L | Proposed | P0 | 14 | 8HAYWOOD TN | VH |  |  |  |  | 1.0656 | 1.0656 | 0.92 | 1.05 | 0 | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202037 | 18L | Proposed | P0 | 14 | 8LAG CRK CT | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202038 | 18L | Proposed | P0 | 14 | 8PIN HOOK TN | VH |  |  |  |  | 1.0778 | 1.0778 | 0.92 | 1.05 | 0 | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202039 | 18L | Proposed | P0 | 14 | 8GLEASON CT | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202040 | 18L | Proposed | P0 | 14 | 8BENTON MS | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202041 | 18L | Proposed | P0 | 14 | 8MAGNOL CC1 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202042 | 18L | Proposed | P0 | 14 | 8MAGNOL CC2 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202043 | 18L | Proposed | P0 | 14 | 8LAG CRK CC | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202044 | 18L | Proposed | P1 | 14 | 3PARAGOULD! | VH |  |  |  |  | 1.0504 | 1.061 | 0.92 | 1.05 | 110 | G-337910-1 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | G-337910-1 |  |  | VH
202045 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0714 | 0.92 | 1.05 | 110 | G-337910-1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | G-337910-1 |  |  | VH
202046 | 18L | Proposed | P1 | 14 | 3PARAGOULD! | VH |  |  |  |  | 1.05 | 1.061 | 0.92 | 1.05 | 111 | G-337911-1 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | G-337911-1 |  |  | VH
202047 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0509 | 1.0714 | 0.92 | 1.05 | 111 | G-337911-1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | G-337911-1 |  |  | VH
202048 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.058 | 1.0714 | 0.92 | 1.05 | 113 | G-338146-1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | G-338146-1 |  |  | VH
202049 | 18L | Proposed | P1 | 14 | 2MCCLELLAN | VH |  |  |  |  | 1.0617 | 1.0256 | 0.92 | 1.05 | 117 | G-338500-1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | G-338500-1 |  |  | VH
202050 | 18L | Proposed | P1 | 14 | 8NEWMAD | VH |  |  |  |  | 1.0585 | 1.0463 | 0.92 | 1.05 | 159 | P1_2-1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202051 | 18L | Proposed | P1 | 14 | 7ESSEX | VH |  |  |  |  | 1.0571 | 1.0462 | 0.92 | 1.05 | 159 | P1_2-1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202052 | 18L | Proposed | P1 | 14 | 7NEWMAD | VH |  |  |  |  | 1.0549 | 1.0372 | 0.92 | 1.05 | 159 | P1_2-1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202053 | 18L | Proposed | P1 | 14 | 7STFRAN | VH |  |  |  |  | 1.0611 | 1.0473 | 0.92 | 1.05 | 159 | P1_2-1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202054 | 18L | Proposed | P1 | 14 | 7GOBKNOB | VH |  |  |  |  | 1.062 | 1.0515 | 0.92 | 1.05 | 159 | P1_2-1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202055 | 18L | Proposed | P1 | 14 | 8WNEWMADRID | VH |  |  |  |  | 1.0585 | 1.0462 | 0.92 | 1.05 | 159 | P1_2-1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202056 | 18L | Proposed | P1 | 14 | 7WNEWMADRID | VH |  |  |  |  | 1.0549 | 1.0373 | 0.92 | 1.05 | 159 | P1_2-1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202057 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0714 | 0.92 | 1.05 | 159 | P1_2-1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% |  |  | VH
202058 | 18L | Proposed | P1 | 14 | 7STFRAN | VH |  |  |  |  | 1.0743 | 1.0473 | 0.92 | 1.05 | 165 | P1_2-7 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! |  |  | VH
202059 | 18L | Proposed | P1 | 14 | 7GOBKNOB | VH |  |  |  |  | 1.0724 | 1.0515 | 0.92 | 1.05 | 165 | P1_2-7 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! |  |  | VH
202060 | 18L | Proposed | P1 | 14 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.0462 | 0.92 | 1.05 | 169 | P1_2-11 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID |  |  | VH
202061 | 18L | Proposed | P1 | 14 | 7WNEWMADRID | VH |  |  |  |  | 1.0545 | 1.0373 | 0.92 | 1.05 | 169 | P1_2-11 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID |  |  | VH
202062 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0613 | 1.0714 | 0.92 | 1.05 | 196 | P1_2-38 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! |  |  | VH
202063 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0607 | 1.0714 | 0.92 | 1.05 | 217 | P1_2-59 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% |  |  | VH
202064 | 18L | Proposed | P1 | 14 | 2APLHERN | VH |  |  |  |  | 1.0525 | 1.0135 | 0.92 | 1.05 | 283 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
202065 | 18L | Proposed | P1 | 14 | 2BRYAN A! | VH |  |  |  |  | 1.095 | 1.0219 | 0.92 | 1.05 | 283 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | VH
202066 | 18L | Proposed | P1 | 14 | 2CALDWEL! | VH |  |  |  |  | 1.0552 | 1.0212 | 0.92 | 1.05 | 284 | P1_2-126 | 334009 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-126 |  |  | VH
202067 | 18L | Proposed | P1 | 14 | 2SOMERVL! | VH |  |  |  |  | 1.0571 | 1.0188 | 0.92 | 1.05 | 287 | P1_2-129 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-129 |  |  | VH
202068 | 18L | Proposed | P1 | 14 | 2SOMERVL! | VH |  |  |  |  | 1.0629 | 1.0188 | 0.92 | 1.05 | 288 | P1_2-130 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
202069 | 18L | Proposed | P1 | 14 | 2INDEPEN | VH |  |  |  |  | 1.0636 | 1.0137 | 0.92 | 1.05 | 288 | P1_2-130 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
202070 | 18L | Proposed | P1 | 14 | 2IN.AT$T | VH |  |  |  |  | 1.064 | 1.0102 | 0.92 | 1.05 | 288 | P1_2-130 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
202071 | 18L | Proposed | P1 | 14 | 2ANAVSOT! | VH |  |  |  |  | 1.0645 | 1.0012 | 0.92 | 1.05 | 288 | P1_2-130 | 334013 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-130 |  |  | VH
202072 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0401 | 0.92 | 1.05 | 376 | P1_2-219 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-219 |  |  | VH
202073 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0514 | 1.0401 | 0.92 | 1.05 | 377 | P1_2-220 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! |  |  | VH
202074 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0703 | 1.0401 | 0.92 | 1.05 | 378 | P1_2-221 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! |  |  | VH
202075 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0534 | 1.0401 | 0.92 | 1.05 | 379 | P1_2-222 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! |  |  | VH
202076 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 380 | P1_2-223 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! |  |  | VH
202077 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0578 | 1.0401 | 0.92 | 1.05 | 386 | P1_2-229 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! |  |  | VH
202078 | 18L | Proposed | P1 | 14 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0401 | 0.92 | 1.05 | 390 | P1_2-233 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! |  |  | VH
202079 | 18L | Proposed | P1 | 14 | 2WEIRGAT | VL |  |  |  |  | 0.9154 | 0.9382 | 0.92 | 1.05 | 394 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202080 | 18L | Proposed | P1 | 14 | 2PINELND | VL |  |  |  |  | 0.9134 | 0.9566 | 0.92 | 1.05 | 396 | P1_2-239 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202081 | 18L | Proposed | P1 | 14 | 2TEMPL1* | VL |  |  |  |  | 0.9115 | 0.9548 | 0.92 | 1.05 | 396 | P1_2-239 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202082 | 18L | Proposed | P1 | 14 | 2TEMPLE1 | VL |  |  |  |  | 0.9112 | 0.9546 | 0.92 | 1.05 | 396 | P1_2-239 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202083 | 18L | Proposed | P1 | 14 | 2TEMPL2* | VL |  |  |  |  | 0.9112 | 0.9545 | 0.92 | 1.05 | 396 | P1_2-239 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202084 | 18L | Proposed | P1 | 14 | 2TEMPLE2 | VL |  |  |  |  | 0.911 | 0.9544 | 0.92 | 1.05 | 396 | P1_2-239 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202085 | 18L | Proposed | P1 | 14 | 2TMPLSWC | VL |  |  |  |  | 0.911 | 0.9544 | 0.92 | 1.05 | 396 | P1_2-239 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202086 | 18L | Proposed | P1 | 14 | 2WEIRGAT | VL |  |  |  |  | 0.8944 | 0.9382 | 0.92 | 1.05 | 396 | P1_2-239 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202087 | 18L | Proposed | P1 | 14 | 2JACKSON! | VH |  |  |  |  | 1.1552 | 1.0243 | 0.92 | 1.05 | 913 | P1_2-758 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202088 | 18L | Proposed | P1 | 14 | 2FELICIANA | VH |  |  |  |  | 1.1607 | 1.0173 | 0.92 | 1.05 | 913 | P1_2-758 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202089 | 18L | Proposed | P1 | 14 | 2MCMANUS | VH |  |  |  |  | 1.1644 | 1.013 | 0.92 | 1.05 | 913 | P1_2-758 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202090 | 18L | Proposed | P1 | 14 | 2BRADY_HGHTS | VH |  |  |  |  | 1.1597 | 1.0076 | 0.92 | 1.05 | 913 | P1_2-758 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202091 | 18L | Proposed | P1 | 14 | 2CLINTON | VH |  |  |  |  | 1.1594 | 1.0072 | 0.92 | 1.05 | 913 | P1_2-758 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202092 | 18L | Proposed | P1 | 14 | 2CLINTON_REA | VH |  |  |  |  | 1.1597 | 1.0076 | 0.92 | 1.05 | 913 | P1_2-758 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202093 | 18L | Proposed | P1 | 14 | 2TEJAC | VH |  |  |  |  | 1.1494 | 1.03 | 0.92 | 1.05 | 913 | P1_2-758 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202094 | 18L | Proposed | P1 | 14 | 2MARYDALE | VH |  |  |  |  | 1.1433 | 1.0359 | 0.92 | 1.05 | 913 | P1_2-758 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202095 | 18L | Proposed | P1 | 14 | 2FRANCIS! | VH |  |  |  |  | 1.1118 | 1.035 | 0.92 | 1.05 | 913 | P1_2-758 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202096 | 18L | Proposed | P1 | 14 | 2ANGOLA | VH |  |  |  |  | 1.098 | 1.02 | 0.92 | 1.05 | 913 | P1_2-758 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202097 | 18L | Proposed | P1 | 14 | 2GRANT | VH |  |  |  |  | 1.0828 | 1.0285 | 0.92 | 1.05 | 913 | P1_2-758 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! |  |  | VH
202098 | 18L | Proposed | P1 | 14 | 2JACKSON! | VH |  |  |  |  | 1.0969 | 1.0243 | 0.92 | 1.05 | 920 | P1_2-765 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202099 | 18L | Proposed | P1 | 14 | 2FELICIANA | VH |  |  |  |  | 1.1014 | 1.0173 | 0.92 | 1.05 | 920 | P1_2-765 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202100 | 18L | Proposed | P1 | 14 | 2MCMANUS | VH |  |  |  |  | 1.1045 | 1.013 | 0.92 | 1.05 | 920 | P1_2-765 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202101 | 18L | Proposed | P1 | 14 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0995 | 1.0076 | 0.92 | 1.05 | 920 | P1_2-765 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202102 | 18L | Proposed | P1 | 14 | 2CLINTON | VH |  |  |  |  | 1.0991 | 1.0072 | 0.92 | 1.05 | 920 | P1_2-765 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202103 | 18L | Proposed | P1 | 14 | 2CLINTON_REA | VH |  |  |  |  | 1.0995 | 1.0076 | 0.92 | 1.05 | 920 | P1_2-765 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202104 | 18L | Proposed | P1 | 14 | 2TEJAC | VH |  |  |  |  | 1.1076 | 1.03 | 0.92 | 1.05 | 920 | P1_2-765 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202105 | 18L | Proposed | P1 | 14 | 2MARYDALE | VH |  |  |  |  | 1.119 | 1.0359 | 0.92 | 1.05 | 920 | P1_2-765 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202106 | 18L | Proposed | P1 | 14 | 2FRANCIS! | VH |  |  |  |  | 1.1287 | 1.035 | 0.92 | 1.05 | 920 | P1_2-765 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202107 | 18L | Proposed | P1 | 14 | 2ANGOLA | VH |  |  |  |  | 1.115 | 1.02 | 0.92 | 1.05 | 920 | P1_2-765 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! |  |  | VH
202108 | 18L | Proposed | P1 | 14 | 3GMEADW! | VH |  |  |  |  | 1.1709 | 1.0242 | 0.92 | 1.05 | 963 | P1_2-808 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202109 | 18L | Proposed | P1 | 14 | 3LEEVLL | VH |  |  |  |  | 1.1952 | 1.0174 | 0.92 | 1.05 | 963 | P1_2-808 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202110 | 18L | Proposed | P1 | 14 | 3FOURCHN | VH |  |  |  |  | 1.195 | 1.0079 | 0.92 | 1.05 | 963 | P1_2-808 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202111 | 18L | Proposed | P1 | 14 | 6TUNICA! | VH |  |  |  |  | 1.0513 | 1.0379 | 0.92 | 1.05 | 1315 | P1_2-1160 | 337160 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! |  |  | VH
202112 | 18L | Proposed | P1 | 14 | 5HORN LAKE% | VH |  |  |  |  | 1.0536 | 1.0684 | 0.92 | 1.05 | 1317 | P1_2-1162 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% |  |  | VH
202113 | 18L | Proposed | P1 | 14 | 3BLACK_RIV | VH |  |  |  |  | 1.0907 | 0.9969 | 0.92 | 1.05 | 1336 | P1_2-1181 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202114 | 18L | Proposed | P1 | 14 | 3GILBERT | VH |  |  |  |  | 1.227 | 1.0243 | 0.92 | 1.05 | 1336 | P1_2-1181 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202115 | 18L | Proposed | P1 | 14 | 3PERSIM_MIL | VH |  |  |  |  | 1.1161 | 1.0243 | 0.92 | 1.05 | 1336 | P1_2-1181 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202116 | 18L | Proposed | P1 | 14 | 3NATCHEZSES% | VH |  |  |  |  | 1.1242 | 1.0345 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202117 | 18L | Proposed | P1 | 14 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1238 | 1.0346 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202118 | 18L | Proposed | P1 | 14 | 3PINE RIDGE | VH |  |  |  |  | 1.1237 | 1.0344 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202119 | 18L | Proposed | P1 | 14 | 3NATCHEZ! | VH |  |  |  |  | 1.1232 | 1.0352 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202120 | 18L | Proposed | P1 | 14 | 3J.MANVILLE | VH |  |  |  |  | 1.1214 | 1.0339 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202121 | 18L | Proposed | P1 | 14 | 3INTL PAPER | VH |  |  |  |  | 1.1205 | 1.0333 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202122 | 18L | Proposed | P1 | 14 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1198 | 1.0329 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202123 | 18L | Proposed | P1 | 14 | 3NATCHEZ IND | VH |  |  |  |  | 1.1181 | 1.032 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202124 | 18L | Proposed | P1 | 14 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1157 | 1.0325 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202125 | 18L | Proposed | P1 | 14 | 3CROSBY+ | VH |  |  |  |  | 1.0934 | 1.0279 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202126 | 18L | Proposed | P1 | 14 | 3GLOSTER | VH |  |  |  |  | 1.0868 | 1.0268 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202127 | 18L | Proposed | P1 | 14 | 3LIBERTY P/L | VH |  |  |  |  | 1.0566 | 1.0359 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202128 | 18L | Proposed | P1 | 14 | 3WOODVILLE | VH |  |  |  |  | 1.067 | 1.0055 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202129 | 18L | Proposed | P1 | 14 | 3LIBERTY! | VH |  |  |  |  | 1.0567 | 1.036 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202130 | 18L | Proposed | P1 | 14 | 3INTRSTE P/L | VH |  |  |  |  | 1.0567 | 1.036 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202131 | 18L | Proposed | P1 | 14 | 3KINGSTON MS | VH |  |  |  |  | 1.1145 | 1.0312 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202132 | 18L | Proposed | P1 | 14 | 3CENTREVILLE | VH |  |  |  |  | 1.0727 | 1.0117 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202133 | 18L | Proposed | P1 | 14 | 3WASHINGTON+ | VH |  |  |  |  | 1.1162 | 1.0334 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202134 | 18L | Proposed | P1 | 14 | 3ROXIE | VH |  |  |  |  | 1.0912 | 1.0327 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202135 | 18L | Proposed | P1 | 14 | 3MEADVILLE | VH |  |  |  |  | 1.0718 | 1.034 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202136 | 18L | Proposed | P1 | 14 | 3CRANFIELD+ | VH |  |  |  |  | 1.1074 | 1.0326 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202137 | 18L | Proposed | P1 | 14 | 3FAYETTE | VH |  |  |  |  | 1.1154 | 1.033 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202138 | 18L | Proposed | P1 | 14 | 3LORMAN+ | VH |  |  |  |  | 1.0963 | 1.0337 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202139 | 18L | Proposed | P1 | 14 | 3LORMAN | VH |  |  |  |  | 1.0962 | 1.0336 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202140 | 18L | Proposed | P1 | 14 | 3PORTGIBSON! | VH |  |  |  |  | 1.0835 | 1.0374 | 0.92 | 1.05 | 1336 | P1_2-1181 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202141 | 18L | Proposed | P1 | 14 | 3GGNS | VH |  |  |  |  | 1.0825 | 1.0364 | 0.975 | 1.05 | 1336 | P1_2-1181 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202142 | 18L | Proposed | P1 | 14 | 3BLACK_RIVER | VH |  |  |  |  | 1.0907 | 0.997 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202143 | 18L | Proposed | P1 | 14 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1152 | 1.024 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202144 | 18L | Proposed | P1 | 14 | 3PLANTATION! | VH |  |  |  |  | 1.1103 | 1.0279 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202145 | 18L | Proposed | P1 | 14 | 3VIDALIA_LA | VH |  |  |  |  | 1.112 | 1.0282 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202146 | 18L | Proposed | P1 | 14 | 3RED_GUM! | VH |  |  |  |  | 1.1368 | 1.0348 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202147 | 18L | Proposed | P1 | 14 | 3METROPOLIS | VH |  |  |  |  | 1.2149 | 1.0261 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202148 | 18L | Proposed | P1 | 14 | 3WISNER | VH |  |  |  |  | 1.2205 | 1.0255 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202149 | 18L | Proposed | P1 | 14 | 3WINNSBORO! | VH |  |  |  |  | 1.2423 | 1.0252 | 0.92 | 1.05 | 1336 | P1_2-1181 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202150 | 18L | Proposed | P1 | 14 | JNESVIL3 | VH |  |  |  |  | 1.0907 | 0.997 | 0.92 | 1.05 | 1336 | P1_2-1181 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202151 | 18L | Proposed | P1 | 14 | VIDALIA3 | VH |  |  |  |  | 1.112 | 1.0282 | 0.92 | 1.05 | 1336 | P1_2-1181 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202152 | 18L | Proposed | P1 | 14 | 3DELHI_LA! | VH |  |  |  |  | 1.0715 | 1.026 | 0.92 | 1.05 | 1412 | P1_2-1257 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! |  |  | VH
202153 | 18L | Proposed | P1 | 14 | 8ETTA% | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 1503 | P1_2-1350 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
202154 | 18L | Proposed | P1 | 14 | 8DUKE HS-1! | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 1503 | P1_2-1350 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
202155 | 18L | Proposed | P1 | 14 | 8DUKE HS-2! | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 1503 | P1_2-1350 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% |  |  | VH
202156 | 18L | Proposed | P1 | 14 | 3PARAGOULD! | VH |  |  |  |  | 1.0503 | 1.061 | 0.92 | 1.05 | 1558 | P1_2-1405 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1405 |  |  | VH
202157 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.051 | 1.0714 | 0.92 | 1.05 | 1558 | P1_2-1405 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1405 |  |  | VH
202158 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0542 | 1.0714 | 0.92 | 1.05 | 1559 | P1_2-1406 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1406 |  |  | VH
202159 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.055 | 1.0714 | 0.92 | 1.05 | 1595 | P1_2-1442 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
202160 | 18L | Proposed | P1 | 14 | 2WARD | VH |  |  |  |  | 1.0502 | 1.0603 | 0.92 | 1.05 | 1595 | P1_2-1442 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% |  |  | VH
202161 | 18L | Proposed | P1 | 14 | 3STUTGART.N+ | VH |  |  |  |  | 1.0563 | 1.0458 | 0.92 | 1.05 | 1599 | P1_2-1446 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
202162 | 18L | Proposed | P1 | 14 | 3STUTGART.N | VH |  |  |  |  | 1.0553 | 1.0448 | 0.92 | 1.05 | 1599 | P1_2-1446 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
202163 | 18L | Proposed | P1 | 14 | 3RICUSKEY! | VH |  |  |  |  | 1.0603 | 1.0492 | 0.92 | 1.05 | 1599 | P1_2-1446 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! |  |  | VH
202164 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.058 | 1.0714 | 0.92 | 1.05 | 1644 | P1_2-1494 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% |  |  | VH
202165 | 18L | Proposed | P1 | 14 | 2BLACK ROCK | VH |  |  |  |  | 1.0597 | 1.0714 | 0.92 | 1.05 | 1645 | P1_2-1495 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1495_8ISES%,8DELL% |  |  | VH
202166 | 18L | Proposed | P1 | 14 | 3PARAGOULD! | VH |  |  |  |  | 1.0506 | 1.061 | 0.92 | 1.05 | 1672 | P1_2-1522 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | VH
202167 | 18L | Proposed | P1 | 14 | 8SHELBY TN | VH |  |  |  |  | 1.0509 | 1.0613 | 0.92 | 1.05 | 1673 | P1_2-1523 | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1523 |  |  | VH
202168 | 18L | Proposed | P1 | 14 | 3SEDGWICK | VH |  |  |  |  | 1.0617 | 1.0506 | 0.92 | 1.05 | 1685 | P1_2-1535 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
202169 | 18L | Proposed | P1 | 14 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0529 | 1.0419 | 0.92 | 1.05 | 1685 | P1_2-1535 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
202170 | 18L | Proposed | P1 | 14 | 3WALNUT RDG! | VH |  |  |  |  | 1.062 | 1.0484 | 0.92 | 1.05 | 1685 | P1_2-1535 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% |  |  | VH
202171 | 18L | Proposed | P1 | 14 | 2MCCLELLAN | VH |  |  |  |  | 1.0617 | 1.0256 | 0.92 | 1.05 | 1701 | P1_2-1551 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! |  |  | VH
202172 | 18L | Proposed | P1 | 14 | 8LAG CRK CT | VH |  |  |  |  | 1.0574 | 1.0725 | 0.92 | 1.05 | 1710 | P1_2-1560 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% |  |  | VH
202173 | 18L | Proposed | P1 | 14 | 8LAG CRK CC | VH |  |  |  |  | 1.0574 | 1.0725 | 0.92 | 1.05 | 1710 | P1_2-1560 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% |  |  | VH
202174 | 18L | Proposed | P1 | 14 | 8WEAKLEY TN | VH |  |  |  |  | 1.0925 | 1.0785 | 0.92 | 1.05 | 1715 | P1_2-1565 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
202175 | 18L | Proposed | P1 | 14 | 8LAG CRK CT | VH |  |  |  |  | 1.0997 | 1.0725 | 0.92 | 1.05 | 1715 | P1_2-1565 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
202176 | 18L | Proposed | P1 | 14 | 8GLEASON CT | VH |  |  |  |  | 1.0926 | 1.0808 | 0.92 | 1.05 | 1715 | P1_2-1565 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
202177 | 18L | Proposed | P1 | 14 | 8LAG CRK CC | VH |  |  |  |  | 1.0997 | 1.0725 | 0.92 | 1.05 | 1715 | P1_2-1565 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% |  |  | VH
202178 | 18L | Proposed | P1 | 14 | 5HORN LAKE% | VH |  |  |  |  | 1.0535 | 1.0684 | 0.92 | 1.05 | 1717 | P1_2-1567 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! |  |  | VH
202179 | 18L | Proposed | P1 | 14 | 8CHOCTAW CC | VH |  |  |  |  | 1.0528 | 1.0348 | 0.92 | 1.05 | 1741 | P1_2-1591 | 360627 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% |  |  | VH
202180 | 18L | Proposed | P1 | 14 | 8CHOCTAW MS | VH |  |  |  |  | 1.0528 | 1.0347 | 0.92 | 1.05 | 1741 | P1_2-1591 | 360654 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% |  |  | VH
202181 | 18L | Proposed | P1 | 14 | 8DANIEL | VH |  |  |  |  | 1.0812 | 1.0287 | 0.92 | 1.05 | 1757 | P1_2-1607 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! |  |  | VH
202182 | 18L | Proposed | P1 | 14 | PNPRARIE 4 | VL |  |  |  |  | 0.9173 | 1.0029 | 0.92 | 1.05 | 1806 | P1_2-1656 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
202183 | 18L | Proposed | P1 | 14 | TENRUSK7 | VH |  |  |  |  | 1.0566 | 1.0205 | 0.92 | 1.05 | 2016 | P1_2-1866 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
202184 | 18L | Proposed | P1 | 14 | TENGEN 7 | VH |  |  |  |  | 1.0566 | 1.0205 | 0.92 | 1.05 | 2016 | P1_2-1866 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
202185 | 18L | Proposed | P1 | 14 | FTSMITH7 | VH |  |  |  |  | 1.0539 | 1.0376 | 0.92 | 1.05 | 2042 | P1_2-1892 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | P1_2-1892_FTSMITH7%,FTSMITH8% |  |  | VH
202186 | 18L | Proposed | P0 | 15 | 8GPDELL | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
202187 | 18L | Proposed | P0 | 15 | 7GOBKNOB | VH |  |  |  |  | 1.0515 | 1.0515 | 0.92 | 1.05 | 0 | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
202188 | 18L | Proposed | P0 | 15 | 2BATSON! | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
202189 | 18L | Proposed | P0 | 15 | 5HORN LAKE% | VH |  |  |  |  | 1.0684 | 1.0684 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202190 | 18L | Proposed | P0 | 15 | 8DELL% | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202191 | 18L | Proposed | P0 | 15 | 8SANS SOUCI% | VH |  |  |  |  | 1.0625 | 1.0625 | 0.92 | 1.05 | 0 | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202192 | 18L | Proposed | P0 | 15 | 3PARAGOULD! | VH |  |  |  |  | 1.061 | 1.061 | 0.92 | 1.05 | 0 | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202193 | 18L | Proposed | P0 | 15 | 3SEDGWICK | VH |  |  |  |  | 1.0506 | 1.0506 | 0.92 | 1.05 | 0 | ** Base Case ** | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202194 | 18L | Proposed | P0 | 15 | 3DATTO | VH |  |  |  |  | 1.0518 | 1.0518 | 0.92 | 1.05 | 0 | ** Base Case ** | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202195 | 18L | Proposed | P0 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.0714 | 1.0714 | 0.92 | 1.05 | 0 | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202196 | 18L | Proposed | P0 | 15 | 2OPPELLO | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202197 | 18L | Proposed | P0 | 15 | 2WARD | VH |  |  |  |  | 1.0603 | 1.0603 | 0.92 | 1.05 | 0 | ** Base Case ** | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202198 | 18L | Proposed | P0 | 15 | 5DELL# | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202199 | 18L | Proposed | P0 | 15 | 3LIGHT# | VH |  |  |  |  | 1.0539 | 1.0539 | 0.92 | 1.05 | 0 | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202200 | 18L | Proposed | P0 | 15 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0571 | 1.0571 | 0.92 | 1.05 | 0 | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202201 | 18L | Proposed | P0 | 15 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 | 0 | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202202 | 18L | Proposed | P0 | 15 | 7SHAWNEE FP | VH |  |  |  |  | 1.0766 | 1.0766 | 0.92 | 1.05 | 0 | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202203 | 18L | Proposed | P0 | 15 | 8RUTHERFORD | VH |  |  |  |  | 1.0689 | 1.0689 | 0.92 | 1.05 | 0 | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202204 | 18L | Proposed | P0 | 15 | 8MARSHALL KY | VH |  |  |  |  | 1.0819 | 1.0819 | 0.92 | 1.05 | 0 | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202205 | 18L | Proposed | P0 | 15 | 8WEAKLEY TN | VH |  |  |  |  | 1.0785 | 1.0785 | 0.92 | 1.05 | 0 | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202206 | 18L | Proposed | P0 | 15 | 8JACKSON TN | VH |  |  |  |  | 1.0673 | 1.0673 | 0.92 | 1.05 | 0 | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202207 | 18L | Proposed | P0 | 15 | 8SHELBY TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202208 | 18L | Proposed | P0 | 15 | 8CORDOVA TN | VH |  |  |  |  | 1.0568 | 1.0568 | 0.92 | 1.05 | 0 | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202209 | 18L | Proposed | P0 | 15 | 8UNION MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202210 | 18L | Proposed | P0 | 15 | 8JVILLE FP | VH |  |  |  |  | 1.0829 | 1.0829 | 0.92 | 1.05 | 0 | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202211 | 18L | Proposed | P0 | 15 | 8CUMBERLAND | VH |  |  |  |  | 1.0876 | 1.0876 | 0.92 | 1.05 | 0 | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202212 | 18L | Proposed | P0 | 15 | 8PARADISE FP | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 | 0 | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202213 | 18L | Proposed | P0 | 15 | 8MONTGOMERY | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202214 | 18L | Proposed | P0 | 15 | 8DAVIDSON TN | VH |  |  |  |  | 1.0799 | 1.0799 | 0.92 | 1.05 | 0 | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202215 | 18L | Proposed | P0 | 15 | 8MAURY TN | VH |  |  |  |  | 1.0682 | 1.0682 | 0.92 | 1.05 | 0 | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202216 | 18L | Proposed | P0 | 15 | 8FRANKLIN TN | VH |  |  |  |  | 1.0523 | 1.0523 | 0.92 | 1.05 | 0 | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202217 | 18L | Proposed | P0 | 15 | 8WILSON TN | VH |  |  |  |  | 1.077 | 1.077 | 0.92 | 1.05 | 0 | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202218 | 18L | Proposed | P0 | 15 | 8PLATEAU TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202219 | 18L | Proposed | P0 | 15 | 8BULL RUN FP | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 | 0 | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202220 | 18L | Proposed | P0 | 15 | 8VOLUNTEER | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202221 | 18L | Proposed | P0 | 15 | 8PHIPPS B NP | VH |  |  |  |  | 1.0678 | 1.0678 | 0.92 | 1.05 | 0 | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202222 | 18L | Proposed | P0 | 15 | 8SULLIVAN TN | VH |  |  |  |  | 1.0612 | 1.0612 | 0.92 | 1.05 | 0 | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202223 | 18L | Proposed | P0 | 15 | 8PLEASANT HL | VH |  |  |  |  | 1.053 | 1.053 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202224 | 18L | Proposed | P0 | 15 | 8HAYWOOD TN | VH |  |  |  |  | 1.0656 | 1.0656 | 0.92 | 1.05 | 0 | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202225 | 18L | Proposed | P0 | 15 | 8LAG CRK CT | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202226 | 18L | Proposed | P0 | 15 | 8PIN HOOK TN | VH |  |  |  |  | 1.0778 | 1.0778 | 0.92 | 1.05 | 0 | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202227 | 18L | Proposed | P0 | 15 | 8GLEASON CT | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202228 | 18L | Proposed | P0 | 15 | 8BENTON MS | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202229 | 18L | Proposed | P0 | 15 | 8MAGNOL CC1 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202230 | 18L | Proposed | P0 | 15 | 8MAGNOL CC2 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202231 | 18L | Proposed | P0 | 15 | 8LAG CRK CC | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202232 | 18L | Proposed | P1 | 15 | 3BLACK_RIV | VH |  |  |  |  | 1.0937 | 0.9969 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202233 | 18L | Proposed | P1 | 15 | 3GILBERT | VH |  |  |  |  | 1.1233 | 1.0243 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202234 | 18L | Proposed | P1 | 15 | 3PERSIM_MIL | VH |  |  |  |  | 1.1186 | 1.0243 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202235 | 18L | Proposed | P1 | 15 | 3BASKIN | VH |  |  |  |  | 1.0902 | 1.0191 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202236 | 18L | Proposed | P1 | 15 | 3NATCHEZSES% | VH |  |  |  |  | 1.146 | 1.0345 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202237 | 18L | Proposed | P1 | 15 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1452 | 1.0346 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202238 | 18L | Proposed | P1 | 15 | 3PINE RIDGE | VH |  |  |  |  | 1.145 | 1.0344 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202239 | 18L | Proposed | P1 | 15 | 3NATCHEZ! | VH |  |  |  |  | 1.1432 | 1.0352 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202240 | 18L | Proposed | P1 | 15 | 3J.MANVILLE | VH |  |  |  |  | 1.1404 | 1.0339 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202241 | 18L | Proposed | P1 | 15 | 3INTL PAPER | VH |  |  |  |  | 1.1383 | 1.0333 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202242 | 18L | Proposed | P1 | 15 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1368 | 1.0329 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202243 | 18L | Proposed | P1 | 15 | 3NATCHEZ IND | VH |  |  |  |  | 1.1332 | 1.032 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202244 | 18L | Proposed | P1 | 15 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1358 | 1.0325 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202245 | 18L | Proposed | P1 | 15 | 3CROSBY+ | VH |  |  |  |  | 1.1139 | 1.0279 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202246 | 18L | Proposed | P1 | 15 | 3GLOSTER | VH |  |  |  |  | 1.1075 | 1.0268 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202247 | 18L | Proposed | P1 | 15 | 3LIBERTY P/L | VH |  |  |  |  | 1.0762 | 1.0359 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202248 | 18L | Proposed | P1 | 15 | 3WOODVILLE | VH |  |  |  |  | 1.0881 | 1.0055 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202249 | 18L | Proposed | P1 | 15 | 3LIBERTY! | VH |  |  |  |  | 1.0763 | 1.036 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202250 | 18L | Proposed | P1 | 15 | 3INTRSTE P/L | VH |  |  |  |  | 1.0763 | 1.036 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202251 | 18L | Proposed | P1 | 15 | 3GILLSBURG+ | VH |  |  |  |  | 1.0543 | 1.0262 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336517 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202252 | 18L | Proposed | P1 | 15 | 3GILLSBURG | VH |  |  |  |  | 1.0527 | 1.0245 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336518 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202253 | 18L | Proposed | P1 | 15 | 3KINGSTON MS | VH |  |  |  |  | 1.1346 | 1.0312 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202254 | 18L | Proposed | P1 | 15 | 3CENTREVILLE | VH |  |  |  |  | 1.0937 | 1.0117 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202255 | 18L | Proposed | P1 | 15 | 3SMITHDALE+ | VH |  |  |  |  | 1.0548 | 1.0355 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336525 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202256 | 18L | Proposed | P1 | 15 | 3WASHINGTON+ | VH |  |  |  |  | 1.1355 | 1.0334 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202257 | 18L | Proposed | P1 | 15 | 3ROXIE | VH |  |  |  |  | 1.1019 | 1.0327 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202258 | 18L | Proposed | P1 | 15 | 3MEADVILLE | VH |  |  |  |  | 1.0762 | 1.034 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202259 | 18L | Proposed | P1 | 15 | 3CRANFIELD+ | VH |  |  |  |  | 1.1237 | 1.0326 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202260 | 18L | Proposed | P1 | 15 | 3FAYETTE | VH |  |  |  |  | 1.2119 | 1.033 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202261 | 18L | Proposed | P1 | 15 | 3LORMAN+ | VH |  |  |  |  | 1.2394 | 1.0337 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202262 | 18L | Proposed | P1 | 15 | 3LORMAN | VH |  |  |  |  | 1.2393 | 1.0336 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202263 | 18L | Proposed | P1 | 15 | 3PORTGIBSON! | VH |  |  |  |  | 1.2647 | 1.0374 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202264 | 18L | Proposed | P1 | 15 | 3GGNS | VH |  |  |  |  | 1.2639 | 1.0364 | 0.975 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202265 | 18L | Proposed | P1 | 15 | 3S.VICKSBURG | VH |  |  |  |  | 1.2987 | 1.0326 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202266 | 18L | Proposed | P1 | 15 | 3BLACK_RIVER | VH |  |  |  |  | 1.0937 | 0.997 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202267 | 18L | Proposed | P1 | 15 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1181 | 1.024 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202268 | 18L | Proposed | P1 | 15 | 3PLANTATION! | VH |  |  |  |  | 1.1189 | 1.0279 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202269 | 18L | Proposed | P1 | 15 | 3VIDALIA_LA | VH |  |  |  |  | 1.123 | 1.0282 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202270 | 18L | Proposed | P1 | 15 | 3RED_GUM! | VH |  |  |  |  | 1.1315 | 1.0348 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202271 | 18L | Proposed | P1 | 15 | 3METROPOLIS | VH |  |  |  |  | 1.1329 | 1.0261 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202272 | 18L | Proposed | P1 | 15 | 3WISNER | VH |  |  |  |  | 1.1331 | 1.0255 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202273 | 18L | Proposed | P1 | 15 | 3WINNSBORO! | VH |  |  |  |  | 1.1079 | 1.0252 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202274 | 18L | Proposed | P1 | 15 | 3ALTO_LA | VH |  |  |  |  | 1.0665 | 1.0136 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337331 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202275 | 18L | Proposed | P1 | 15 | JNESVIL3 | VH |  |  |  |  | 1.0937 | 0.997 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202276 | 18L | Proposed | P1 | 15 | VIDALIA3 | VH |  |  |  |  | 1.123 | 1.0282 | 0.92 | 1.05 | 91 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202277 | 18L | Proposed | P2 | 15 | 3ONWARD+ | VH |  |  |  |  | 1.0537 | 1.0185 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336967 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202278 | 18L | Proposed | P2 | 15 | 3ROLING FRK! | VH |  |  |  |  | 1.0671 | 1.0163 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336968 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202279 | 18L | Proposed | P2 | 15 | 3MAYERSVILLE | VH |  |  |  |  | 1.0622 | 1.0111 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336969 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202280 | 18L | Proposed | P2 | 15 | 3NITTA YUMA+ | VH |  |  |  |  | 1.0665 | 1.018 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336970 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202281 | 18L | Proposed | P2 | 15 | 3MURPHY+ | VH |  |  |  |  | 1.0661 | 1.0195 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 336992 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202282 | 18L | Proposed | P2 | 15 | 3SE.GREENVL | VH |  |  |  |  | 1.0532 | 1.0368 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337045 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202283 | 18L | Proposed | P2 | 15 | 3GREENVILLE+ | VH |  |  |  |  | 1.0542 | 1.0337 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202284 | 18L | Proposed | P2 | 15 | 3HOLLANDALE | VH |  |  |  |  | 1.067 | 1.0204 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337048 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202285 | 18L | Proposed | P2 | 15 | 3ARCOLA+ | VH |  |  |  |  | 1.0602 | 1.0267 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202286 | 18L | Proposed | P2 | 15 | 3SWIFTWATER | VH |  |  |  |  | 1.0539 | 1.0333 | 0.92 | 1.05 | 263 | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337044 3GREENVILLE! 115 337045 3SE.GREENVL 115 1 |  | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
202287 | 18L | Proposed | P1 | 15 | 5HORN LAKE% | VH |  |  |  |  | 1.0536 | 1.0684 | 0.92 | 1.05 | 363 | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | 337162 6FREEPORT% 230 337180 6HORN LAKE% 230 1 |  |  | VH
202288 | 18L | Proposed | P1 | 15 | 6TUNICA! | VH |  |  |  |  | 1.0513 | 1.0379 | 0.92 | 1.05 | 401 | 337160 6TUNICA! 230 337998 6RITCHIE-1! 230 1 | 337160 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | 337160 6TUNICA! 230 337998 6RITCHIE-1! 230 1 |  |  | VH
202289 | 18L | Proposed | P1 | 15 | 8ETTA% | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 618 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
202290 | 18L | Proposed | P1 | 15 | 8DUKE HS-1! | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 618 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
202291 | 18L | Proposed | P1 | 15 | 8DUKE HS-2! | VH |  |  |  |  | 1.0603 | 1.0359 | 0.92 | 1.05 | 618 | 337753 8HS EHV% 500 337754 8ETTA% 500 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 337753 8HS EHV% 500 337754 8ETTA% 500 1 |  |  | VH
202292 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.055 | 1.0714 | 0.92 | 1.05 | 729 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
202293 | 18L | Proposed | P1 | 15 | 2WARD | VH |  |  |  |  | 1.0502 | 1.0603 | 0.92 | 1.05 | 729 | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337957 8KEO% 500 338140 8HOLND BTM% 500 1 |  |  | VH
202294 | 18L | Proposed | P1 | 15 | 3HUMPHREY# | VH |  |  |  |  | 1.0509 | 1.0386 | 0.92 | 1.05 | 733 | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337962 3ALTHEIMER+ 115 338738 3WABASEKA.W# 115 1 |  |  | VH
202295 | 18L | Proposed | P1 | 15 | 3WABBASEKA | VH |  |  |  |  | 1.0519 | 1.0323 | 0.92 | 1.05 | 734 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 |  |  | VH
202296 | 18L | Proposed | P1 | 15 | 3HUMPHREY# | VH |  |  |  |  | 1.0524 | 1.0386 | 0.92 | 1.05 | 734 | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337964 3WABBASEKA 115 338738 3WABASEKA.W# 115 1 |  |  | VH
202297 | 18L | Proposed | P1 | 15 | 3HUMPHREY# | VH |  |  |  |  | 1.053 | 1.0386 | 0.92 | 1.05 | 735 | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337964 3WABBASEKA 115 338741 3HUMPHREY# 115 1 |  |  | VH
202298 | 18L | Proposed | P1 | 15 | 3ALMYRA | VH |  |  |  |  | 1.0555 | 1.0362 | 0.92 | 1.05 | 746 | 337972 3ALMYRA 115 337973 3DEWITT 115 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337972 3ALMYRA 115 337973 3DEWITT 115 1 |  |  | VH
202299 | 18L | Proposed | P1 | 15 | 2DELUCE | VH |  |  |  |  | 1.0583 | 1.0471 | 0.92 | 1.05 | 749 | 337974 3GILLETT! 115 338514 3L&D#2! 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337974 3GILLETT! 115 338514 3L&D#2! 115 1 |  |  | VH
202300 | 18L | Proposed | P1 | 15 | 2DELUCE | VH |  |  |  |  | 1.0617 | 1.0471 | 0.92 | 1.05 | 750 | 337974 3GILLETT! 115 338752 3DELUCE# 115 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 337974 3GILLETT! 115 338752 3DELUCE# 115 1 |  |  | VH
202301 | 18L | Proposed | P1 | 15 | 2PALESTINE | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 789 | 338020 5BRINKLEY.E 161 338882 5PALESTINE# 161 1 | 338630 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338020 5BRINKLEY.E 161 338882 5PALESTINE# 161 1 |  |  | VH
202302 | 18L | Proposed | P1 | 15 | 2WYNNE.E | VH |  |  |  |  | 1.0651 | 1.0487 | 0.92 | 1.05 | 800 | 338031 5WYNNE.S 161 338883 5WYNNE.E# 161 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338031 5WYNNE.S 161 338883 5WYNNE.E# 161 1 |  |  | VH
202303 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.0597 | 1.0714 | 0.92 | 1.05 | 859 | 338145 8ISES% 500 338187 8DELL% 500 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338145 8ISES% 500 338187 8DELL% 500 1 |  |  | VH
202304 | 18L | Proposed | P1 | 15 | 3PARAGOULD! | VH |  |  |  |  | 1.0506 | 1.061 | 0.92 | 1.05 | 892 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
202305 | 18L | Proposed | P1 | 15 | 3LIGHT# | VH |  |  |  |  | 1.0666 | 1.0539 | 0.92 | 1.05 | 914 | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338206 3SEDGWICK 115 338704 3LIGHT# 115 1 |  |  | VH
202306 | 18L | Proposed | P1 | 15 | 3SEDGWICK | VH |  |  |  |  | 1.0617 | 1.0506 | 0.92 | 1.05 | 915 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
202307 | 18L | Proposed | P1 | 15 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0529 | 1.0419 | 0.92 | 1.05 | 915 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
202308 | 18L | Proposed | P1 | 15 | 3WALNUT RDG! | VH |  |  |  |  | 1.062 | 1.0484 | 0.92 | 1.05 | 915 | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338208 3WALNUT RDG! 115 338213 5WALNUT RDG% 161 1 |  |  | VH
202309 | 18L | Proposed | P1 | 15 | 3DATTO | VH |  |  |  |  | 1.0645 | 1.0518 | 0.92 | 1.05 | 931 | 338227 3DATTO 115 338691 3CORNING.N# 115 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338227 3DATTO 115 338691 3CORNING.N# 115 1 |  |  | VH
202310 | 18L | Proposed | P1 | 15 | 3CORNING | VH |  |  |  |  | 1.0596 | 1.0456 | 0.92 | 1.05 | 932 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 |  |  | VH
202311 | 18L | Proposed | P1 | 15 | 3CORNING.N# | VH |  |  |  |  | 1.0598 | 1.0463 | 0.92 | 1.05 | 932 | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338229 3T.E.P/S-8 115 1 |  |  | VH
202312 | 18L | Proposed | P1 | 15 | 3DATTO | VH |  |  |  |  | 1.0641 | 1.0518 | 0.92 | 1.05 | 933 | 338228 3CORNING 115 338691 3CORNING.N# 115 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338691 3CORNING.N# 115 1 |  |  | VH
202313 | 18L | Proposed | P1 | 15 | 3CORNING.N# | VH |  |  |  |  | 1.0638 | 1.0463 | 0.92 | 1.05 | 933 | 338228 3CORNING 115 338691 3CORNING.N# 115 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338228 3CORNING 115 338691 3CORNING.N# 115 1 |  |  | VH
202314 | 18L | Proposed | P1 | 15 | 3PARAGOULD! | VH |  |  |  |  | 1.0504 | 1.061 | 0.92 | 1.05 | 978 | Unit:337910 1ANO U1 22.0 Id:1 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | Unit:337910 1ANO U1 22.0 Id:1 |  |  | VH
202315 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0714 | 0.92 | 1.05 | 978 | Unit:337910 1ANO U1 22.0 Id:1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | Unit:337910 1ANO U1 22.0 Id:1 |  |  | VH
202316 | 18L | Proposed | P1 | 15 | 3PARAGOULD! | VH |  |  |  |  | 1.05 | 1.061 | 0.92 | 1.05 | 979 | Unit:337911 1ANO U2 22.0 Id:1 | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | Unit:337911 1ANO U2 22.0 Id:1 |  |  | VH
202317 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.0509 | 1.0714 | 0.92 | 1.05 | 979 | Unit:337911 1ANO U2 22.0 Id:1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | Unit:337911 1ANO U2 22.0 Id:1 |  |  | VH
202318 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.058 | 1.0714 | 0.92 | 1.05 | 981 | Unit:338146 1ISES U2 26.0 Id:1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | Unit:338146 1ISES U2 26.0 Id:1 |  |  | VH
202319 | 18L | Proposed | P1 | 15 | 2APLHERN | VH |  |  |  |  | 1.0525 | 1.0135 | 0.92 | 1.05 | 1080 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
202320 | 18L | Proposed | P1 | 15 | 2BRYAN A! | VH |  |  |  |  | 1.095 | 1.0219 | 0.92 | 1.05 | 1080 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | VH
202321 | 18L | Proposed | P1 | 15 | 2CALDWEL! | VH |  |  |  |  | 1.0552 | 1.0212 | 0.92 | 1.05 | 1083 | 334008 2BRYAN B! 69.0 334009 2CALDWEL! 69.0 1 | 334009 |  |  |  | 69 | 69 | 351 | EES |  |  | 334008 2BRYAN B! 69.0 334009 2CALDWEL! 69.0 1 |  |  | VH
202322 | 18L | Proposed | P1 | 15 | 2SOMERVL! | VH |  |  |  |  | 1.0572 | 1.0188 | 0.92 | 1.05 | 1086 | 334010 2SOMERVL! 69.0 334011 2INDEPEN 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334010 2SOMERVL! 69.0 334011 2INDEPEN 69.0 1 |  |  | VH
202323 | 18L | Proposed | P1 | 15 | 2SOMERVL! | VH |  |  |  |  | 1.0579 | 1.0188 | 0.92 | 1.05 | 1087 | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 |  |  | VH
202324 | 18L | Proposed | P1 | 15 | 2INDEPEN | VH |  |  |  |  | 1.0579 | 1.0137 | 0.92 | 1.05 | 1087 | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334011 2INDEPEN 69.0 334012 2IN.AT$T 69.0 1 |  |  | VH
202325 | 18L | Proposed | P1 | 15 | 2SOMERVL! | VH |  |  |  |  | 1.0593 | 1.0188 | 0.92 | 1.05 | 1088 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
202326 | 18L | Proposed | P1 | 15 | 2INDEPEN | VH |  |  |  |  | 1.0594 | 1.0137 | 0.92 | 1.05 | 1088 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
202327 | 18L | Proposed | P1 | 15 | 2IN.AT$T | VH |  |  |  |  | 1.0595 | 1.0102 | 0.92 | 1.05 | 1088 | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | 334012 2IN.AT$T 69.0 334013 2ANAVSOT! 69.0 1 |  |  | VH
202328 | 18L | Proposed | P1 | 15 | 2SOMERVL! | VH |  |  |  |  | 1.0629 | 1.0188 | 0.92 | 1.05 | 1089 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334010 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
202329 | 18L | Proposed | P1 | 15 | 2INDEPEN | VH |  |  |  |  | 1.0636 | 1.0137 | 0.92 | 1.05 | 1089 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334011 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
202330 | 18L | Proposed | P1 | 15 | 2IN.AT$T | VH |  |  |  |  | 1.064 | 1.0102 | 0.92 | 1.05 | 1089 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334012 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
202331 | 18L | Proposed | P1 | 15 | 2ANAVSOT! | VH |  |  |  |  | 1.0645 | 1.0012 | 0.92 | 1.05 | 1089 | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 | 334013 |  |  |  | 69 | 69 | 351 | EES |  |  | 334013 2ANAVSOT! 69.0 334023 4NAVSOTA! 138 1 |  |  | VH
202332 | 18L | Proposed | P1 | 15 | 4MAGROVE | VH |  |  |  |  | 1.1567 | 1.0321 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202333 | 18L | Proposed | P1 | 15 | 4L111T411 | VH |  |  |  |  | 1.1447 | 1.0258 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202334 | 18L | Proposed | P1 | 15 | 4KICKAPO | VH |  |  |  |  | 1.1446 | 1.0257 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202335 | 18L | Proposed | P1 | 15 | 4CORIGAN! | VH |  |  |  |  | 1.1318 | 1.0197 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202336 | 18L | Proposed | P1 | 15 | 4SHECORR | VH |  |  |  |  | 1.1301 | 1.0193 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202337 | 18L | Proposed | P1 | 15 | 4CAMDEN | VH |  |  |  |  | 1.1215 | 1.0179 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202338 | 18L | Proposed | P1 | 15 | 4DEER 1 | VH |  |  |  |  | 1.0971 | 1.0173 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202339 | 18L | Proposed | P1 | 15 | 4TURKEYCRK | VH |  |  |  |  | 1.0873 | 1.0173 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202340 | 18L | Proposed | P1 | 15 | 4DOUCETT! | VH |  |  |  |  | 1.088 | 1.0173 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202341 | 18L | Proposed | P1 | 15 | 4FORK CK | VH |  |  |  |  | 1.0791 | 1.017 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202342 | 18L | Proposed | P1 | 15 | 4RAYBURN% | VH |  |  |  |  | 1.0616 | 1.0177 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334282 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202343 | 18L | Proposed | P1 | 15 | 4MILLCR! | VH |  |  |  |  | 1.0567 | 1.0156 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202344 | 18L | Proposed | P1 | 15 | 4HRTNHIL | VH |  |  |  |  | 1.0509 | 1.0133 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202345 | 18L | Proposed | P1 | 15 | 4PEACH! | VH |  |  |  |  | 1.0521 | 1.0155 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202346 | 18L | Proposed | P1 | 15 | 4URLAND! | VH |  |  |  |  | 1.0784 | 1.0184 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202347 | 18L | Proposed | P1 | 15 | 4WOODVILLE | VH |  |  |  |  | 1.0813 | 1.018 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202348 | 18L | Proposed | P1 | 15 | 4WARREN! | VH |  |  |  |  | 1.0651 | 1.0202 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334316 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202349 | 18L | Proposed | P1 | 15 | 4JASPER | VH |  |  |  |  | 1.0583 | 1.0161 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334330 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202350 | 18L | Proposed | P1 | 15 | 4JASON | VH |  |  |  |  | 1.0567 | 1.0145 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334331 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202351 | 18L | Proposed | P1 | 15 | 4HLYSPG# | VH |  |  |  |  | 1.0525 | 1.0144 | 0.92 | 1.05 | 1193 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334332 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202352 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0521 | 1.0401 | 0.92 | 1.05 | 1247 | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334221 4BAYSHOR 138 334222 4HANKAMR 138 1 |  |  | VH
202353 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0533 | 1.0401 | 0.92 | 1.05 | 1248 | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334222 4HANKAMR 138 334223 4CROKBYU 138 1 |  |  | VH
202354 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0401 | 0.92 | 1.05 | 1250 | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334223 4CROKBYU 138 334225 4STOWELL! 138 1 |  |  | VH
202355 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0514 | 1.0401 | 0.92 | 1.05 | 1251 | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334227 4BIGHILL! 138 1 |  |  | VH
202356 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0703 | 1.0401 | 0.92 | 1.05 | 1252 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 |  |  | VH
202357 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0534 | 1.0401 | 0.92 | 1.05 | 1253 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 2 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 2 |  |  | VH
202358 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 1254 | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334226 4BYUFARM 138 334227 4BIGHILL! 138 1 |  |  | VH
202359 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0578 | 1.0401 | 0.92 | 1.05 | 1260 | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334235 2STOWELL! 69.0 334265 2WINSHIR! 69.0 1 |  |  | VH
202360 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0544 | 1.0401 | 0.92 | 1.05 | 1272 | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334265 2WINSHIR! 69.0 334266 2CRAIGEN 69.0 1 |  |  | VH
202361 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0526 | 1.0401 | 0.92 | 1.05 | 1273 | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334266 2CRAIGEN 69.0 334267 2BYFANTA 69.0 1 |  |  | VH
202362 | 18L | Proposed | P1 | 15 | 2HIMEX | VH |  |  |  |  | 1.0522 | 1.0401 | 0.92 | 1.05 | 1275 | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334267 2BYFANTA 69.0 334269 2PANSY! 69.0 1 |  |  | VH
202363 | 18L | Proposed | P1 | 15 | 2WEIRGAT | VL |  |  |  |  | 0.9154 | 0.9382 | 0.92 | 1.05 | 1283 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202364 | 18L | Proposed | P1 | 15 | 2PINELND | VL |  |  |  |  | 0.9134 | 0.9566 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202365 | 18L | Proposed | P1 | 15 | 2TEMPL1* | VL |  |  |  |  | 0.9115 | 0.9548 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202366 | 18L | Proposed | P1 | 15 | 2TEMPLE1 | VL |  |  |  |  | 0.9112 | 0.9546 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202367 | 18L | Proposed | P1 | 15 | 2TEMPL2* | VL |  |  |  |  | 0.9112 | 0.9545 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202368 | 18L | Proposed | P1 | 15 | 2TEMPLE2 | VL |  |  |  |  | 0.911 | 0.9544 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202369 | 18L | Proposed | P1 | 15 | 2TMPLSWC | VL |  |  |  |  | 0.911 | 0.9544 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202370 | 18L | Proposed | P1 | 15 | 2WEIRGAT | VL |  |  |  |  | 0.8944 | 0.9382 | 0.92 | 1.05 | 1285 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202371 | 18L | Proposed | P1 | 15 | 2WEIRGAT | VL |  |  |  |  | 0.9128 | 0.9382 | 0.92 | 1.05 | 1288 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202372 | 18L | Proposed | P1 | 15 | 2GRAVEL_RIDG | VH |  |  |  |  | 1.1481 | 1.0172 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335784 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202373 | 18L | Proposed | P1 | 15 | 2JACKSON! | VH |  |  |  |  | 1.1493 | 1.0243 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202374 | 18L | Proposed | P1 | 15 | 2FELICIANA | VH |  |  |  |  | 1.1547 | 1.0173 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202375 | 18L | Proposed | P1 | 15 | 2MCMANUS | VH |  |  |  |  | 1.1584 | 1.013 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202376 | 18L | Proposed | P1 | 15 | 2BRADY_HGHTS | VH |  |  |  |  | 1.1537 | 1.0076 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202377 | 18L | Proposed | P1 | 15 | 2CLINTON | VH |  |  |  |  | 1.1534 | 1.0072 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202378 | 18L | Proposed | P1 | 15 | 2CLINTON_REA | VH |  |  |  |  | 1.1537 | 1.0076 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202379 | 18L | Proposed | P1 | 15 | 2TEJAC | VH |  |  |  |  | 1.1437 | 1.03 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202380 | 18L | Proposed | P1 | 15 | 2MARYDALE | VH |  |  |  |  | 1.1379 | 1.0359 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202381 | 18L | Proposed | P1 | 15 | 2FRANCIS! | VH |  |  |  |  | 1.1076 | 1.035 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202382 | 18L | Proposed | P1 | 15 | 2ANGOLA | VH |  |  |  |  | 1.0937 | 1.02 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202383 | 18L | Proposed | P1 | 15 | 2GRANT | VH |  |  |  |  | 1.0795 | 1.0285 | 0.92 | 1.05 | 2033 | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | 335783 2SANDY_CREEK69.0 335784 2GRAVEL_RIDG69.0 1 |  |  | VH
202384 | 18L | Proposed | P1 | 15 | 2JACKSON! | VH |  |  |  |  | 1.1547 | 1.0243 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202385 | 18L | Proposed | P1 | 15 | 2FELICIANA | VH |  |  |  |  | 1.1602 | 1.0173 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202386 | 18L | Proposed | P1 | 15 | 2MCMANUS | VH |  |  |  |  | 1.1638 | 1.013 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202387 | 18L | Proposed | P1 | 15 | 2BRADY_HGHTS | VH |  |  |  |  | 1.1591 | 1.0076 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202388 | 18L | Proposed | P1 | 15 | 2CLINTON | VH |  |  |  |  | 1.1588 | 1.0072 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202389 | 18L | Proposed | P1 | 15 | 2CLINTON_REA | VH |  |  |  |  | 1.1591 | 1.0076 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202390 | 18L | Proposed | P1 | 15 | 2TEJAC | VH |  |  |  |  | 1.1488 | 1.03 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202391 | 18L | Proposed | P1 | 15 | 2MARYDALE | VH |  |  |  |  | 1.1427 | 1.0359 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202392 | 18L | Proposed | P1 | 15 | 2FRANCIS! | VH |  |  |  |  | 1.1113 | 1.035 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202393 | 18L | Proposed | P1 | 15 | 2ANGOLA | VH |  |  |  |  | 1.0974 | 1.02 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202394 | 18L | Proposed | P1 | 15 | 2GRANT | VH |  |  |  |  | 1.0823 | 1.0285 | 0.92 | 1.05 | 2034 | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | 335784 2GRAVEL_RIDG69.0 335785 2JACKSON! 69.0 1 |  |  | VH
202395 | 18L | Proposed | P1 | 15 | 2JACKSON! | VH |  |  |  |  | 1.0968 | 1.0243 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202396 | 18L | Proposed | P1 | 15 | 2FELICIANA | VH |  |  |  |  | 1.1014 | 1.0173 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202397 | 18L | Proposed | P1 | 15 | 2MCMANUS | VH |  |  |  |  | 1.1044 | 1.013 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202398 | 18L | Proposed | P1 | 15 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0995 | 1.0076 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202399 | 18L | Proposed | P1 | 15 | 2CLINTON | VH |  |  |  |  | 1.0991 | 1.0072 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202400 | 18L | Proposed | P1 | 15 | 2CLINTON_REA | VH |  |  |  |  | 1.0995 | 1.0076 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202401 | 18L | Proposed | P1 | 15 | 2TEJAC | VH |  |  |  |  | 1.1075 | 1.03 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202402 | 18L | Proposed | P1 | 15 | 2MARYDALE | VH |  |  |  |  | 1.1189 | 1.0359 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202403 | 18L | Proposed | P1 | 15 | 2FRANCIS! | VH |  |  |  |  | 1.1286 | 1.035 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202404 | 18L | Proposed | P1 | 15 | 2ANGOLA | VH |  |  |  |  | 1.115 | 1.02 | 0.92 | 1.05 | 2044 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  |  | VH
202405 | 18L | Proposed | P1 | 15 | 2JACKSON! | VH |  |  |  |  | 1.0954 | 1.0243 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202406 | 18L | Proposed | P1 | 15 | 2FELICIANA | VH |  |  |  |  | 1.0999 | 1.0173 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202407 | 18L | Proposed | P1 | 15 | 2MCMANUS | VH |  |  |  |  | 1.103 | 1.013 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202408 | 18L | Proposed | P1 | 15 | 2BRADY_HGHTS | VH |  |  |  |  | 1.098 | 1.0076 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202409 | 18L | Proposed | P1 | 15 | 2CLINTON | VH |  |  |  |  | 1.0976 | 1.0072 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202410 | 18L | Proposed | P1 | 15 | 2CLINTON_REA | VH |  |  |  |  | 1.098 | 1.0076 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202411 | 18L | Proposed | P1 | 15 | 2TEJAC | VH |  |  |  |  | 1.106 | 1.03 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202412 | 18L | Proposed | P1 | 15 | 2MARYDALE | VH |  |  |  |  | 1.1172 | 1.0359 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202413 | 18L | Proposed | P1 | 15 | 2FRANCIS! | VH |  |  |  |  | 1.1264 | 1.035 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202414 | 18L | Proposed | P1 | 15 | 2ANGOLA | VH |  |  |  |  | 1.1127 | 1.02 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202415 | 18L | Proposed | P1 | 15 | 2GRANT | VH |  |  |  |  | 1.126 | 1.0285 | 0.92 | 1.05 | 2045 | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 | 335795 |  |  |  | 69 | 69 | 351 | EES |  |  | 335795 2GRANT 69.0 335796 2PORT_HUD_B!69.0 1 |  |  | VH
202416 | 18L | Proposed | P1 | 15 | 3GMEADW! | VH |  |  |  |  | 1.1709 | 1.0242 | 0.92 | 1.05 | 2121 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202417 | 18L | Proposed | P1 | 15 | 3LEEVLL | VH |  |  |  |  | 1.1953 | 1.0174 | 0.92 | 1.05 | 2121 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202418 | 18L | Proposed | P1 | 15 | 3FOURCHN | VH |  |  |  |  | 1.195 | 1.0079 | 0.92 | 1.05 | 2121 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202419 | 18L | Proposed | P1 | 15 | 3CARLSL | VL |  |  |  |  | 0.883 | 0.9827 | 0.92 | 1.05 | 2131 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
202420 | 18L | Proposed | P1 | 15 | 3LUCKY | VH |  |  |  |  | 1.054 | 1.0405 | 0.92 | 1.05 | 2287 | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 |  |  | VH
202421 | 18L | Proposed | P1 | 15 | 3LUCKY | VH |  |  |  |  | 1.0546 | 1.0405 | 0.92 | 1.05 | 2288 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
202422 | 18L | Proposed | P1 | 15 | 3TX_EAST_E | VH |  |  |  |  | 1.0546 | 1.0377 | 0.92 | 1.05 | 2288 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337350 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
202423 | 18L | Proposed | P1 | 15 | 3DELHI_LA! | VH |  |  |  |  | 1.0714 | 1.026 | 0.92 | 1.05 | 2346 | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 |  |  | VH
202424 | 18L | Proposed | P1 | 15 | 3DELHI_LA! | VH |  |  |  |  | 1.0714 | 1.026 | 0.92 | 1.05 | 2350 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
202425 | 18L | Proposed | P1 | 15 | 3DELHI_RX | VH |  |  |  |  | 1.0714 | 1.0129 | 0.92 | 1.05 | 2350 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
202426 | 18L | Proposed | P1 | 15 | 3MINDEN_LG | VH |  |  |  |  | 1.0566 | 1.0356 | 0.92 | 1.05 | 2470 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 |  |  | VH
202427 | 18L | Proposed | P1 | 15 | 3MINDEN_LA! | VH |  |  |  |  | 1.0525 | 1.0368 | 0.92 | 1.05 | 2470 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 |  |  | VH
202428 | 18L | Proposed | P1 | 15 | 3LA_ORD_PLNT | VH |  |  |  |  | 1.0518 | 1.0361 | 0.92 | 1.05 | 2470 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 |  |  | VH
202429 | 18L | Proposed | P1 | 15 | 3ARCADIA | VH |  |  |  |  | 1.0712 | 1.032 | 0.92 | 1.05 | 2470 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | 337367 |  |  |  | 115 | 115 | 351 | EES |  |  | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 |  |  | VH
202430 | 18L | Proposed | P1 | 15 | 3BLACK_RIV | VH |  |  |  |  | 1.0906 | 0.9969 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202431 | 18L | Proposed | P1 | 15 | 3GILBERT | VH |  |  |  |  | 1.2269 | 1.0243 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202432 | 18L | Proposed | P1 | 15 | 3PERSIM_MIL | VH |  |  |  |  | 1.116 | 1.0243 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202433 | 18L | Proposed | P2 | 15 | 3NATCHEZSES% | VH |  |  |  |  | 1.1241 | 1.0345 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202434 | 18L | Proposed | P2 | 15 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1237 | 1.0346 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202435 | 18L | Proposed | P2 | 15 | 3PINE RIDGE | VH |  |  |  |  | 1.1236 | 1.0344 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202436 | 18L | Proposed | P2 | 15 | 3NATCHEZ! | VH |  |  |  |  | 1.1231 | 1.0352 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202437 | 18L | Proposed | P2 | 15 | 3J.MANVILLE | VH |  |  |  |  | 1.1213 | 1.0339 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202438 | 18L | Proposed | P2 | 15 | 3INTL PAPER | VH |  |  |  |  | 1.1204 | 1.0333 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202439 | 18L | Proposed | P2 | 15 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1197 | 1.0329 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202440 | 18L | Proposed | P2 | 15 | 3NATCHEZ IND | VH |  |  |  |  | 1.118 | 1.032 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202441 | 18L | Proposed | P2 | 15 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1156 | 1.0325 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202442 | 18L | Proposed | P2 | 15 | 3CROSBY+ | VH |  |  |  |  | 1.0934 | 1.0279 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202443 | 18L | Proposed | P2 | 15 | 3GLOSTER | VH |  |  |  |  | 1.0868 | 1.0268 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202444 | 18L | Proposed | P2 | 15 | 3LIBERTY P/L | VH |  |  |  |  | 1.0566 | 1.0359 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202445 | 18L | Proposed | P2 | 15 | 3WOODVILLE | VH |  |  |  |  | 1.0669 | 1.0055 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202446 | 18L | Proposed | P2 | 15 | 3LIBERTY! | VH |  |  |  |  | 1.0566 | 1.036 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202447 | 18L | Proposed | P2 | 15 | 3INTRSTE P/L | VH |  |  |  |  | 1.0566 | 1.036 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202448 | 18L | Proposed | P2 | 15 | 3KINGSTON MS | VH |  |  |  |  | 1.1144 | 1.0312 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202449 | 18L | Proposed | P2 | 15 | 3CENTREVILLE | VH |  |  |  |  | 1.0726 | 1.0117 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202450 | 18L | Proposed | P2 | 15 | 3WASHINGTON+ | VH |  |  |  |  | 1.1161 | 1.0334 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202451 | 18L | Proposed | P2 | 15 | 3ROXIE | VH |  |  |  |  | 1.0911 | 1.0327 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202452 | 18L | Proposed | P2 | 15 | 3MEADVILLE | VH |  |  |  |  | 1.0717 | 1.034 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202453 | 18L | Proposed | P2 | 15 | 3CRANFIELD+ | VH |  |  |  |  | 1.1073 | 1.0326 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202454 | 18L | Proposed | P2 | 15 | 3FAYETTE | VH |  |  |  |  | 1.1153 | 1.033 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202455 | 18L | Proposed | P2 | 15 | 3LORMAN+ | VH |  |  |  |  | 1.0962 | 1.0337 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202456 | 18L | Proposed | P2 | 15 | 3LORMAN | VH |  |  |  |  | 1.0961 | 1.0336 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202457 | 18L | Proposed | P2 | 15 | 3PORTGIBSON! | VH |  |  |  |  | 1.0834 | 1.0374 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202458 | 18L | Proposed | P2 | 15 | 3GGNS | VH |  |  |  |  | 1.0824 | 1.0364 | 0.975 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202459 | 18L | Proposed | P2 | 15 | 3BLACK_RIVER | VH |  |  |  |  | 1.0907 | 0.997 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202460 | 18L | Proposed | P2 | 15 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1151 | 1.024 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202461 | 18L | Proposed | P2 | 15 | 3PLANTATION! | VH |  |  |  |  | 1.1102 | 1.0279 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202462 | 18L | Proposed | P2 | 15 | 3VIDALIA_LA | VH |  |  |  |  | 1.112 | 1.0282 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202463 | 18L | Proposed | P2 | 15 | 3RED_GUM! | VH |  |  |  |  | 1.1367 | 1.0348 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202464 | 18L | Proposed | P2 | 15 | 3METROPOLIS | VH |  |  |  |  | 1.2148 | 1.0261 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202465 | 18L | Proposed | P2 | 15 | 3WISNER | VH |  |  |  |  | 1.2204 | 1.0255 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202466 | 18L | Proposed | P2 | 15 | 3WINNSBORO! | VH |  |  |  |  | 1.2422 | 1.0252 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202467 | 18L | Proposed | P2 | 15 | JNESVIL3 | VH |  |  |  |  | 1.0907 | 0.997 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202468 | 18L | Proposed | P2 | 15 | VIDALIA3 | VH |  |  |  |  | 1.1119 | 1.0282 | 0.92 | 1.05 | 2485 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
202469 | 18L | Proposed | P1 | 15 | 3BLACK_RIV | VL |  |  |  |  | 0.8324 | 0.9969 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202470 | 18L | Proposed | P1 | 15 | 3GILBERT | VL |  |  |  |  | 0.8053 | 1.0243 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202471 | 18L | Proposed | P1 | 15 | 3PERSIM_MIL | VL |  |  |  |  | 0.8653 | 1.0243 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202472 | 18L | Proposed | P1 | 15 | 3BASKIN | VL |  |  |  |  | 0.7875 | 1.0191 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202473 | 18L | Proposed | P1 | 15 | 3NATCHEZSES% | VL |  |  |  |  | 0.8932 | 1.0345 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202474 | 18L | Proposed | P1 | 15 | 3PINE RIDGE+ | VL |  |  |  |  | 0.8923 | 1.0346 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202475 | 18L | Proposed | P1 | 15 | 3PINE RIDGE | VL |  |  |  |  | 0.8921 | 1.0344 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202476 | 18L | Proposed | P1 | 15 | 3NATCHEZ! | VL |  |  |  |  | 0.8901 | 1.0352 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202477 | 18L | Proposed | P1 | 15 | 3J.MANVILLE | VL |  |  |  |  | 0.8867 | 1.0339 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202478 | 18L | Proposed | P1 | 15 | 3INTL PAPER | VL |  |  |  |  | 0.8844 | 1.0333 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202479 | 18L | Proposed | P1 | 15 | 3S.NATCHEZ! | VL |  |  |  |  | 0.8828 | 1.0329 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202480 | 18L | Proposed | P1 | 15 | 3NATCHEZ IND | VL |  |  |  |  | 0.8788 | 1.032 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202481 | 18L | Proposed | P1 | 15 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.8961 | 1.0325 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202482 | 18L | Proposed | P1 | 15 | 3WOODVILLE | VL |  |  |  |  | 0.9095 | 1.0055 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202483 | 18L | Proposed | P1 | 15 | 3KINGSTON MS | VL |  |  |  |  | 0.8946 | 1.0312 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202484 | 18L | Proposed | P1 | 15 | 3CENTREVILLE | VL |  |  |  |  | 0.9164 | 1.0117 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202485 | 18L | Proposed | P1 | 15 | 3WASHINGTON+ | VL |  |  |  |  | 0.9013 | 1.0334 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202486 | 18L | Proposed | P1 | 15 | 3CRANFIELD+ | VL |  |  |  |  | 0.9116 | 1.0326 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202487 | 18L | Proposed | P1 | 15 | 3FAYETTE | VL |  |  |  |  | 0.9187 | 1.033 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202488 | 18L | Proposed | P1 | 15 | 3GGNS | VL |  |  |  |  | 0.9553 | 1.0364 | 0.975 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202489 | 18L | Proposed | P1 | 15 | 3BLACK_RIVER | VL |  |  |  |  | 0.8324 | 0.997 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202490 | 18L | Proposed | P1 | 15 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8651 | 1.024 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202491 | 18L | Proposed | P1 | 15 | 3PLANTATION! | VL |  |  |  |  | 0.8729 | 1.0279 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202492 | 18L | Proposed | P1 | 15 | 3VIDALIA_LA | VL |  |  |  |  | 0.8736 | 1.0282 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202493 | 18L | Proposed | P1 | 15 | 3RED_GUM! | VL |  |  |  |  | 0.8746 | 1.0348 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202494 | 18L | Proposed | P1 | 15 | 3METROPOLIS | VL |  |  |  |  | 0.819 | 1.0261 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202495 | 18L | Proposed | P1 | 15 | 3WISNER | VL |  |  |  |  | 0.8156 | 1.0255 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202496 | 18L | Proposed | P1 | 15 | 3WINNSBORO! | VL |  |  |  |  | 0.7907 | 1.0252 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202497 | 18L | Proposed | P1 | 15 | JNESVIL3 | VL |  |  |  |  | 0.8324 | 0.997 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202498 | 18L | Proposed | P1 | 15 | VIDALIA3 | VL |  |  |  |  | 0.8736 | 1.0282 | 0.92 | 1.05 | 2486 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202499 | 18L | Proposed | P1 | 15 | PNPRARIE 4 | VL |  |  |  |  | 0.9173 | 1.0029 | 0.92 | 1.05 | 2639 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202500 | 18L | Proposed | P1 | 15 | ELKS 6 | VL |  |  |  |  | 0.9004 | 1.0081 | 0.92 | 1.05 | 2749 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
202501 | 18L | Proposed | P1 | 15 | 7FLETCH | VH |  |  |  |  | 1.0632 | 1.0469 | 0.92 | 1.05 | 2760 | 3Wnd: OPEN B$0909 FLETCHE1 1 | 300040 |  |  |  | 345 | 345 | 330 | AECI |  |  | 3Wnd: OPEN B$0909 FLETCHE1 1 |  |  | VH
202502 | 18L | Proposed | P1 | 15 | 7SALEM | VH |  |  |  |  | 1.0578 | 1.0473 | 0.92 | 1.05 | 2760 | 3Wnd: OPEN B$0909 FLETCHE1 1 | 300047 |  |  |  | 345 | 345 | 330 | AECI |  |  | 3Wnd: OPEN B$0909 FLETCHE1 1 |  |  | VH
202503 | 18L | Proposed | P1 | 15 | 7STFRAN | VH |  |  |  |  | 1.0743 | 1.0473 | 0.92 | 1.05 | 2767 | 300046 7NEWMAD 345 300048 7STFRAN 345 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 300048 7STFRAN 345 1 |  |  | VH
202504 | 18L | Proposed | P1 | 15 | 7GOBKNOB | VH |  |  |  |  | 1.0724 | 1.0515 | 0.92 | 1.05 | 2767 | 300046 7NEWMAD 345 300048 7STFRAN 345 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 300048 7STFRAN 345 1 |  |  | VH
202505 | 18L | Proposed | P1 | 15 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.0462 | 0.92 | 1.05 | 2768 | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 |  |  | VH
202506 | 18L | Proposed | P1 | 15 | 7WNEWMADRID | VH |  |  |  |  | 1.0545 | 1.0373 | 0.92 | 1.05 | 2768 | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300046 7NEWMAD 345 301407 7WNEWMADRID 345 1 |  |  | VH
202507 | 18L | Proposed | P1 | 15 | 8NEWMAD | VH |  |  |  |  | 1.0585 | 1.0463 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202508 | 18L | Proposed | P1 | 15 | 7ESSEX | VH |  |  |  |  | 1.0571 | 1.0462 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202509 | 18L | Proposed | P1 | 15 | 7NEWMAD | VH |  |  |  |  | 1.0549 | 1.0372 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202510 | 18L | Proposed | P1 | 15 | 7STFRAN | VH |  |  |  |  | 1.0611 | 1.0473 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202511 | 18L | Proposed | P1 | 15 | 7GOBKNOB | VH |  |  |  |  | 1.062 | 1.0515 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202512 | 18L | Proposed | P1 | 15 | 8WNEWMADRID | VH |  |  |  |  | 1.0585 | 1.0462 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202513 | 18L | Proposed | P1 | 15 | 7WNEWMADRID | VH |  |  |  |  | 1.0549 | 1.0373 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202514 | 18L | Proposed | P1 | 15 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0714 | 0.92 | 1.05 | 2775 | Unit:300007 1NM G2 22.0 Id:1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | Unit:300007 1NM G2 22.0 Id:1 |  |  | VH
202515 | 18L | Proposed | P1 | 15 | 7BLACKBERRY | VH |  |  |  |  | 1.0502 | 1.0389 | 0.92 | 1.05 | 2791 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 300739 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 |  |  | VH
202516 | 18L | Proposed | P1 | 15 | 7SPORTSMAN | VH |  |  |  |  | 1.0524 | 1.0127 | 0.92 | 1.05 | 2791 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 300740 |  |  |  | 345 | 345 | 330 | AECI |  |  | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 |  |  | VH
202517 | 18L | Proposed | P1 | 15 | 8THALMANN | VH |  |  |  |  | 1.0577 | 1.0473 | 0.92 | 1.05 | 2818 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
202518 | 18L | Proposed | P1 | 15 | 8MCCALL RD | VH |  |  |  |  | 1.0725 | 1.0368 | 0.92 | 1.05 | 2818 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
202519 | 18L | Proposed | P1 | 15 | 8FORTSON | VH |  |  |  |  | 1.0595 | 1.0402 | 0.92 | 1.05 | 2820 | 380010 8FORTSON 500 380125 6FORTSON 230 1 | 380010 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380010 8FORTSON 500 380125 6FORTSON 230 1 |  |  | VH
202520 | 18L | Proposed | P1 | 15 | 8TENASKA GA | VH |  |  |  |  | 1.0541 | 1.0379 | 0.92 | 1.05 | 3334 | 383033 8TENASKA GA 500 383034 8HEARD CO 500 Z1 | 383033 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 383033 8TENASKA GA 500 383034 8HEARD CO 500 Z1 |  |  | VH
202521 | 18L | Proposed | P1 | 15 | 8CLAY 8 | VH |  |  |  |  | 1.0667 | 1.0377 | 0.92 | 1.05 | 3348 | 384157 8MILLER8 500 385312 8CLAY 8 500 1 | 385312 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 384157 8MILLER8 500 385312 8CLAY 8 500 1 |  |  | VH
202522 | 18L | Proposed | P1 | 15 | 8DANIEL | VH |  |  |  |  | 1.0812 | 1.0287 | 0.92 | 1.05 | 3532 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
202523 | 18L | Proposed | P1 | 15 | 8E POINT AL | VH |  |  |  |  | 1.0616 | 1.0416 | 0.92 | 1.05 | 3630 | 360058 8E POINT AL 500 384157 8MILLER8 500 1 | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360058 8E POINT AL 500 384157 8MILLER8 500 1 |  |  | VH
202524 | 18L | Proposed | P1 | 15 | 8SHAWNEE FP | VH |  |  |  |  | 1.1078 | 1.0839 | 0.92 | 1.05 | 3644 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
202525 | 18L | Proposed | P1 | 15 | 7SHAWNEE FP | VH |  |  |  |  | 1.0609 | 1.0766 | 0.92 | 1.05 | 3644 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
202526 | 18L | Proposed | P1 | 15 | 8MARSHALL KY | VH |  |  |  |  | 1.1021 | 1.0819 | 0.92 | 1.05 | 3644 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
202527 | 18L | Proposed | P1 | 15 | 8MARSHALL KY | VH |  |  |  |  | 1.0695 | 1.0819 | 0.92 | 1.05 | 3651 | 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  | VH
202528 | 18L | Proposed | P1 | 15 | 8LAG CRK CT | VH |  |  |  |  | 1.0574 | 1.0725 | 0.92 | 1.05 | 3652 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202529 | 18L | Proposed | P1 | 15 | 8LAG CRK CC | VH |  |  |  |  | 1.0574 | 1.0725 | 0.92 | 1.05 | 3652 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202530 | 18L | Proposed | P1 | 15 | 8WEAKLEY TN | VH |  |  |  |  | 1.062 | 1.0785 | 0.92 | 1.05 | 3653 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 |  |  | VH
202531 | 18L | Proposed | P1 | 15 | 8GLEASON CT | VH |  |  |  |  | 1.091 | 1.0808 | 0.92 | 1.05 | 3653 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 |  |  | VH
202532 | 18L | Proposed | P1 | 15 | 8WEAKLEY TN | VH |  |  |  |  | 1.089 | 1.0785 | 0.92 | 1.05 | 3654 | 3Wnd: OPEN B$0188 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0188 1 |  |  | VH
202533 | 18L | Proposed | P1 | 15 | 8HAYWOOD TN | VH |  |  |  |  | 1.0506 | 1.0656 | 0.92 | 1.05 | 3655 | 360019 8JACKSON TN 500 360037 8JVILLE FP 500 1 | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360019 8JACKSON TN 500 360037 8JVILLE FP 500 1 |  |  | VH
202534 | 18L | Proposed | P1 | 15 | 8WEAKLEY TN | VH |  |  |  |  | 1.0925 | 1.0785 | 0.92 | 1.05 | 3661 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202535 | 18L | Proposed | P1 | 15 | 8LAG CRK CT | VH |  |  |  |  | 1.0997 | 1.0725 | 0.92 | 1.05 | 3661 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202536 | 18L | Proposed | P1 | 15 | 8GLEASON CT | VH |  |  |  |  | 1.0926 | 1.0808 | 0.92 | 1.05 | 3661 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202537 | 18L | Proposed | P1 | 15 | 8LAG CRK CC | VH |  |  |  |  | 1.0997 | 1.0725 | 0.92 | 1.05 | 3661 | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360021 8SHELBY TN 500 360568 8LAG CRK CT 500 1 |  |  | VH
202538 | 18L | Proposed | P1 | 15 | 5HORN LAKE% | VH |  |  |  |  | 1.0535 | 1.0684 | 0.92 | 1.05 | 3664 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 |  |  | VH
202539 | 18L | Proposed | P1 | 15 | 8PLEASANT HL | VH |  |  |  |  | 1.0691 | 1.053 | 0.92 | 1.05 | 3676 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | VH
202540 | 18L | Proposed | P1 | 15 | 8BENTON MS | VH |  |  |  |  | 1.0674 | 1.0569 | 0.92 | 1.05 | 3676 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | VH
202541 | 18L | Proposed | P1 | 15 | 8MAGNOL CC1 | VH |  |  |  |  | 1.0674 | 1.0569 | 0.92 | 1.05 | 3676 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | VH
202542 | 18L | Proposed | P1 | 15 | 8MAGNOL CC2 | VH |  |  |  |  | 1.0674 | 1.0569 | 0.92 | 1.05 | 3676 | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360033 8UNION MS 500 360541 8PLEASANT HL 500 1 |  |  | VH
202543 | 18L | Proposed | P1 | 15 | 8WEAKLEY TN | VH |  |  |  |  | 1.0654 | 1.0785 | 0.92 | 1.05 | 3684 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 |  |  | VH
202544 | 18L | Proposed | P1 | 15 | 8GLEASON CT | VH |  |  |  |  | 1.0658 | 1.0808 | 0.92 | 1.05 | 3684 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 |  |  | VH
202545 | 18L | Proposed | P1 | 15 | 8PARADISE FP | VH |  |  |  |  | 1.0758 | 1.0873 | 0.92 | 1.05 | 3685 | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 |  |  | VH
202546 | 18L | Proposed | P1 | 15 | 8MONTGOMERY | VH |  |  |  |  | 1.0694 | 1.0808 | 0.92 | 1.05 | 3685 | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360040 8CUMBERLAND 500 360044 8MONTGOMERY 500 1 |  |  | VH
202547 | 18L | Proposed | P1 | 15 | 8PARADISE FP | VH |  |  |  |  | 1.0975 | 1.0873 | 0.92 | 1.05 | 3691 | 3Wnd: OPEN B$0195 1 | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0195 1 |  |  | VH
202548 | 18L | Proposed | P1 | 15 | 8MONTGOMERY | VH |  |  |  |  | 1.091 | 1.0808 | 0.92 | 1.05 | 3691 | 3Wnd: OPEN B$0195 1 | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0195 1 |  |  | VH
202549 | 18L | Proposed | P1 | 15 | 8RUTHERFORD | VH |  |  |  |  | 1.0559 | 1.0689 | 0.92 | 1.05 | 3692 | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 |  |  | VH
202550 | 18L | Proposed | P1 | 15 | 8MAURY TN | VH |  |  |  |  | 1.0535 | 1.0682 | 0.92 | 1.05 | 3692 | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360048 8DAVIDSON TN 500 360050 8MAURY TN 500 1 |  |  | VH
202551 | 18L | Proposed | P1 | 15 | 8PLATEAU TN | VH |  |  |  |  | 1.0715 | 1.0613 | 0.92 | 1.05 | 3712 | 360077 8PLATEAU TN 500 360090 8ROANE TN 500 1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360077 8PLATEAU TN 500 360090 8ROANE TN 500 1 |  |  | VH
202552 | 18L | Proposed | P1 | 15 | 8PLATEAU TN | VH |  |  |  |  | 1.0733 | 1.0613 | 0.92 | 1.05 | 3713 | 3Wnd: OPEN B$0033 1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0033 1 |  |  | VH
202553 | 18L | Proposed | P1 | 15 | 8SULLIVAN TN | VH |  |  |  |  | 1.0738 | 1.0612 | 0.92 | 1.05 | 3729 | 3Wnd: OPEN B$0258 2 | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | 3Wnd: OPEN B$0258 2 |  |  | VH
202554 | 18L | Proposed | P1 | 15 | 8CHOCTAW CC | VH |  |  |  |  | 1.0528 | 1.0348 | 0.92 | 1.05 | 3756 | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 | 360627 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 |  |  | VH
202555 | 18L | Proposed | P1 | 15 | 8CHOCTAW MS | VH |  |  |  |  | 1.0528 | 1.0347 | 0.92 | 1.05 | 3756 | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 | 360654 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360631 8FRENCH CAMP 500 360654 8CHOCTAW MS 500 1 |  |  | VH
202556 | 18L | Proposed | P1 | 15 | 8FRANKLIN TN | VH |  |  |  |  | 1.0625 | 1.0523 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202557 | 18L | Proposed | P1 | 15 | 8SEQUOYAH NP | VH |  |  |  |  | 1.0565 | 1.04 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360081 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202558 | 18L | Proposed | P1 | 15 | 8WBNP #1 | VH |  |  |  |  | 1.057 | 1.042 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202559 | 18L | Proposed | P1 | 15 | 8ROANE TN | VH |  |  |  |  | 1.0625 | 1.0497 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202560 | 18L | Proposed | P1 | 15 | 8BULL RUN FP | VH |  |  |  |  | 1.0641 | 1.0512 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202561 | 18L | Proposed | P1 | 15 | 8VOLUNTEER | VH |  |  |  |  | 1.0689 | 1.0565 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202562 | 18L | Proposed | P1 | 15 | 8HIWASSEE TN | VH |  |  |  |  | 1.0572 | 1.0416 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360110 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202563 | 18L | Proposed | P1 | 15 | 8BRADLEY TN | VH |  |  |  |  | 1.052 | 1.0367 | 0.92 | 1.05 | 3771 | Unit:364011 1SEQUOYAH N124.0 Id:1 | 360662 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364011 1SEQUOYAH N124.0 Id:1 |  |  | VH
202564 | 18L | Proposed | P1 | 15 | 8PLATEAU TN | VH |  |  |  |  | 1.0745 | 1.0613 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202565 | 18L | Proposed | P1 | 15 | 8SEQUOYAH NP | VH |  |  |  |  | 1.0513 | 1.04 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360081 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202566 | 18L | Proposed | P1 | 15 | 8WBNP #1 | VH |  |  |  |  | 1.0627 | 1.042 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202567 | 18L | Proposed | P1 | 15 | 8ROANE TN | VH |  |  |  |  | 1.0675 | 1.0497 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202568 | 18L | Proposed | P1 | 15 | 8BULL RUN FP | VH |  |  |  |  | 1.0694 | 1.0512 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202569 | 18L | Proposed | P1 | 15 | 8VOLUNTEER | VH |  |  |  |  | 1.0738 | 1.0565 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202570 | 18L | Proposed | P1 | 15 | 8HIWASSEE TN | VH |  |  |  |  | 1.0573 | 1.0416 | 0.92 | 1.05 | 3773 | Unit:364021 1WBNP N1 24.0 Id:1 | 360110 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364021 1WBNP N1 24.0 Id:1 |  |  | VH
202571 | 18L | Proposed | P1 | 15 | 8WBNP #1 | VH |  |  |  |  | 1.0545 | 1.042 | 0.92 | 1.05 | 3774 | Unit:364022 1WBNP N2 24.0 Id:2 | 360085 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
202572 | 18L | Proposed | P1 | 15 | 8ROANE TN | VH |  |  |  |  | 1.0608 | 1.0497 | 0.92 | 1.05 | 3774 | Unit:364022 1WBNP N2 24.0 Id:2 | 360090 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
202573 | 18L | Proposed | P1 | 15 | 8BULL RUN FP | VH |  |  |  |  | 1.0624 | 1.0512 | 0.92 | 1.05 | 3774 | Unit:364022 1WBNP N2 24.0 Id:2 | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
202574 | 18L | Proposed | P1 | 15 | 8VOLUNTEER | VH |  |  |  |  | 1.0674 | 1.0565 | 0.92 | 1.05 | 3774 | Unit:364022 1WBNP N2 24.0 Id:2 | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | Unit:364022 1WBNP N2 24.0 Id:2 |  |  | VH
202575 | 18L | Proposed | P1 | 15 | 8PHIPPS B NP | VH |  |  |  |  | 1.0562 | 1.0678 | 0.92 | 1.05 | 3890 | 324073 8POCKETN 500 360102 8PHIPPS B NP 500 1 | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | 324073 8POCKETN 500 360102 8PHIPPS B NP 500 1 |  |  | VH
202576 | 18L | Proposed | P1 | 15 | 8SHAWNEE FP | VH |  |  |  |  | 1.0969 | 1.0839 | 0.92 | 1.05 | 3892 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
202577 | 18L | Proposed | P1 | 15 | 7SHAWNEE FP | VH |  |  |  |  | 1.094 | 1.0766 | 0.92 | 1.05 | 3892 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
202578 | 18L | Proposed | P1 | 15 | 8MARSHALL KY | VH |  |  |  |  | 1.0923 | 1.0819 | 0.92 | 1.05 | 3892 | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | 347325 7JOPPA TS 345 360002 7SHAWNEE FP 345 1 |  |  | VH
202579 | 18L | Proposed | P1 | 15 | TENRUSK7 | VH |  |  |  |  | 1.0566 | 1.0205 | 0.92 | 1.05 | 4184 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
202580 | 18L | Proposed | P1 | 15 | TENGEN 7 | VH |  |  |  |  | 1.0566 | 1.0205 | 0.92 | 1.05 | 4184 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
202581 | 18L | Proposed | P1 | 15 | ELKCITY7 | VH |  |  |  |  | 1.0575 | 1.035 | 0.92 | 1.05 | 4225 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
202582 | 18L | Proposed | P1 | 15 | GRACMNT7 | VH |  |  |  |  | 1.0521 | 1.0291 | 0.92 | 1.05 | 4282 | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 515800 |  |  |  | 345 | 345 | 524 | OKGE |  |  | 514801 MINCO 7 345 515800 GRACMNT7 345 1 |  |  | VH
202583 | 18L | Proposed | P1 | 15 | FTSMITH7 | VH |  |  |  |  | 1.0539 | 1.0376 | 0.92 | 1.05 | 4325 | 3Wnd: OPEN B$0929 FTSMITH1 1 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | 3Wnd: OPEN B$0929 FTSMITH1 1 |  |  | VH
202584 | 18L | Proposed | P0 | 16 | 8GPDELL | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
202585 | 18L | Proposed | P0 | 16 | 7GOBKNOB | VH |  |  |  |  | 1.0515 | 1.0515 | 0.92 | 1.05 | 0 | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
202586 | 18L | Proposed | P0 | 16 | 2BATSON! | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 | 0 | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
202587 | 18L | Proposed | P0 | 16 | 5HORN LAKE% | VH |  |  |  |  | 1.0684 | 1.0684 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202588 | 18L | Proposed | P0 | 16 | 8DELL% | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202589 | 18L | Proposed | P0 | 16 | 8SANS SOUCI% | VH |  |  |  |  | 1.0625 | 1.0625 | 0.92 | 1.05 | 0 | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202590 | 18L | Proposed | P0 | 16 | 3PARAGOULD! | VH |  |  |  |  | 1.061 | 1.061 | 0.92 | 1.05 | 0 | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202591 | 18L | Proposed | P0 | 16 | 3SEDGWICK | VH |  |  |  |  | 1.0506 | 1.0506 | 0.92 | 1.05 | 0 | ** Base Case ** | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202592 | 18L | Proposed | P0 | 16 | 3DATTO | VH |  |  |  |  | 1.0518 | 1.0518 | 0.92 | 1.05 | 0 | ** Base Case ** | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202593 | 18L | Proposed | P0 | 16 | 2BLACK ROCK | VH |  |  |  |  | 1.0714 | 1.0714 | 0.92 | 1.05 | 0 | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202594 | 18L | Proposed | P0 | 16 | 2OPPELLO | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202595 | 18L | Proposed | P0 | 16 | 2WARD | VH |  |  |  |  | 1.0603 | 1.0603 | 0.92 | 1.05 | 0 | ** Base Case ** | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202596 | 18L | Proposed | P0 | 16 | 5DELL# | VH |  |  |  |  | 1.0566 | 1.0566 | 0.92 | 1.05 | 0 | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202597 | 18L | Proposed | P0 | 16 | 3LIGHT# | VH |  |  |  |  | 1.0539 | 1.0539 | 0.92 | 1.05 | 0 | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202598 | 18L | Proposed | P0 | 16 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0571 | 1.0571 | 0.92 | 1.05 | 0 | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
202599 | 18L | Proposed | P0 | 16 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 | 0 | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202600 | 18L | Proposed | P0 | 16 | 7SHAWNEE FP | VH |  |  |  |  | 1.0766 | 1.0766 | 0.92 | 1.05 | 0 | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202601 | 18L | Proposed | P0 | 16 | 8RUTHERFORD | VH |  |  |  |  | 1.0689 | 1.0689 | 0.92 | 1.05 | 0 | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202602 | 18L | Proposed | P0 | 16 | 8MARSHALL KY | VH |  |  |  |  | 1.0819 | 1.0819 | 0.92 | 1.05 | 0 | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202603 | 18L | Proposed | P0 | 16 | 8WEAKLEY TN | VH |  |  |  |  | 1.0785 | 1.0785 | 0.92 | 1.05 | 0 | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202604 | 18L | Proposed | P0 | 16 | 8JACKSON TN | VH |  |  |  |  | 1.0673 | 1.0673 | 0.92 | 1.05 | 0 | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202605 | 18L | Proposed | P0 | 16 | 8SHELBY TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202606 | 18L | Proposed | P0 | 16 | 8CORDOVA TN | VH |  |  |  |  | 1.0568 | 1.0568 | 0.92 | 1.05 | 0 | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202607 | 18L | Proposed | P0 | 16 | 8UNION MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202608 | 18L | Proposed | P0 | 16 | 8JVILLE FP | VH |  |  |  |  | 1.0829 | 1.0829 | 0.92 | 1.05 | 0 | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202609 | 18L | Proposed | P0 | 16 | 8CUMBERLAND | VH |  |  |  |  | 1.0876 | 1.0876 | 0.92 | 1.05 | 0 | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202610 | 18L | Proposed | P0 | 16 | 8PARADISE FP | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 | 0 | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202611 | 18L | Proposed | P0 | 16 | 8MONTGOMERY | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202612 | 18L | Proposed | P0 | 16 | 8DAVIDSON TN | VH |  |  |  |  | 1.0799 | 1.0799 | 0.92 | 1.05 | 0 | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202613 | 18L | Proposed | P0 | 16 | 8MAURY TN | VH |  |  |  |  | 1.0682 | 1.0682 | 0.92 | 1.05 | 0 | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202614 | 18L | Proposed | P0 | 16 | 8FRANKLIN TN | VH |  |  |  |  | 1.0523 | 1.0523 | 0.92 | 1.05 | 0 | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202615 | 18L | Proposed | P0 | 16 | 8WILSON TN | VH |  |  |  |  | 1.077 | 1.077 | 0.92 | 1.05 | 0 | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202616 | 18L | Proposed | P0 | 16 | 8PLATEAU TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 | 0 | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202617 | 18L | Proposed | P0 | 16 | 8BULL RUN FP | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 | 0 | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202618 | 18L | Proposed | P0 | 16 | 8VOLUNTEER | VH |  |  |  |  | 1.0565 | 1.0565 | 0.92 | 1.05 | 0 | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202619 | 18L | Proposed | P0 | 16 | 8PHIPPS B NP | VH |  |  |  |  | 1.0678 | 1.0678 | 0.92 | 1.05 | 0 | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202620 | 18L | Proposed | P0 | 16 | 8SULLIVAN TN | VH |  |  |  |  | 1.0612 | 1.0612 | 0.92 | 1.05 | 0 | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202621 | 18L | Proposed | P0 | 16 | 8PLEASANT HL | VH |  |  |  |  | 1.053 | 1.053 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202622 | 18L | Proposed | P0 | 16 | 8HAYWOOD TN | VH |  |  |  |  | 1.0656 | 1.0656 | 0.92 | 1.05 | 0 | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202623 | 18L | Proposed | P0 | 16 | 8LAG CRK CT | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202624 | 18L | Proposed | P0 | 16 | 8PIN HOOK TN | VH |  |  |  |  | 1.0778 | 1.0778 | 0.92 | 1.05 | 0 | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202625 | 18L | Proposed | P0 | 16 | 8GLEASON CT | VH |  |  |  |  | 1.0808 | 1.0808 | 0.92 | 1.05 | 0 | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202626 | 18L | Proposed | P0 | 16 | 8BENTON MS | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202627 | 18L | Proposed | P0 | 16 | 8MAGNOL CC1 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202628 | 18L | Proposed | P0 | 16 | 8MAGNOL CC2 | VH |  |  |  |  | 1.0569 | 1.0569 | 0.92 | 1.05 | 0 | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202629 | 18L | Proposed | P0 | 16 | 8LAG CRK CC | VH |  |  |  |  | 1.0725 | 1.0725 | 0.92 | 1.05 | 0 | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202630 | 18S | Proposed | P0 | 17 | 2WEIRGAT | VL |  |  |  |  | 0.9182 | 0.9182 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202631 | 18S | Proposed | P0 | 17 | 5HORN LAKE% | VH |  |  |  |  | 1.0572 | 1.0572 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202632 | 18S | Proposed | P0 | 17 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202633 | 18S | Proposed | P0 | 17 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202634 | 18S | Proposed | P0 | 17 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
202635 | 18S | Proposed | P1 | 17 | 2PINELND | VL |  |  |  |  | 0.9198 | 0.9319 | 0.92 | 1.05 | 24 | G-334282-1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202636 | 18S | Proposed | P1 | 17 | 2TEMPL1* | VL |  |  |  |  | 0.9179 | 0.93 | 0.92 | 1.05 | 24 | G-334282-1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202637 | 18S | Proposed | P1 | 17 | 2TEMPLE1 | VL |  |  |  |  | 0.9176 | 0.9296 | 0.92 | 1.05 | 24 | G-334282-1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202638 | 18S | Proposed | P1 | 17 | 2TEMPL2* | VL |  |  |  |  | 0.9176 | 0.9297 | 0.92 | 1.05 | 24 | G-334282-1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202639 | 18S | Proposed | P1 | 17 | 2TEMPLE2 | VL |  |  |  |  | 0.9174 | 0.9295 | 0.92 | 1.05 | 24 | G-334282-1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202640 | 18S | Proposed | P1 | 17 | 2TMPLSWC | VL |  |  |  |  | 0.9175 | 0.9296 | 0.92 | 1.05 | 24 | G-334282-1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202641 | 18S | Proposed | P1 | 17 | 2WEIRGAT | VL |  |  |  |  | 0.906 | 0.9182 | 0.92 | 1.05 | 24 | G-334282-1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202642 | 18S | Proposed | P1 | 17 | 3GILBERT | VH |  |  |  |  | 1.054 | 1.0325 | 0.92 | 1.05 | 352 | P1_2-116 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202643 | 18S | Proposed | P1 | 17 | 3NATCHEZSES% | VH |  |  |  |  | 1.0586 | 1.0378 | 0.92 | 1.05 | 352 | P1_2-116 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202644 | 18S | Proposed | P1 | 17 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0581 | 1.0375 | 0.92 | 1.05 | 352 | P1_2-116 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202645 | 18S | Proposed | P1 | 17 | 3PINE RIDGE | VH |  |  |  |  | 1.0578 | 1.0372 | 0.92 | 1.05 | 352 | P1_2-116 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202646 | 18S | Proposed | P1 | 17 | 3NATCHEZ! | VH |  |  |  |  | 1.0574 | 1.0372 | 0.92 | 1.05 | 352 | P1_2-116 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202647 | 18S | Proposed | P1 | 17 | 3J.MANVILLE | VH |  |  |  |  | 1.0551 | 1.0347 | 0.92 | 1.05 | 352 | P1_2-116 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202648 | 18S | Proposed | P1 | 17 | 3INTL PAPER | VH |  |  |  |  | 1.0539 | 1.034 | 0.92 | 1.05 | 352 | P1_2-116 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202649 | 18S | Proposed | P1 | 17 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0531 | 1.0334 | 0.92 | 1.05 | 352 | P1_2-116 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202650 | 18S | Proposed | P1 | 17 | 3NATCHEZ IND | VH |  |  |  |  | 1.0516 | 1.0322 | 0.92 | 1.05 | 352 | P1_2-116 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202651 | 18S | Proposed | P1 | 17 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0512 | 1.0327 | 0.92 | 1.05 | 352 | P1_2-116 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202652 | 18S | Proposed | P1 | 17 | 3WASHINGTON+ | VH |  |  |  |  | 1.0537 | 1.0341 | 0.92 | 1.05 | 352 | P1_2-116 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202653 | 18S | Proposed | P1 | 17 | 3FAYETTE | VH |  |  |  |  | 1.0646 | 1.0466 | 0.92 | 1.05 | 352 | P1_2-116 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202654 | 18S | Proposed | P1 | 17 | 3LORMAN+ | VH |  |  |  |  | 1.0568 | 1.0407 | 0.92 | 1.05 | 352 | P1_2-116 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202655 | 18S | Proposed | P1 | 17 | 3LORMAN | VH |  |  |  |  | 1.0566 | 1.0405 | 0.92 | 1.05 | 352 | P1_2-116 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202656 | 18S | Proposed | P1 | 17 | 3PORTGIBSON! | VH |  |  |  |  | 1.0549 | 1.0407 | 0.92 | 1.05 | 352 | P1_2-116 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202657 | 18S | Proposed | P1 | 17 | 3GGNS | VH |  |  |  |  | 1.0539 | 1.0397 | 0.975 | 1.05 | 352 | P1_2-116 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202658 | 18S | Proposed | P1 | 17 | 3RED_GUM! | VH |  |  |  |  | 1.065 | 1.0352 | 0.92 | 1.05 | 352 | P1_2-116 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202659 | 18S | Proposed | P1 | 17 | 3METROPOLIS | VH |  |  |  |  | 1.0628 | 1.0393 | 0.92 | 1.05 | 352 | P1_2-116 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202660 | 18S | Proposed | P1 | 17 | 3WISNER | VH |  |  |  |  | 1.0629 | 1.0398 | 0.92 | 1.05 | 352 | P1_2-116 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
202661 | 18S | Proposed | P1 | 17 | 2SINHERN | VH |  |  |  |  | 1.0577 | 1.0151 | 0.92 | 1.05 | 360 | P1_2-124 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
202662 | 18S | Proposed | P1 | 17 | 2HEARNE! | VH |  |  |  |  | 1.0697 | 1.0286 | 0.92 | 1.05 | 360 | P1_2-124 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
202663 | 18S | Proposed | P1 | 17 | 2TXHEARN | VH |  |  |  |  | 1.0683 | 1.0285 | 0.92 | 1.05 | 360 | P1_2-124 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
202664 | 18S | Proposed | P1 | 17 | 2APLHERN | VH |  |  |  |  | 1.0647 | 1.0284 | 0.92 | 1.05 | 360 | P1_2-124 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
202665 | 18S | Proposed | P1 | 17 | 2PINELND | VL |  |  |  |  | 0.8917 | 0.9319 | 0.92 | 1.05 | 472 | P1_2-237 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202666 | 18S | Proposed | P1 | 17 | 2TEMPL1* | VL |  |  |  |  | 0.8898 | 0.93 | 0.92 | 1.05 | 472 | P1_2-237 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202667 | 18S | Proposed | P1 | 17 | 2TEMPLE1 | VL |  |  |  |  | 0.8894 | 0.9296 | 0.92 | 1.05 | 472 | P1_2-237 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202668 | 18S | Proposed | P1 | 17 | 2TEMPL2* | VL |  |  |  |  | 0.8895 | 0.9297 | 0.92 | 1.05 | 472 | P1_2-237 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202669 | 18S | Proposed | P1 | 17 | 2TEMPLE2 | VL |  |  |  |  | 0.8893 | 0.9295 | 0.92 | 1.05 | 472 | P1_2-237 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202670 | 18S | Proposed | P1 | 17 | 2TMPLSWC | VL |  |  |  |  | 0.8893 | 0.9296 | 0.92 | 1.05 | 472 | P1_2-237 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202671 | 18S | Proposed | P1 | 17 | 2WEIRGAT | VL |  |  |  |  | 0.8775 | 0.9182 | 0.92 | 1.05 | 472 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202672 | 18S | Proposed | P1 | 17 | 2PINELND | VL |  |  |  |  | 0.8729 | 0.9319 | 0.92 | 1.05 | 474 | P1_2-239 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202673 | 18S | Proposed | P1 | 17 | 2TEMPL1* | VL |  |  |  |  | 0.8709 | 0.93 | 0.92 | 1.05 | 474 | P1_2-239 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202674 | 18S | Proposed | P1 | 17 | 2TEMPLE1 | VL |  |  |  |  | 0.8706 | 0.9296 | 0.92 | 1.05 | 474 | P1_2-239 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202675 | 18S | Proposed | P1 | 17 | 2TEMPL2* | VL |  |  |  |  | 0.8706 | 0.9297 | 0.92 | 1.05 | 474 | P1_2-239 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202676 | 18S | Proposed | P1 | 17 | 2TEMPLE2 | VL |  |  |  |  | 0.8704 | 0.9295 | 0.92 | 1.05 | 474 | P1_2-239 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202677 | 18S | Proposed | P1 | 17 | 2TMPLSWC | VL |  |  |  |  | 0.8705 | 0.9296 | 0.92 | 1.05 | 474 | P1_2-239 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202678 | 18S | Proposed | P1 | 17 | 2WEIRGAT | VL |  |  |  |  | 0.8584 | 0.9182 | 0.92 | 1.05 | 474 | P1_2-239 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202679 | 18S | Proposed | P1 | 17 | 2ANGOLA | VL |  |  |  |  | 0.8912 | 0.9942 | 0.92 | 1.05 | 997 | P1_2-764 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-764 |  | None
202680 | 18S | Proposed | P1 | 17 | 3MCCALL! | VH |  |  |  |  | 1.0514 | 1.0201 | 0.92 | 1.05 | 1026 | P1_2-793 | 336016 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-793 |  |  | VH
202681 | 18S | Proposed | P1 | 17 | 3PVILLE! | VH |  |  |  |  | 1.0536 | 1.0152 | 0.92 | 1.05 | 1026 | P1_2-793 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-793 |  |  | VH
202682 | 18S | Proposed | P1 | 17 | 3ASHLAND | VH |  |  |  |  | 1.0616 | 1.0015 | 0.92 | 1.05 | 1035 | P1_2-802 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
202683 | 18S | Proposed | P1 | 17 | 3HOUMA! | VH |  |  |  |  | 1.0703 | 1.006 | 0.92 | 1.05 | 1035 | P1_2-802 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
202684 | 18S | Proposed | P1 | 17 | 3CHAVIN! | VH |  |  |  |  | 1.0511 | 0.9991 | 0.92 | 1.05 | 1035 | P1_2-802 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
202685 | 18S | Proposed | P1 | 17 | HOUMA 3 | VH |  |  |  |  | 1.0703 | 1.006 | 0.92 | 1.05 | 1035 | P1_2-802 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
202686 | 18S | Proposed | P1 | 17 | 3GMEADW! | VH |  |  |  |  | 1.1572 | 1.013 | 0.92 | 1.05 | 1040 | P1_2-807 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
202687 | 18S | Proposed | P1 | 17 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 1.0026 | 0.92 | 1.05 | 1040 | P1_2-807 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
202688 | 18S | Proposed | P1 | 17 | 3FOURCHN | VH |  |  |  |  | 1.1773 | 0.9928 | 0.92 | 1.05 | 1040 | P1_2-807 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
202689 | 18S | Proposed | P1 | 17 | 3JNCTN CITY! | VH |  |  |  |  | 1.061 | 1.0297 | 0.92 | 1.05 | 1510 | P1_2-1277 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1277 |  |  | VH
202690 | 18S | Proposed | P1 | 17 | 3MT PINE.S% | VL |  |  |  |  | 0.8465 | 0.993 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202691 | 18S | Proposed | P1 | 17 | 3ROYAL | VL |  |  |  |  | 0.8568 | 0.9902 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202692 | 18S | Proposed | P1 | 17 | 3MILTON | VL |  |  |  |  | 0.8815 | 0.987 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202693 | 18S | Proposed | P1 | 17 | 3HS.W | VL |  |  |  |  | 0.8342 | 0.9888 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202694 | 18S | Proposed | P1 | 17 | 3HS.S | VL |  |  |  |  | 0.8271 | 0.9875 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202695 | 18S | Proposed | P1 | 17 | 3ALBRIGHT | VL |  |  |  |  | 0.9135 | 0.9873 | 0.92 | 1.05 | 1572 | P1_2-1341 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
202696 | 18S | Proposed | P1 | 17 | 8SANS SOUCI% | VH |  |  |  |  | 1.054 | 1.0382 | 0.92 | 1.05 | 1744 | P1_2-1519 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1519 |  |  | VH
202697 | 18S | Proposed | P1 | 17 | 8DANIEL | VH |  |  |  |  | 1.0765 | 1.0431 | 0.92 | 1.05 | 1829 | P1_2-1604 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! |  |  | VH
202698 | 18S | Proposed | P1 | 17 | 4CANEY | VL |  |  |  |  | 0.8703 | 0.9942 | 0.92 | 1.05 | 1878 | P1_2-1653 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
202699 | 18S | Proposed | P1 | 17 | CENTNL 4 | VL |  |  |  |  | 0.9181 | 0.9915 | 0.92 | 1.05 | 1878 | P1_2-1653 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
202700 | 18S | Proposed | P1 | 17 | OAKDALE4 | VL |  |  |  |  | 0.8722 | 0.9923 | 0.92 | 1.05 | 1878 | P1_2-1653 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
202701 | 18S | Proposed | P1 | 17 | PNPRARIE 4 | VL |  |  |  |  | 0.8631 | 1.0067 | 0.92 | 1.05 | 1878 | P1_2-1653 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
202702 | 18S | Proposed | P1 | 17 | WSTBAY 4 | VL |  |  |  |  | 0.8841 | 0.9908 | 0.92 | 1.05 | 1878 | P1_2-1653 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
202703 | 18S | Proposed | P1 | 17 | 4VEAZIE | VL |  |  |  |  | 0.8935 | 0.9792 | 0.92 | 1.05 | 1879 | P1_2-1654 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202704 | 18S | Proposed | P1 | 17 | GUIDRY 4 | VL |  |  |  |  | 0.8921 | 0.978 | 0.92 | 1.05 | 1879 | P1_2-1654 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202705 | 18S | Proposed | P1 | 17 | PLAISAN4 | VL |  |  |  |  | 0.9075 | 0.9919 | 0.92 | 1.05 | 1879 | P1_2-1654 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202706 | 18S | Proposed | P1 | 17 | TENRUSK7 | VH |  |  |  |  | 1.052 | 1.0181 | 0.92 | 1.05 | 2088 | P1_2-1863 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
202707 | 18S | Proposed | P1 | 17 | TENGEN 7 | VH |  |  |  |  | 1.052 | 1.0181 | 0.92 | 1.05 | 2088 | P1_2-1863 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
202708 | 18S | Proposed | P0 | 18 | 2WEIRGAT | VL |  |  |  |  | 0.9182 | 0.9182 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202709 | 18S | Proposed | P0 | 18 | 5HORN LAKE% | VH |  |  |  |  | 1.0572 | 1.0572 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202710 | 18S | Proposed | P0 | 18 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202711 | 18S | Proposed | P0 | 18 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202712 | 18S | Proposed | P0 | 18 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
202713 | 18S | Proposed | P1 | 18 | 3FAYETTE | VH |  |  |  |  | 1.0881 | 1.0466 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202714 | 18S | Proposed | P1 | 18 | 3LORMAN+ | VH |  |  |  |  | 1.0771 | 1.0407 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202715 | 18S | Proposed | P1 | 18 | 3LORMAN | VH |  |  |  |  | 1.0769 | 1.0405 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202716 | 18S | Proposed | P1 | 18 | 3PORTGIBSON! | VH |  |  |  |  | 1.0723 | 1.0407 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202717 | 18S | Proposed | P1 | 18 | 3GGNS | VH |  |  |  |  | 1.0713 | 1.0397 | 0.975 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202718 | 18S | Proposed | P1 | 18 | 3S.VICKSBURG | VH |  |  |  |  | 1.0521 | 1.0354 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
202719 | 18S | Proposed | P1 | 18 | 3COLNIAL P/L | VH |  |  |  |  | 1.0581 | 1.0183 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
202720 | 18S | Proposed | P1 | 18 | 3FERNWOOD MS | VH |  |  |  |  | 1.0625 | 1.0168 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
202721 | 18S | Proposed | P1 | 18 | 3PROGRESS+ | VH |  |  |  |  | 1.0501 | 1.0037 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
202722 | 18S | Proposed | P1 | 18 | 3NATCHEZSES% | VH |  |  |  |  | 1.0675 | 1.0378 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202723 | 18S | Proposed | P1 | 18 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0668 | 1.0375 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202724 | 18S | Proposed | P1 | 18 | 3PINE RIDGE | VH |  |  |  |  | 1.0664 | 1.0372 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202725 | 18S | Proposed | P1 | 18 | 3NATCHEZ! | VH |  |  |  |  | 1.0653 | 1.0372 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202726 | 18S | Proposed | P1 | 18 | 3J.MANVILLE | VH |  |  |  |  | 1.0624 | 1.0347 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202727 | 18S | Proposed | P1 | 18 | 3INTL PAPER | VH |  |  |  |  | 1.061 | 1.034 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202728 | 18S | Proposed | P1 | 18 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0601 | 1.0334 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202729 | 18S | Proposed | P1 | 18 | 3NATCHEZ IND | VH |  |  |  |  | 1.0579 | 1.0322 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202730 | 18S | Proposed | P1 | 18 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0589 | 1.0327 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202731 | 18S | Proposed | P1 | 18 | 3KINGSTON MS | VH |  |  |  |  | 1.0566 | 1.0303 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202732 | 18S | Proposed | P1 | 18 | 3WASHINGTON+ | VH |  |  |  |  | 1.0608 | 1.0341 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202733 | 18S | Proposed | P1 | 18 | 3CRANFIELD+ | VH |  |  |  |  | 1.054 | 1.0309 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202734 | 18S | Proposed | P1 | 18 | 3FAYETTE | VH |  |  |  |  | 1.1045 | 1.0466 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202735 | 18S | Proposed | P1 | 18 | 3LORMAN+ | VH |  |  |  |  | 1.1192 | 1.0407 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202736 | 18S | Proposed | P1 | 18 | 3LORMAN | VH |  |  |  |  | 1.119 | 1.0405 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202737 | 18S | Proposed | P1 | 18 | 3PORTGIBSON! | VH |  |  |  |  | 1.1363 | 1.0407 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202738 | 18S | Proposed | P1 | 18 | 3GGNS | VH |  |  |  |  | 1.1354 | 1.0397 | 0.975 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202739 | 18S | Proposed | P1 | 18 | 3S.VICKSBURG | VH |  |  |  |  | 1.1634 | 1.0354 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202740 | 18S | Proposed | P1 | 18 | 3VIDALIA_LA | VH |  |  |  |  | 1.0512 | 1.0277 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202741 | 18S | Proposed | P1 | 18 | 3RED_GUM! | VH |  |  |  |  | 1.0563 | 1.0352 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202742 | 18S | Proposed | P1 | 18 | 3METROPOLIS | VH |  |  |  |  | 1.053 | 1.0393 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202743 | 18S | Proposed | P1 | 18 | 3WISNER | VH |  |  |  |  | 1.053 | 1.0398 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202744 | 18S | Proposed | P1 | 18 | VIDALIA3 | VH |  |  |  |  | 1.0512 | 1.0277 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202745 | 18S | Proposed | P1 | 18 | 3JNCTN CITY! | VH |  |  |  |  | 1.0606 | 1.0297 | 0.92 | 1.05 | 464 | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 |  |  | VH
202746 | 18S | Proposed | P2 | 18 | 3STUTGART IN | VL |  |  |  |  | 0.9034 | 1.0136 | 0.92 | 1.05 | 753 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
202747 | 18S | Proposed | P2 | 18 | 3ULM | VL |  |  |  |  | 0.9119 | 1.0108 | 0.92 | 1.05 | 753 | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337967 3RICUSKEY! 115 337969 3STUTGART IN 115 1 |  | Project Horizon | Model: Stuttgart Ind cap bank missing | 14-EAI-003-HZ | 2014-06-01 | Install 21.4 Mvar capacitor bank at Ulm 115 kV
202748 | 18S | Proposed | P2 | 18 | 3WARD# | VL |  |  |  |  | 0.9197 | 0.9945 | 0.92 | 1.05 | 789 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  | Project Proposed |  | 14-EAI-005-CP | 2019-06-01 | Construct Holland Bottoms-Beebe 161 kV; Install 161/115 kV auto
202749 | 18S | Proposed | P1 | 18 | 2HARRISON.S | VH |  |  |  |  | 1.0511 | 1.0349 | 0.92 | 1.05 | 833 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
202750 | 18S | Proposed | P1 | 18 | 8SANS SOUCI% | VH |  |  |  |  | 1.054 | 1.0382 | 0.92 | 1.05 | 904 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
202751 | 18S | Proposed | P1 | 18 | 2SINHERN | VH |  |  |  |  | 1.0581 | 1.0151 | 0.92 | 1.05 | 1106 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
202752 | 18S | Proposed | P1 | 18 | 2HEARNE! | VH |  |  |  |  | 1.0701 | 1.0286 | 0.92 | 1.05 | 1106 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
202753 | 18S | Proposed | P1 | 18 | 2TXHEARN | VH |  |  |  |  | 1.0687 | 1.0285 | 0.92 | 1.05 | 1106 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
202754 | 18S | Proposed | P1 | 18 | 2APLHERN | VH |  |  |  |  | 1.065 | 1.0284 | 0.92 | 1.05 | 1106 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
202755 | 18S | Proposed | P1 | 18 | 2SINHERN | VH |  |  |  |  | 1.0584 | 1.0151 | 0.92 | 1.05 | 1110 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
202756 | 18S | Proposed | P1 | 18 | 2HEARNE! | VH |  |  |  |  | 1.0704 | 1.0286 | 0.92 | 1.05 | 1110 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
202757 | 18S | Proposed | P1 | 18 | 2TXHEARN | VH |  |  |  |  | 1.069 | 1.0285 | 0.92 | 1.05 | 1110 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
202758 | 18S | Proposed | P1 | 18 | 2APLHERN | VH |  |  |  |  | 1.0653 | 1.0284 | 0.92 | 1.05 | 1110 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
202759 | 18S | Proposed | P1 | 18 | 2HUMBHRN | VH |  |  |  |  | 1.0704 | 1.0282 | 0.92 | 1.05 | 1110 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
202760 | 18S | Proposed | P1 | 18 | 2SINHERN | VH |  |  |  |  | 1.0606 | 1.0151 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202761 | 18S | Proposed | P1 | 18 | 2HEARNE! | VH |  |  |  |  | 1.0725 | 1.0286 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202762 | 18S | Proposed | P1 | 18 | 2TXHEARN | VH |  |  |  |  | 1.071 | 1.0285 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202763 | 18S | Proposed | P1 | 18 | 2APLHERN | VH |  |  |  |  | 1.0671 | 1.0284 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202764 | 18S | Proposed | P1 | 18 | 2HUMBHRN | VH |  |  |  |  | 1.0725 | 1.0282 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202765 | 18S | Proposed | P1 | 18 | 2TESCO | VH |  |  |  |  | 1.0727 | 1.0271 | 0.92 | 1.05 | 1111 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334007 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
202766 | 18S | Proposed | P1 | 18 | 4MAGROVE | VH |  |  |  |  | 1.0885 | 1.0139 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202767 | 18S | Proposed | P1 | 18 | 4L111T411 | VH |  |  |  |  | 1.0773 | 1.0114 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202768 | 18S | Proposed | P1 | 18 | 4KICKAPO | VH |  |  |  |  | 1.0772 | 1.0112 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202769 | 18S | Proposed | P1 | 18 | 4CORIGAN! | VH |  |  |  |  | 1.0666 | 1.0108 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202770 | 18S | Proposed | P1 | 18 | 4SHECORR | VH |  |  |  |  | 1.0652 | 1.0102 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202771 | 18S | Proposed | P1 | 18 | 4CAMDEN | VH |  |  |  |  | 1.0588 | 1.0085 | 0.92 | 1.05 | 1222 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
202772 | 18S | Proposed | P1 | 18 | 2PINELND | VL |  |  |  |  | 0.8917 | 0.9319 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202773 | 18S | Proposed | P1 | 18 | 2TEMPL1* | VL |  |  |  |  | 0.8898 | 0.93 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202774 | 18S | Proposed | P1 | 18 | 2TEMPLE1 | VL |  |  |  |  | 0.8894 | 0.9296 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202775 | 18S | Proposed | P1 | 18 | 2TEMPL2* | VL |  |  |  |  | 0.8895 | 0.9297 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202776 | 18S | Proposed | P1 | 18 | 2TEMPLE2 | VL |  |  |  |  | 0.8893 | 0.9295 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202777 | 18S | Proposed | P1 | 18 | 2TMPLSWC | VL |  |  |  |  | 0.8893 | 0.9296 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202778 | 18S | Proposed | P1 | 18 | 2WEIRGAT | VL |  |  |  |  | 0.8775 | 0.9182 | 0.92 | 1.05 | 1314 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202779 | 18S | Proposed | P1 | 18 | 2PINELND | VL |  |  |  |  | 0.8729 | 0.9319 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202780 | 18S | Proposed | P1 | 18 | 2TEMPL1* | VL |  |  |  |  | 0.8709 | 0.93 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202781 | 18S | Proposed | P1 | 18 | 2TEMPLE1 | VL |  |  |  |  | 0.8706 | 0.9296 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202782 | 18S | Proposed | P1 | 18 | 2TEMPL2* | VL |  |  |  |  | 0.8706 | 0.9297 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202783 | 18S | Proposed | P1 | 18 | 2TEMPLE2 | VL |  |  |  |  | 0.8704 | 0.9295 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202784 | 18S | Proposed | P1 | 18 | 2TMPLSWC | VL |  |  |  |  | 0.8705 | 0.9296 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202785 | 18S | Proposed | P1 | 18 | 2WEIRGAT | VL |  |  |  |  | 0.8584 | 0.9182 | 0.92 | 1.05 | 1316 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202786 | 18S | Proposed | P1 | 18 | 2PINELND | VL |  |  |  |  | 0.8958 | 0.9319 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202787 | 18S | Proposed | P1 | 18 | 2TEMPL1* | VL |  |  |  |  | 0.8938 | 0.93 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202788 | 18S | Proposed | P1 | 18 | 2TEMPLE1 | VL |  |  |  |  | 0.8935 | 0.9296 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202789 | 18S | Proposed | P1 | 18 | 2TEMPL2* | VL |  |  |  |  | 0.8935 | 0.9297 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202790 | 18S | Proposed | P1 | 18 | 2TEMPLE2 | VL |  |  |  |  | 0.8933 | 0.9295 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202791 | 18S | Proposed | P1 | 18 | 2TMPLSWC | VL |  |  |  |  | 0.8934 | 0.9296 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202792 | 18S | Proposed | P1 | 18 | 2WEIRGAT | VL |  |  |  |  | 0.8816 | 0.9182 | 0.92 | 1.05 | 1319 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202793 | 18S | Proposed | P1 | 18 | 2LINE-625_OP | VL |  |  |  |  | 0.9191 | 0.9898 | 0.92 | 1.05 | 1838 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 | 335428 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
202794 | 18S | Proposed | P1 | 18 | 2ST_MARTIN | VL |  |  |  |  | 0.9137 | 0.9849 | 0.92 | 1.05 | 1838 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
202795 | 18S | Proposed | P1 | 18 | LONGFL 2 | VL |  |  |  |  | 0.9138 | 0.9849 | 0.92 | 1.05 | 1838 | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 335408 2NEW_IBERIA!69.0 335427 2LN-625A_TP 69.0 1
202796 | 18S | Proposed | P1 | 18 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9191 | 0.9661 | 0.92 | 1.05 | 1865 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202797 | 18S | Proposed | P1 | 18 | 4BOBCAT | VL |  |  |  |  | 0.9156 | 0.9724 | 0.92 | 1.05 | 1865 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202798 | 18S | Proposed | P1 | 18 | 4LINE-642_TP | VL |  |  |  |  | 0.9192 | 0.9662 | 0.92 | 1.05 | 1865 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202799 | 18S | Proposed | P1 | 18 | 4COL_SPRINGS | VL |  |  |  |  | 0.9192 | 0.9661 | 0.92 | 1.05 | 1865 | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | 335453 4BOBCAT 138 335455 4CHAMPAGNE! 138 1 |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
202800 | 18S | Proposed | P1 | 18 | 2NESSER_TP | VL |  |  |  |  | 0.8824 | 0.9786 | 0.92 | 1.05 | 2002 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
202801 | 18S | Proposed | P1 | 18 | 2NESSER | VL |  |  |  |  | 0.8774 | 0.9741 | 0.92 | 1.05 | 2002 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
202802 | 18S | Proposed | P1 | 18 | 2LN-372A_TP | VL |  |  |  |  | 0.8977 | 0.9922 | 0.92 | 1.05 | 2002 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335710 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
202803 | 18S | Proposed | P1 | 18 | 2JONESCREEK! | VL |  |  |  |  | 0.9011 | 0.9888 | 0.92 | 1.05 | 2002 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335711 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
202804 | 18S | Proposed | P1 | 18 | 2ANGOLA | VL |  |  |  |  | 0.891 | 0.9942 | 0.92 | 1.05 | 2074 | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | 335793 2FRANCIS! 69.0 335795 2GRANT 69.0 1 |  | None
202805 | 18S | Proposed | P1 | 18 | 3MCCALL! | VH |  |  |  |  | 1.0514 | 1.0201 | 0.92 | 1.05 | 2112 | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 | 336016 |  |  |  | 115 | 115 | 351 | EES |  |  | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 |  |  | VH
202806 | 18S | Proposed | P1 | 18 | 3PVILLE! | VH |  |  |  |  | 1.0536 | 1.0152 | 0.92 | 1.05 | 2112 | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 |  |  | VH
202807 | 18S | Proposed | P1 | 18 | 3ASHLAND | VH |  |  |  |  | 1.0616 | 1.0015 | 0.92 | 1.05 | 2122 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
202808 | 18S | Proposed | P1 | 18 | 3HOUMA! | VH |  |  |  |  | 1.0703 | 1.006 | 0.92 | 1.05 | 2122 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
202809 | 18S | Proposed | P1 | 18 | 3CHAVIN! | VH |  |  |  |  | 1.0511 | 0.9991 | 0.92 | 1.05 | 2122 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
202810 | 18S | Proposed | P1 | 18 | HOUMA 3 | VH |  |  |  |  | 1.0703 | 1.006 | 0.92 | 1.05 | 2122 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
202811 | 18S | Proposed | P1 | 18 | 3GMEADW! | VH |  |  |  |  | 1.1573 | 1.013 | 0.92 | 1.05 | 2151 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202812 | 18S | Proposed | P1 | 18 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 1.0026 | 0.92 | 1.05 | 2151 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202813 | 18S | Proposed | P1 | 18 | 3FOURCHN | VH |  |  |  |  | 1.1774 | 0.9928 | 0.92 | 1.05 | 2151 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
202814 | 18S | Proposed | P1 | 18 | 3CARLSL | VL |  |  |  |  | 0.8817 | 0.9834 | 0.92 | 1.05 | 2161 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
202815 | 18S | Proposed | P1 | 18 | 3GILBERT | VH |  |  |  |  | 1.0537 | 1.0325 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202816 | 18S | Proposed | P1 | 18 | 3PERSIM_MIL | VH |  |  |  |  | 1.0532 | 1.0236 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202817 | 18S | Proposed | P1 | 18 | 3NATCHEZSES% | VH |  |  |  |  | 1.0573 | 1.0378 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202818 | 18S | Proposed | P1 | 18 | 3PINE RIDGE+ | VH |  |  |  |  | 1.057 | 1.0375 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202819 | 18S | Proposed | P1 | 18 | 3PINE RIDGE | VH |  |  |  |  | 1.0567 | 1.0372 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202820 | 18S | Proposed | P1 | 18 | 3NATCHEZ! | VH |  |  |  |  | 1.0569 | 1.0372 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202821 | 18S | Proposed | P1 | 18 | 3J.MANVILLE | VH |  |  |  |  | 1.055 | 1.0347 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202822 | 18S | Proposed | P1 | 18 | 3INTL PAPER | VH |  |  |  |  | 1.0546 | 1.034 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202823 | 18S | Proposed | P1 | 18 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0543 | 1.0334 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202824 | 18S | Proposed | P1 | 18 | 3NATCHEZ IND | VH |  |  |  |  | 1.0537 | 1.0322 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202825 | 18S | Proposed | P1 | 18 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0509 | 1.0327 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202826 | 18S | Proposed | P1 | 18 | 3WASHINGTON+ | VH |  |  |  |  | 1.0524 | 1.0341 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202827 | 18S | Proposed | P1 | 18 | 3FAYETTE | VH |  |  |  |  | 1.0632 | 1.0466 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202828 | 18S | Proposed | P1 | 18 | 3LORMAN+ | VH |  |  |  |  | 1.0553 | 1.0407 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202829 | 18S | Proposed | P1 | 18 | 3LORMAN | VH |  |  |  |  | 1.0551 | 1.0405 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202830 | 18S | Proposed | P1 | 18 | 3PORTGIBSON! | VH |  |  |  |  | 1.0535 | 1.0407 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202831 | 18S | Proposed | P1 | 18 | 3GGNS | VH |  |  |  |  | 1.0525 | 1.0397 | 0.975 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | VH
202832 | 18S | Proposed | P1 | 18 | 3S_FERDAY_TP | VH |  |  |  |  | 1.053 | 1.0231 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202833 | 18S | Proposed | P1 | 18 | 3PLANTATION! | VH |  |  |  |  | 1.0503 | 1.0271 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202834 | 18S | Proposed | P1 | 18 | 3VIDALIA_LA | VH |  |  |  |  | 1.0503 | 1.0277 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202835 | 18S | Proposed | P1 | 18 | 3RED_GUM! | VH |  |  |  |  | 1.0602 | 1.0352 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202836 | 18S | Proposed | P1 | 18 | 3METROPOLIS | VH |  |  |  |  | 1.0616 | 1.0393 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202837 | 18S | Proposed | P1 | 18 | 3WISNER | VH |  |  |  |  | 1.0619 | 1.0398 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202838 | 18S | Proposed | P1 | 18 | VIDALIA3 | VH |  |  |  |  | 1.0503 | 1.0277 | 0.92 | 1.05 | 2297 | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 337318 3BLACK_RIVER 115 337319 3S_FERDAY_TP 115 1 |  |  | Facility: Radial
202839 | 18S | Proposed | P1 | 18 | 3GILBERT | VH |  |  |  |  | 1.0501 | 1.0325 | 0.92 | 1.05 | 2303 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | VH
202840 | 18S | Proposed | P1 | 18 | 3WISNER | VH |  |  |  |  | 1.0592 | 1.0398 | 0.92 | 1.05 | 2303 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | VH
202841 | 18S | Proposed | P1 | 18 | 3LUCKY | VH |  |  |  |  | 1.056 | 1.0236 | 0.92 | 1.05 | 2315 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 |  |  | VH
202842 | 18S | Proposed | P1 | 18 | 2PINELND | VL |  |  |  |  | 0.9198 | 0.9319 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202843 | 18S | Proposed | P1 | 18 | 2TEMPL1* | VL |  |  |  |  | 0.9179 | 0.93 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202844 | 18S | Proposed | P1 | 18 | 2TEMPLE1 | VL |  |  |  |  | 0.9176 | 0.9296 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202845 | 18S | Proposed | P1 | 18 | 2TEMPL2* | VL |  |  |  |  | 0.9176 | 0.9297 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202846 | 18S | Proposed | P1 | 18 | 2TEMPLE2 | VL |  |  |  |  | 0.9174 | 0.9295 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202847 | 18S | Proposed | P1 | 18 | 2TMPLSWC | VL |  |  |  |  | 0.9175 | 0.9296 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202848 | 18S | Proposed | P1 | 18 | 2WEIRGAT | VL |  |  |  |  | 0.906 | 0.9182 | 0.92 | 1.05 | 2389 | Unit:334282 4RAYBURN% 138 Id:1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202849 | 18S | Proposed | P1 | 18 | 3PERSIM_MIL | VH |  |  |  |  | 1.0509 | 1.0236 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202850 | 18S | Proposed | P1 | 18 | 3NATCHEZSES% | VH |  |  |  |  | 1.0608 | 1.0378 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202851 | 18S | Proposed | P1 | 18 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0604 | 1.0375 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202852 | 18S | Proposed | P1 | 18 | 3PINE RIDGE | VH |  |  |  |  | 1.0601 | 1.0372 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202853 | 18S | Proposed | P1 | 18 | 3NATCHEZ! | VH |  |  |  |  | 1.0599 | 1.0372 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202854 | 18S | Proposed | P1 | 18 | 3J.MANVILLE | VH |  |  |  |  | 1.0576 | 1.0347 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202855 | 18S | Proposed | P1 | 18 | 3INTL PAPER | VH |  |  |  |  | 1.0569 | 1.034 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202856 | 18S | Proposed | P1 | 18 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0564 | 1.0334 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202857 | 18S | Proposed | P1 | 18 | 3NATCHEZ IND | VH |  |  |  |  | 1.0554 | 1.0322 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202858 | 18S | Proposed | P1 | 18 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.0539 | 1.0327 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202859 | 18S | Proposed | P1 | 18 | 3KINGSTON MS | VH |  |  |  |  | 1.0515 | 1.0303 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202860 | 18S | Proposed | P1 | 18 | 3WASHINGTON+ | VH |  |  |  |  | 1.0555 | 1.0341 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202861 | 18S | Proposed | P1 | 18 | 3CRANFIELD+ | VH |  |  |  |  | 1.0503 | 1.0309 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202862 | 18S | Proposed | P1 | 18 | 3FAYETTE | VH |  |  |  |  | 1.0719 | 1.0466 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202863 | 18S | Proposed | P1 | 18 | 3LORMAN+ | VH |  |  |  |  | 1.0669 | 1.0407 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202864 | 18S | Proposed | P1 | 18 | 3LORMAN | VH |  |  |  |  | 1.0667 | 1.0405 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202865 | 18S | Proposed | P1 | 18 | 3PORTGIBSON! | VH |  |  |  |  | 1.0675 | 1.0407 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202866 | 18S | Proposed | P1 | 18 | 3GGNS | VH |  |  |  |  | 1.0665 | 1.0397 | 0.975 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | VH
202867 | 18S | Proposed | P1 | 18 | 3S_FERDAY_TP | VH |  |  |  |  | 1.0502 | 1.0231 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202868 | 18S | Proposed | P1 | 18 | 3PLANTATION! | VH |  |  |  |  | 1.0503 | 1.0271 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202869 | 18S | Proposed | P1 | 18 | 3VIDALIA_LA | VH |  |  |  |  | 1.051 | 1.0277 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202870 | 18S | Proposed | P1 | 18 | 3RED_GUM! | VH |  |  |  |  | 1.0672 | 1.0352 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202871 | 18S | Proposed | P1 | 18 | 3METROPOLIS | VH |  |  |  |  | 1.1087 | 1.0393 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202872 | 18S | Proposed | P1 | 18 | 3WISNER | VH |  |  |  |  | 1.1118 | 1.0398 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202873 | 18S | Proposed | P1 | 18 | VIDALIA3 | VH |  |  |  |  | 1.051 | 1.0277 | 0.92 | 1.05 | 2522 | 303322 3GILBERT 115 337329 3WISNER 115 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 303322 3GILBERT 115 337329 3WISNER 115 1 |  |  | Contingency: invalid, no breakers
202874 | 18S | Proposed | P1 | 18 | 3GILBERT | VH |  |  |  |  | 1.0743 | 1.0325 | 0.92 | 1.05 | 2523 | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 |  |  | VH
202875 | 18S | Proposed | P1 | 18 | 3METROPOLIS | VH |  |  |  |  | 1.0737 | 1.0393 | 0.92 | 1.05 | 2523 | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 |  |  | VH
202876 | 18S | Proposed | P1 | 18 | 3WISNER | VH |  |  |  |  | 1.0761 | 1.0398 | 0.92 | 1.05 | 2523 | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303322 3GILBERT 115 337330 3WINNSBORO! 115 1 |  |  | VH
202877 | 18S | Proposed | P1 | 18 | 3GILBERT | VL |  |  |  |  | 0.8624 | 1.0325 | 0.92 | 1.05 | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202878 | 18S | Proposed | P1 | 18 | 3BASKIN | VL |  |  |  |  | 0.8378 | 1.0124 | 0.92 | 1.05 | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
202879 | 18S | Proposed | P1 | 18 | 3METROPOLIS | VL |  |  |  |  | 0.881 | 1.0393 | 0.92 | 1.05 | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202880 | 18S | Proposed | P1 | 18 | 3WISNER | VL |  |  |  |  | 0.8762 | 1.0398 | 0.92 | 1.05 | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202881 | 18S | Proposed | P1 | 18 | 3WINNSBORO! | VL |  |  |  |  | 0.8408 | 1.0218 | 0.92 | 1.05 | 2528 | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337331 3ALTO_LA 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
202882 | 18S | Proposed | P1 | 18 | 4CANEY | VL |  |  |  |  | 0.9191 | 0.9942 | 0.92 | 1.05 | 2626 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
202883 | 18S | Proposed | P1 | 18 | OAKDALE4 | VL |  |  |  |  | 0.9197 | 0.9923 | 0.92 | 1.05 | 2626 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
202884 | 18S | Proposed | P1 | 18 | 4CANEY | VL |  |  |  |  | 0.8703 | 0.9942 | 0.92 | 1.05 | 2686 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202885 | 18S | Proposed | P1 | 18 | CENTNL 4 | VL |  |  |  |  | 0.9181 | 0.9915 | 0.92 | 1.05 | 2686 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202886 | 18S | Proposed | P1 | 18 | OAKDALE4 | VL |  |  |  |  | 0.8722 | 0.9923 | 0.92 | 1.05 | 2686 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202887 | 18S | Proposed | P1 | 18 | PNPRARIE 4 | VL |  |  |  |  | 0.8631 | 1.0067 | 0.92 | 1.05 | 2686 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202888 | 18S | Proposed | P1 | 18 | WSTBAY 4 | VL |  |  |  |  | 0.8841 | 0.9908 | 0.92 | 1.05 | 2686 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
202892 | 18S | Proposed | P1 | 18 | ELKS 6 | VL |  |  |  |  | 0.9165 | 0.9842 | 0.92 | 1.05 | 2779 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 |  | turn on switch shunt at BEADLE 230kV sub
202893 | 18S | Proposed | P1 | 18 | BEADLE 6 | VL |  |  |  |  | 0.917 | 0.9859 | 0.92 | 1.05 | 2779 | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1
202894 | 18S | Proposed | P1 | 18 | ELKS 6 | VL |  |  |  |  | 0.9013 | 0.9842 | 0.92 | 1.05 | 2804 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
202895 | 18S | Proposed | P1 | 18 | 8THALMANN | VH |  |  |  |  | 1.0514 | 1.04 | 0.92 | 1.05 | 2895 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
202896 | 18S | Proposed | P1 | 18 | 8MCCALL RD | VH |  |  |  |  | 1.0661 | 1.0334 | 0.92 | 1.05 | 2895 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
202897 | 18S | Proposed | P1 | 18 | 8DANIEL | VH |  |  |  |  | 1.0765 | 1.0431 | 0.92 | 1.05 | 3617 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
202898 | 18S | Proposed | P2 | 18 | 5HIGHLAND | VL |  |  |  |  | 0.9191 | 0.9843 | 0.92 | 1.05 | 4401 | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 | 338220 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | 504080 GLENCOE 5 161 505448 NORFORK5 161 1 |  | None
202899 | 18S | Proposed | P1 | 18 | TENRUSK7 | VH |  |  |  |  | 1.052 | 1.0181 | 0.92 | 1.05 | 4604 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
202900 | 18S | Proposed | P1 | 18 | TENGEN 7 | VH |  |  |  |  | 1.052 | 1.0181 | 0.92 | 1.05 | 4604 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
202901 | 18S | Proposed | P1 | 18 | ELKCITY7 | VH |  |  |  |  | 1.0516 | 1.0271 | 0.92 | 1.05 | 4645 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
202902 | 18S | Proposed | P0 | 19 | 2WEIRGAT | VL |  |  |  |  | 0.9182 | 0.9182 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202903 | 18S | Proposed | P0 | 19 | 5HORN LAKE% | VH |  |  |  |  | 1.0572 | 1.0572 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202904 | 18S | Proposed | P0 | 19 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202905 | 18S | Proposed | P0 | 19 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202906 | 18S | Proposed | P0 | 19 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
202907 | 18S | Proposed | P1 | 19 | 4NEW_IBERIA! | VL |  |  |  |  | 0.902 | 0.9953 | 0.92 | 1.05 | 5 | P1_2-562-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-562-a |  |  | Contingency: Trip bus as result of con
202908 | 18S | Proposed | P1 | 19 | 4NEW_IBERIA! | VL |  |  |  |  | 0.902 | 0.9953 | 0.92 | 1.05 | 6 | P1_2-568-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-568-a |  |  | Contingency: Trip bus as result of con
202909 | 18W | Proposed | P0 | 20 | 5HORN LAKE% | VH |  |  |  |  | 1.0604 | 1.0604 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202910 | 18W | Proposed | P0 | 20 | 8UNION MS | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202911 | 18W | Proposed | P0 | 20 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202912 | 18W | Proposed | P0 | 20 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202913 | 18W | Proposed | P0 | 20 | 8PLEASANT HL | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202914 | 18W | Proposed | P0 | 20 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202915 | 18W | Proposed | P0 | 20 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
202916 | 18W | Proposed | P1 | 20 | 2MCCLELLAN | VH |  |  |  |  | 1.0547 | 1.0256 | 0.92 | 1.05 | 139 | G-338500-1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | G-338500-1 |  |  | VH
202918 | 18W | Proposed | P1 | 20 | 2CALVERT! | VL |  |  |  |  | 0.8075 | 0.9855 | 0.92 | 1.05 | 344 | P1_2-125 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202919 | 18W | Proposed | P1 | 20 | 2SINHERN | VL |  |  |  |  | 0.8441 | 1.002 | 0.92 | 1.05 | 344 | P1_2-125 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202920 | 18W | Proposed | P1 | 20 | 2HEARNE! | VL |  |  |  |  | 0.8774 | 1.018 | 0.92 | 1.05 | 344 | P1_2-125 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202921 | 18W | Proposed | P1 | 20 | 2TXHEARN | VL |  |  |  |  | 0.8773 | 1.0185 | 0.92 | 1.05 | 344 | P1_2-125 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202922 | 18W | Proposed | P1 | 20 | 2APLHERN | VL |  |  |  |  | 0.8771 | 1.0197 | 0.92 | 1.05 | 344 | P1_2-125 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202923 | 18W | Proposed | P1 | 20 | 2BRYAN A! | VL |  |  |  |  | 0.877 | 1.0251 | 0.92 | 1.05 | 344 | P1_2-125 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202924 | 18W | Proposed | P1 | 20 | 2HUMBHRN | VL |  |  |  |  | 0.887 | 1.018 | 0.92 | 1.05 | 344 | P1_2-125 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-125 |  |  | Solution: Adjust caps
202925 | 18W | Proposed | P1 | 20 | 4PEE DEE! | VH |  |  |  |  | 1.051 | 1.0206 | 0.92 | 1.05 | 365 | P1_2-146 | 334050 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-146 |  |  | VH
202926 | 18W | Proposed | P1 | 20 | 4CORIGAN! | VH |  |  |  |  | 1.0533 | 1.0167 | 0.92 | 1.05 | 408 | P1_2-190 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! |  |  | VH
202927 | 18W | Proposed | P1 | 20 | 2HIMEX | VH |  |  |  |  | 1.0519 | 1.026 | 0.92 | 1.05 | 439 | P1_2-221 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! |  |  | VH
202928 | 18W | Proposed | P1 | 20 | 2PINELND | VL |  |  |  |  | 0.9155 | 0.9517 | 0.92 | 1.05 | 455 | P1_2-237 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202929 | 18W | Proposed | P1 | 20 | 2TEMPL1* | VL |  |  |  |  | 0.9136 | 0.9499 | 0.92 | 1.05 | 455 | P1_2-237 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202930 | 18W | Proposed | P1 | 20 | 2TEMPLE1 | VL |  |  |  |  | 0.9133 | 0.9496 | 0.92 | 1.05 | 455 | P1_2-237 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202931 | 18W | Proposed | P1 | 20 | 2TEMPL2* | VL |  |  |  |  | 0.9133 | 0.9495 | 0.92 | 1.05 | 455 | P1_2-237 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202932 | 18W | Proposed | P1 | 20 | 2TEMPLE2 | VL |  |  |  |  | 0.9131 | 0.9494 | 0.92 | 1.05 | 455 | P1_2-237 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202933 | 18W | Proposed | P1 | 20 | 2TMPLSWC | VL |  |  |  |  | 0.9131 | 0.9494 | 0.92 | 1.05 | 455 | P1_2-237 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202934 | 18W | Proposed | P1 | 20 | 2WEIRGAT | VL |  |  |  |  | 0.896 | 0.933 | 0.92 | 1.05 | 455 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202935 | 18W | Proposed | P1 | 20 | 2PINELND | VL |  |  |  |  | 0.9102 | 0.9517 | 0.92 | 1.05 | 457 | P1_2-239 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202936 | 18W | Proposed | P1 | 20 | 2TEMPL1* | VL |  |  |  |  | 0.9083 | 0.9499 | 0.92 | 1.05 | 457 | P1_2-239 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202937 | 18W | Proposed | P1 | 20 | 2TEMPLE1 | VL |  |  |  |  | 0.9081 | 0.9496 | 0.92 | 1.05 | 457 | P1_2-239 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202938 | 18W | Proposed | P1 | 20 | 2TEMPL2* | VL |  |  |  |  | 0.908 | 0.9495 | 0.92 | 1.05 | 457 | P1_2-239 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202939 | 18W | Proposed | P1 | 20 | 2TEMPLE2 | VL |  |  |  |  | 0.9078 | 0.9494 | 0.92 | 1.05 | 457 | P1_2-239 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202940 | 18W | Proposed | P1 | 20 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9494 | 0.92 | 1.05 | 457 | P1_2-239 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202941 | 18W | Proposed | P1 | 20 | 2WEIRGAT | VL |  |  |  |  | 0.8906 | 0.933 | 0.92 | 1.05 | 457 | P1_2-239 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202942 | 18W | Proposed | P1 | 20 | 2WEIRGAT | VL |  |  |  |  | 0.92 | 0.933 | 0.92 | 1.05 | 486 | P1_2-268 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-268 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202943 | 18W | Proposed | P1 | 20 | 2SERPENT | VL |  |  |  |  | 0.9183 | 0.9329 | 0.92 | 1.05 | 674 | P1_2-457 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-457_6CARLYSS%,6BOUDOIN% |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
202944 | 18W | Proposed | P1 | 20 | 3ASHLAND | VH |  |  |  |  | 1.0921 | 1.0071 | 0.92 | 1.05 | 1019 | P1_2-803 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
202945 | 18W | Proposed | P1 | 20 | 3HOUMA! | VH |  |  |  |  | 1.1021 | 1.0112 | 0.92 | 1.05 | 1019 | P1_2-803 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
202946 | 18W | Proposed | P1 | 20 | 3CHAVIN! | VH |  |  |  |  | 1.0755 | 1.0045 | 0.92 | 1.05 | 1019 | P1_2-803 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
202947 | 18W | Proposed | P1 | 20 | HOUMA 3 | VH |  |  |  |  | 1.1021 | 1.0112 | 0.92 | 1.05 | 1019 | P1_2-803 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! |  |  | VH
202948 | 18W | Proposed | P1 | 20 | 3GMEADW! | VH |  |  |  |  | 1.1753 | 1.0203 | 0.92 | 1.05 | 1024 | P1_2-808 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202949 | 18W | Proposed | P1 | 20 | 3LEEVLL | VH |  |  |  |  | 1.1984 | 1.0115 | 0.92 | 1.05 | 1024 | P1_2-808 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202950 | 18W | Proposed | P1 | 20 | 3FOURCHN | VH |  |  |  |  | 1.1981 | 1.0019 | 0.92 | 1.05 | 1024 | P1_2-808 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! |  |  | VH
202951 | 18W | Proposed | P1 | 20 | 3GILBERT | VH |  |  |  |  | 1.1234 | 1.0101 | 0.92 | 1.05 | 1397 | P1_2-1181 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202952 | 18W | Proposed | P1 | 20 | 3RED_GUM! | VH |  |  |  |  | 1.0549 | 1.027 | 0.92 | 1.05 | 1397 | P1_2-1181 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202953 | 18W | Proposed | P1 | 20 | 3METROPOLIS | VH |  |  |  |  | 1.115 | 1.0131 | 0.92 | 1.05 | 1397 | P1_2-1181 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202954 | 18W | Proposed | P1 | 20 | 3WISNER | VH |  |  |  |  | 1.1194 | 1.0122 | 0.92 | 1.05 | 1397 | P1_2-1181 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202955 | 18W | Proposed | P1 | 20 | 3WINNSBORO! | VH |  |  |  |  | 1.133 | 1.0078 | 0.92 | 1.05 | 1397 | P1_2-1181 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! |  |  | VH
202956 | 18W | Proposed | P1 | 20 | 3DELHI_LA! | VH |  |  |  |  | 1.0529 | 1.0149 | 0.92 | 1.05 | 1473 | P1_2-1257 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! |  |  | VH
202957 | 18W | Proposed | P1 | 20 | 3HS.W | VL |  |  |  |  | 0.918 | 0.9989 | 0.92 | 1.05 | 1558 | P1_2-1344 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344 |  |  | Contingency: invalid after Albright
202958 | 18W | Proposed | P1 | 20 | 3HS.S | VL |  |  |  |  | 0.9139 | 1.0001 | 0.92 | 1.05 | 1558 | P1_2-1344 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344 |  |  | Contingency: invalid after Albright
202959 | 18W | Proposed | P1 | 20 | 8SANS SOUCI% | VH |  |  |  |  | 1.0618 | 1.0496 | 0.92 | 1.05 | 1730 | P1_2-1522 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% |  |  | VH
202960 | 18W | Proposed | P1 | 20 | 2MCCLELLAN | VH |  |  |  |  | 1.0547 | 1.0256 | 0.92 | 1.05 | 1759 | P1_2-1551 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! |  |  | VH
202961 | 18W | Proposed | P1 | 20 | 8LAG CRK CT | VH |  |  |  |  | 1.0568 | 1.0414 | 0.92 | 1.05 | 1793 | P1_2-1585 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! |  |  | VH
202962 | 18W | Proposed | P1 | 20 | 8DANIEL | VH |  |  |  |  | 1.0759 | 1.042 | 0.92 | 1.05 | 1815 | P1_2-1607 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! |  |  | VH
202963 | 18W | Proposed | P1 | 20 | 4CANEY | VL |  |  |  |  | 0.8868 | 0.9995 | 0.92 | 1.05 | 1864 | P1_2-1656 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
202964 | 18W | Proposed | P1 | 20 | OAKDALE4 | VL |  |  |  |  | 0.8887 | 0.9981 | 0.92 | 1.05 | 1864 | P1_2-1656 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
202965 | 18W | Proposed | P1 | 20 | PNPRARIE 4 | VL |  |  |  |  | 0.8797 | 1.0094 | 0.92 | 1.05 | 1864 | P1_2-1656 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
202966 | 18W | Proposed | P1 | 20 | WSTBAY 4 | VL |  |  |  |  | 0.8984 | 0.9965 | 0.92 | 1.05 | 1864 | P1_2-1656 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4%
202967 | 18W | Proposed | P1 | 20 | 2WEIRGAT | VL |  |  |  |  | 0.9167 | 0.933 | 0.92 | 1.05 | 1872 | P1_2-1664 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
202968 | 18W | Proposed | P1 | 20 | TENRUSK7 | VH |  |  |  |  | 1.0513 | 1.0185 | 0.92 | 1.05 | 2074 | P1_2-1866 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
202969 | 18W | Proposed | P1 | 20 | TENGEN 7 | VH |  |  |  |  | 1.0513 | 1.0185 | 0.92 | 1.05 | 2074 | P1_2-1866 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! |  |  | VH
202970 | 18W | Proposed | P0 | 21 | 5HORN LAKE% | VH |  |  |  |  | 1.0604 | 1.0604 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
202971 | 18W | Proposed | P0 | 21 | 8UNION MS | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202972 | 18W | Proposed | P0 | 21 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202973 | 18W | Proposed | P0 | 21 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202974 | 18W | Proposed | P0 | 21 | 8PLEASANT HL | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202975 | 18W | Proposed | P0 | 21 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
202976 | 18W | Proposed | P0 | 21 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
202977 | 18W | Proposed | P1 | 21 | 3CHATAWA+ | VH |  |  |  |  | 1.0506 | 0.9945 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202978 | 18W | Proposed | P1 | 21 | 3COLNIAL P/L | VH |  |  |  |  | 1.0606 | 0.9936 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202979 | 18W | Proposed | P1 | 21 | 3FERNWOOD MS | VH |  |  |  |  | 1.0658 | 0.9944 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202980 | 18W | Proposed | P1 | 21 | 3PROGRESS+ | VH |  |  |  |  | 1.0563 | 0.9842 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202981 | 18W | Proposed | P1 | 21 | 3OAKDALE+ | VH |  |  |  |  | 1.0653 | 0.9973 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202982 | 18W | Proposed | P1 | 21 | 3PLANT.P/L | VH |  |  |  |  | 1.0562 | 0.9841 | 0.92 | 1.05 | 36 | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336539 3OAKDALE+ 115 336551 3MCCOMB! 115 1 |  |  | VH
202983 | 18W | Proposed | P1 | 21 | 3COLNIAL P/L | VH |  |  |  |  | 1.0564 | 0.9936 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202984 | 18W | Proposed | P1 | 21 | 3FERNWOOD MS | VH |  |  |  |  | 1.0623 | 0.9944 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202985 | 18W | Proposed | P1 | 21 | 3PROGRESS+ | VH |  |  |  |  | 1.0528 | 0.9842 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202986 | 18W | Proposed | P1 | 21 | 3OAKDALE+ | VH |  |  |  |  | 1.0622 | 0.9973 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202987 | 18W | Proposed | P1 | 21 | 3PLANT.P/L | VH |  |  |  |  | 1.0527 | 0.9841 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202988 | 18W | Proposed | P1 | 21 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0561 | 1.0005 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202989 | 18W | Proposed | P1 | 21 | 3MCCOMB! | VH |  |  |  |  | 1.0626 | 1.0004 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202990 | 18W | Proposed | P1 | 21 | 3NORFIELD+ | VH |  |  |  |  | 1.0605 | 1.0038 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336552 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202991 | 18W | Proposed | P1 | 21 | 3PISGAH MS+ | VH |  |  |  |  | 1.0586 | 0.9961 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202992 | 18W | Proposed | P1 | 21 | 3W.MCCOMB | VH |  |  |  |  | 1.0578 | 0.9953 | 0.92 | 1.05 | 46 | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336552 3NORFIELD+ 115 336553 3MALLALIEU+ 115 1 |  |  | VH
202993 | 18W | Proposed | P1 | 21 | 3FAYETTE | VH |  |  |  |  | 1.077 | 1.0246 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202994 | 18W | Proposed | P1 | 21 | 3LORMAN+ | VH |  |  |  |  | 1.1002 | 1.0228 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202995 | 18W | Proposed | P1 | 21 | 3LORMAN | VH |  |  |  |  | 1.1001 | 1.0227 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202996 | 18W | Proposed | P1 | 21 | 3PORTGIBSON! | VH |  |  |  |  | 1.121 | 1.0225 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202997 | 18W | Proposed | P1 | 21 | 3GGNS | VH |  |  |  |  | 1.12 | 1.0215 | 0.975 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202998 | 18W | Proposed | P1 | 21 | 3S.VICKSBURG | VH |  |  |  |  | 1.1484 | 1.0315 | 0.92 | 1.05 | 92 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
202999 | 18W | Proposed | P1 | 21 | 3ONWARD+ | VH |  |  |  |  | 1.0505 | 1.0088 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336967 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203000 | 18W | Proposed | P1 | 21 | 3ROLING FRK! | VH |  |  |  |  | 1.0652 | 1.004 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336968 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203001 | 18W | Proposed | P1 | 21 | 3MAYERSVILLE | VH |  |  |  |  | 1.0603 | 0.9987 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336969 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203002 | 18W | Proposed | P1 | 21 | 3NITTA YUMA+ | VH |  |  |  |  | 1.0662 | 1.0047 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336970 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203003 | 18W | Proposed | P1 | 21 | 3MURPHY+ | VH |  |  |  |  | 1.0679 | 1.0057 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 336992 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203004 | 18W | Proposed | P1 | 21 | 3GREENVILLE+ | VH |  |  |  |  | 1.0585 | 1.0177 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337046 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203005 | 18W | Proposed | P1 | 21 | 3HOLLANDALE | VH |  |  |  |  | 1.0685 | 1.0063 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337048 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203006 | 18W | Proposed | P1 | 21 | 3ARCOLA+ | VH |  |  |  |  | 1.063 | 1.0116 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337049 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203007 | 18W | Proposed | P1 | 21 | 3SWIFTWATER | VH |  |  |  |  | 1.0581 | 1.0173 | 0.92 | 1.05 | 272 | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 | 337071 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 337045 3SE.GREENVL 115 337046 3GREENVILLE+ 115 1 |  | Project Proposed | Contingency: invalid, no breakers | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
203008 | 18W | Proposed | P1 | 21 | 3JNCTN CITY! | VH |  |  |  |  | 1.0732 | 1.0338 | 0.92 | 1.05 | 463 | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 |  |  | VH
203009 | 18W | Proposed | P2 | 21 | 2WARD | VH |  |  |  |  | 1.0529 | 1.0406 | 0.92 | 1.05 | 788 | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338006 3CABOT 115 338016 3HOLND BTM! 115 1 |  |  | VH
203010 | 18W | Proposed | P1 | 21 | 2BLACK ROCK | VH |  |  |  |  | 1.0519 | 1.03 | 0.92 | 1.05 | 880 | 338153 5SWIFTON 161 338705 5HOXIE.S# 161 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338153 5SWIFTON 161 338705 5HOXIE.S# 161 1 |  |  | VH
203011 | 18W | Proposed | P1 | 21 | 8SANS SOUCI% | VH |  |  |  |  | 1.0618 | 1.0496 | 0.92 | 1.05 | 903 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
203012 | 18W | Proposed | P1 | 21 | 2MCCLELLAN | VH |  |  |  |  | 1.0547 | 1.0256 | 0.92 | 1.05 | 1007 | Unit:338500 1MCCLELAN U114.4 Id:1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | Unit:338500 1MCCLELAN U114.4 Id:1 |  |  | VH
203013 | 18W | Proposed | P1 | 21 | 2CALVERT! | VL |  |  |  |  | 0.8075 | 0.9855 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203014 | 18W | Proposed | P1 | 21 | 2SINHERN | VL |  |  |  |  | 0.8441 | 1.002 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203015 | 18W | Proposed | P1 | 21 | 2HEARNE! | VL |  |  |  |  | 0.8774 | 1.018 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203016 | 18W | Proposed | P1 | 21 | 2TXHEARN | VL |  |  |  |  | 0.8773 | 1.0185 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203017 | 18W | Proposed | P1 | 21 | 2APLHERN | VL |  |  |  |  | 0.8771 | 1.0197 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203018 | 18W | Proposed | P1 | 21 | 2BRYAN A! | VL |  |  |  |  | 0.877 | 1.0251 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334005 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203019 | 18W | Proposed | P1 | 21 | 2HUMBHRN | VL |  |  |  |  | 0.887 | 1.018 | 0.92 | 1.05 | 1107 | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334005 2BRYAN A! 69.0 334020 4BRYAN! 138 1 |  |  | Solution: Adjust caps
203020 | 18W | Proposed | P1 | 21 | 2HEARNE! | VH |  |  |  |  | 1.0515 | 1.018 | 0.92 | 1.05 | 1109 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203021 | 18W | Proposed | P1 | 21 | 2TXHEARN | VH |  |  |  |  | 1.051 | 1.0185 | 0.92 | 1.05 | 1109 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203022 | 18W | Proposed | P1 | 21 | 2HUMBHRN | VH |  |  |  |  | 1.0516 | 1.018 | 0.92 | 1.05 | 1109 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203023 | 18W | Proposed | P1 | 21 | 2TESCO | VH |  |  |  |  | 1.0517 | 1.0181 | 0.92 | 1.05 | 1109 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334007 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203024 | 18W | Proposed | P1 | 21 | 4PEE DEE! | VH |  |  |  |  | 1.0508 | 1.0206 | 0.92 | 1.05 | 1141 | 334050 4PEE DEE! 138 334051 4BISHOP 138 1 | 334050 |  |  |  | 138 | 138 | 351 | EES |  |  | 334050 4PEE DEE! 138 334051 4BISHOP 138 1 |  |  | VH
203025 | 18W | Proposed | P1 | 21 | 4MAGROVE | VH |  |  |  |  | 1.0955 | 1.0202 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203026 | 18W | Proposed | P1 | 21 | 4L111T411 | VH |  |  |  |  | 1.0843 | 1.0175 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203027 | 18W | Proposed | P1 | 21 | 4KICKAPO | VH |  |  |  |  | 1.0841 | 1.0173 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203028 | 18W | Proposed | P1 | 21 | 4CORIGAN! | VH |  |  |  |  | 1.0735 | 1.0167 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203029 | 18W | Proposed | P1 | 21 | 4SHECORR | VH |  |  |  |  | 1.072 | 1.0161 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203030 | 18W | Proposed | P1 | 21 | 4CAMDEN | VH |  |  |  |  | 1.0654 | 1.0142 | 0.92 | 1.05 | 1220 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203031 | 18W | Proposed | P1 | 21 | 4CORIGAN! | VH |  |  |  |  | 1.0534 | 1.0167 | 0.92 | 1.05 | 1224 | 334129 4CORIGAN! 138 334130 4SHECORR 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334129 4CORIGAN! 138 334130 4SHECORR 138 1 |  |  | VH
203032 | 18W | Proposed | P1 | 21 | 2HIMEX | VH |  |  |  |  | 1.0519 | 1.026 | 0.92 | 1.05 | 1281 | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | 334225 4STOWELL! 138 334235 2STOWELL! 69.0 1 |  |  | VH
203033 | 18W | Proposed | P1 | 21 | 2PINELND | VL |  |  |  |  | 0.9155 | 0.9517 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203034 | 18W | Proposed | P1 | 21 | 2TEMPL1* | VL |  |  |  |  | 0.9136 | 0.9499 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203035 | 18W | Proposed | P1 | 21 | 2TEMPLE1 | VL |  |  |  |  | 0.9133 | 0.9496 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203036 | 18W | Proposed | P1 | 21 | 2TEMPL2* | VL |  |  |  |  | 0.9133 | 0.9495 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203037 | 18W | Proposed | P1 | 21 | 2TEMPLE2 | VL |  |  |  |  | 0.9131 | 0.9494 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203038 | 18W | Proposed | P1 | 21 | 2TMPLSWC | VL |  |  |  |  | 0.9131 | 0.9494 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203039 | 18W | Proposed | P1 | 21 | 2WEIRGAT | VL |  |  |  |  | 0.896 | 0.933 | 0.92 | 1.05 | 1312 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203040 | 18W | Proposed | P1 | 21 | 2PINELND | VL |  |  |  |  | 0.9102 | 0.9517 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203041 | 18W | Proposed | P1 | 21 | 2TEMPL1* | VL |  |  |  |  | 0.9083 | 0.9499 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203042 | 18W | Proposed | P1 | 21 | 2TEMPLE1 | VL |  |  |  |  | 0.9081 | 0.9496 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203043 | 18W | Proposed | P1 | 21 | 2TEMPL2* | VL |  |  |  |  | 0.908 | 0.9495 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203044 | 18W | Proposed | P1 | 21 | 2TEMPLE2 | VL |  |  |  |  | 0.9078 | 0.9494 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203045 | 18W | Proposed | P1 | 21 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9494 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203046 | 18W | Proposed | P1 | 21 | 2WEIRGAT | VL |  |  |  |  | 0.8906 | 0.933 | 0.92 | 1.05 | 1314 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203047 | 18W | Proposed | P1 | 21 | 2WEIRGAT | VL |  |  |  |  | 0.9111 | 0.933 | 0.92 | 1.05 | 1317 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203048 | 18W | Proposed | P1 | 21 | 2SERPENT | VL |  |  |  |  | 0.9183 | 0.9329 | 0.92 | 1.05 | 1662 | 335070 6CARLYSS% 230 335073 6BOUDOIN% 230 1 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | 335070 6CARLYSS% 230 335073 6BOUDOIN% 230 1 |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
203049 | 18W | Proposed | P1 | 21 | 2NESSER_TP | VL |  |  |  |  | 0.9167 | 0.9819 | 0.92 | 1.05 | 2001 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335671 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
203050 | 18W | Proposed | P1 | 21 | 2NESSER | VL |  |  |  |  | 0.9129 | 0.9783 | 0.92 | 1.05 | 2001 | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 | 335672 |  |  |  | 69 | 69 | 351 | EES |  |  | 335699 2HARELSON! 69.0 335710 2LN-372A_TP 69.0 1 |  | Project Proposed |  | 14-EGL-002-CP | 2020-06-01 | Construct Flannery 230 kV on Coly-Jaguar; Install 230-69 kV Auto; Reconfigure 69 kV Lines
203051 | 18W | Proposed | P1 | 21 | 3ASHLAND | VH |  |  |  |  | 1.0921 | 1.0071 | 0.92 | 1.05 | 2121 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203052 | 18W | Proposed | P1 | 21 | 3HOUMA! | VH |  |  |  |  | 1.1021 | 1.0112 | 0.92 | 1.05 | 2121 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203053 | 18W | Proposed | P1 | 21 | 3CHAVIN! | VH |  |  |  |  | 1.0755 | 1.0045 | 0.92 | 1.05 | 2121 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203054 | 18W | Proposed | P1 | 21 | HOUMA 3 | VH |  |  |  |  | 1.1021 | 1.0112 | 0.92 | 1.05 | 2121 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203055 | 18W | Proposed | P1 | 21 | 3GMEADW! | VH |  |  |  |  | 1.1753 | 1.0203 | 0.92 | 1.05 | 2150 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203056 | 18W | Proposed | P1 | 21 | 3LEEVLL | VH |  |  |  |  | 1.1984 | 1.0115 | 0.92 | 1.05 | 2150 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203057 | 18W | Proposed | P1 | 21 | 3FOURCHN | VH |  |  |  |  | 1.1981 | 1.0019 | 0.92 | 1.05 | 2150 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203058 | 18W | Proposed | P1 | 21 | 3CARLSL | VL |  |  |  |  | 0.883 | 0.9867 | 0.92 | 1.05 | 2160 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
203059 | 18W | Proposed | P1 | 21 | 3GILBERT | VL |  |  |  |  | 0.9121 | 1.0101 | 0.92 | 1.05 | 2300 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  | None
203060 | 18W | Proposed | P1 | 21 | 3METROPOLIS | VL |  |  |  |  | 0.9106 | 1.0131 | 0.92 | 1.05 | 2300 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
203061 | 18W | Proposed | P1 | 21 | 3WISNER | VL |  |  |  |  | 0.9108 | 1.0122 | 0.92 | 1.05 | 2300 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
203062 | 18W | Proposed | P1 | 21 | 3WINNSBORO! | VL |  |  |  |  | 0.9168 | 1.0078 | 0.92 | 1.05 | 2300 | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 337327 3RED_GUM! 115 337328 3METROPOLIS 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
203063 | 18W | Proposed | P1 | 21 | 3GILBERT | VL |  |  |  |  | 0.9195 | 1.0101 | 0.92 | 1.05 | 2302 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  | None
203064 | 18W | Proposed | P1 | 21 | 3WISNER | VL |  |  |  |  | 0.9188 | 1.0122 | 0.92 | 1.05 | 2302 | 337328 3METROPOLIS 115 337329 3WISNER 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 337328 3METROPOLIS 115 337329 3WISNER 115 1 |  |  | Solution: Adjust cap banks at Winnsboro and Wisner
203065 | 18W | Proposed | P1 | 21 | 3LUCKY | VH |  |  |  |  | 1.0501 | 1.0342 | 0.92 | 1.05 | 2316 | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337349 3LUCKY 115 337350 3TX_EAST_E 115 1 |  |  | VH
203066 | 18W | Proposed | P1 | 21 | 3LUCKY | VH |  |  |  |  | 1.0507 | 1.0342 | 0.92 | 1.05 | 2317 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
203067 | 18W | Proposed | P1 | 21 | 3TX_EAST_E | VH |  |  |  |  | 1.0508 | 1.0307 | 0.92 | 1.05 | 2317 | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 | 337350 |  |  |  | 115 | 115 | 351 | EES |  |  | 337350 3TX_EAST_E 115 337351 3SAILES! 115 1 |  |  | VH
203068 | 18W | Proposed | P1 | 21 | 3DELHI_LA! | VH |  |  |  |  | 1.0528 | 1.0149 | 0.92 | 1.05 | 2375 | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337448 3DELHI_LA! 115 337453 3DELHI_RX 115 R1 |  |  | VH
203069 | 18W | Proposed | P1 | 21 | 3DELHI_LA! | VH |  |  |  |  | 1.0528 | 1.0149 | 0.92 | 1.05 | 2379 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
203070 | 18W | Proposed | P1 | 21 | 3DELHI_RX | VH |  |  |  |  | 1.0528 | 1.0017 | 0.92 | 1.05 | 2379 | 337450 3CARSON 115 337453 3DELHI_RX 115 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | 337450 3CARSON 115 337453 3DELHI_RX 115 1 |  |  | VH
203071 | 18W | Proposed | P1 | 21 | 2SERPENT | VL |  |  |  |  | 0.9182 | 0.9329 | 0.92 | 1.05 | 2462 | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 | 335255 |  |  |  | 69 | 69 | 351 | EES |  |  | 303101 6MOSS_BLUFF! 230 335190 6NELSON% 230 1 |  | Project Proposed |  | 14-EGL-007-CP | 2019-12-01 | Upgrade Chlomal-Lacassine 69 kV
203072 | 18W | Proposed | P1 | 21 | 3ARCADIA | VH |  |  |  |  | 1.057 | 1.0247 | 0.92 | 1.05 | 2499 | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 | 337367 |  |  |  | 115 | 115 | 351 | EES |  |  | 303310 3TRUSSEL_CR 115 337367 3ARCADIA 115 1 |  |  | VH
203073 | 18W | Proposed | P1 | 21 | 3GILBERT | VH |  |  |  |  | 1.1233 | 1.0101 | 0.92 | 1.05 | 2514 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203074 | 18W | Proposed | P2 | 21 | 3RED_GUM! | VH |  |  |  |  | 1.0548 | 1.027 | 0.92 | 1.05 | 2514 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203075 | 18W | Proposed | P2 | 21 | 3METROPOLIS | VH |  |  |  |  | 1.1149 | 1.0131 | 0.92 | 1.05 | 2514 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203076 | 18W | Proposed | P2 | 21 | 3WISNER | VH |  |  |  |  | 1.1193 | 1.0122 | 0.92 | 1.05 | 2514 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203077 | 18W | Proposed | P2 | 21 | 3WINNSBORO! | VH |  |  |  |  | 1.1329 | 1.0078 | 0.92 | 1.05 | 2514 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203078 | 18W | Proposed | P1 | 21 | 4CANEY | VL |  |  |  |  | 0.8868 | 0.9995 | 0.92 | 1.05 | 2673 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203079 | 18W | Proposed | P1 | 21 | OAKDALE4 | VL |  |  |  |  | 0.8887 | 0.9981 | 0.92 | 1.05 | 2673 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203080 | 18W | Proposed | P1 | 21 | PNPRARIE 4 | VL |  |  |  |  | 0.8797 | 1.0094 | 0.92 | 1.05 | 2673 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203081 | 18W | Proposed | P1 | 21 | WSTBAY 4 | VL |  |  |  |  | 0.8984 | 0.9965 | 0.92 | 1.05 | 2673 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203082 | 18W | Proposed | P1 | 21 | PRICE 4 | VH |  |  |  |  | 1.0539 | 1.0431 | 0.92 | 1.05 | 2712 | 500590 NATCH 4 138 500730 PRICE 4 138 1 | 500730 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500590 NATCH 4 138 500730 PRICE 4 138 1 |  |  | VH
203083 | 18W | Proposed | P1 | 21 | 2WEIRGAT | VL |  |  |  |  | 0.9167 | 0.933 | 0.92 | 1.05 | 2756 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203084 | 18W | Proposed | P1 | 21 | ELKS 6 | VL |  |  |  |  | 0.8939 | 0.9978 | 0.92 | 1.05 | 2790 | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 |  |  | Facility: Radial
203085 | 18W | Proposed | P1 | 21 | 8THALMANN | VH |  |  |  |  | 1.0551 | 1.0425 | 0.92 | 1.05 | 2876 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
203086 | 18W | Proposed | P1 | 21 | 8MCCALL RD | VH |  |  |  |  | 1.0698 | 1.0325 | 0.92 | 1.05 | 2876 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
203087 | 18W | Proposed | P1 | 21 | 8THOMSON | VH |  |  |  |  | 1.0557 | 1.0384 | 0.92 | 1.05 | 3303 | 381413 6THOMSON 230 381490 8THOMSON 500 1 | 381490 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 381413 6THOMSON 230 381490 8THOMSON 500 1 |  |  | VH
203088 | 18W | Proposed | P1 | 21 | 8DANIEL | VH |  |  |  |  | 1.0759 | 1.042 | 0.92 | 1.05 | 3599 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
203089 | 18W | Proposed | P1 | 21 | 8LAG CRK CT | VH |  |  |  |  | 1.0568 | 1.0414 | 0.92 | 1.05 | 3948 | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360568 8LAG CRK CT 500 360615 8LAG CRK CC 500 1 |  |  | VH
203090 | 18W | Proposed | P1 | 21 | TENRUSK7 | VH |  |  |  |  | 1.0513 | 1.0185 | 0.92 | 1.05 | 4518 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
203091 | 18W | Proposed | P1 | 21 | TENGEN 7 | VH |  |  |  |  | 1.0513 | 1.0185 | 0.92 | 1.05 | 4518 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
203092 | 18W | Proposed | P1 | 21 | ELKCITY7 | VH |  |  |  |  | 1.0537 | 1.0295 | 0.92 | 1.05 | 4559 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
203093 | 18W | Proposed | P0 | 22 | 5HORN LAKE% | VH |  |  |  |  | 1.0604 | 1.0604 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
203094 | 18W | Proposed | P0 | 22 | 8UNION MS | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 | 0 | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203095 | 18W | Proposed | P0 | 22 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 | 0 | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203096 | 18W | Proposed | P0 | 22 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 | 0 | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203097 | 18W | Proposed | P0 | 22 | 8PLEASANT HL | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 | 0 | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203098 | 18W | Proposed | P0 | 22 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203099 | 18W | Proposed | P0 | 22 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203100 | 18W | Proposed | P1 | 22 | 4NEW_IBERIA! | VL |  |  |  |  | 0.9087 | 1.0088 | 0.92 | 1.05 | 5 | P1_2-562-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-562-a |  |  | Contingency: Trip bus as result of con
203101 | 18W | Proposed | P1 | 22 | 4NEW_IBERIA! | VL |  |  |  |  | 0.9087 | 1.0088 | 0.92 | 1.05 | 6 | P1_2-568-a | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-568-a |  |  | Contingency: Trip bus as result of con
203102 | 23S | Proposed | P0 | 23 | 2WEIRGAT | VL |  |  |  |  | 0.9153 | 0.9153 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203103 | 23S | Proposed | P0 | 23 | 5HORN LAKE% | VH |  |  |  |  | 1.0567 | 1.0567 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
203104 | 23S | Proposed | P0 | 23 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203105 | 23S | Proposed | P0 | 23 | 8CENTRLAL | VH |  |  |  |  | 1.05 | 1.05 | 0.92 | 1.05 | 0 | ** Base Case ** | 385337 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203106 | 23S | Proposed | P1 | 23 | 2PINELND | VL |  |  |  |  | 0.9144 | 0.9297 | 0.92 | 1.05 | 30 | G-334282-1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203107 | 23S | Proposed | P1 | 23 | 2TEMPL1* | VL |  |  |  |  | 0.9124 | 0.9277 | 0.92 | 1.05 | 30 | G-334282-1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203108 | 23S | Proposed | P1 | 23 | 2TEMPLE1 | VL |  |  |  |  | 0.912 | 0.9273 | 0.92 | 1.05 | 30 | G-334282-1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203109 | 23S | Proposed | P1 | 23 | 2TEMPL2* | VL |  |  |  |  | 0.9121 | 0.9274 | 0.92 | 1.05 | 30 | G-334282-1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203110 | 23S | Proposed | P1 | 23 | 2TEMPLE2 | VL |  |  |  |  | 0.9119 | 0.9272 | 0.92 | 1.05 | 30 | G-334282-1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203111 | 23S | Proposed | P1 | 23 | 2TMPLSWC | VL |  |  |  |  | 0.912 | 0.9273 | 0.92 | 1.05 | 30 | G-334282-1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203112 | 23S | Proposed | P1 | 23 | 2WEIRGAT | VL |  |  |  |  | 0.8997 | 0.9153 | 0.92 | 1.05 | 30 | G-334282-1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | G-334282-1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203113 | 23S | Proposed | P1 | 23 | 3NATCHEZSES% | VH |  |  |  |  | 1.0562 | 1.0321 | 0.92 | 1.05 | 368 | P1_2-116 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203114 | 23S | Proposed | P1 | 23 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0557 | 1.0317 | 0.92 | 1.05 | 368 | P1_2-116 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203115 | 23S | Proposed | P1 | 23 | 3PINE RIDGE | VH |  |  |  |  | 1.0553 | 1.0314 | 0.92 | 1.05 | 368 | P1_2-116 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203116 | 23S | Proposed | P1 | 23 | 3NATCHEZ! | VH |  |  |  |  | 1.055 | 1.0314 | 0.92 | 1.05 | 368 | P1_2-116 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203117 | 23S | Proposed | P1 | 23 | 3J.MANVILLE | VH |  |  |  |  | 1.0527 | 1.0288 | 0.92 | 1.05 | 368 | P1_2-116 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203118 | 23S | Proposed | P1 | 23 | 3INTL PAPER | VH |  |  |  |  | 1.0516 | 1.028 | 0.92 | 1.05 | 368 | P1_2-116 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203119 | 23S | Proposed | P1 | 23 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0507 | 1.0274 | 0.92 | 1.05 | 368 | P1_2-116 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203120 | 23S | Proposed | P1 | 23 | 3WASHINGTON+ | VH |  |  |  |  | 1.0514 | 1.0287 | 0.92 | 1.05 | 368 | P1_2-116 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203121 | 23S | Proposed | P1 | 23 | 3FAYETTE | VH |  |  |  |  | 1.0617 | 1.0408 | 0.92 | 1.05 | 368 | P1_2-116 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203122 | 23S | Proposed | P1 | 23 | 3LORMAN+ | VH |  |  |  |  | 1.0537 | 1.0351 | 0.92 | 1.05 | 368 | P1_2-116 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203123 | 23S | Proposed | P1 | 23 | 3LORMAN | VH |  |  |  |  | 1.0535 | 1.0349 | 0.92 | 1.05 | 368 | P1_2-116 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203124 | 23S | Proposed | P1 | 23 | 3PORTGIBSON! | VH |  |  |  |  | 1.052 | 1.0356 | 0.92 | 1.05 | 368 | P1_2-116 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203125 | 23S | Proposed | P1 | 23 | 3GGNS | VH |  |  |  |  | 1.051 | 1.0345 | 0.975 | 1.05 | 368 | P1_2-116 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203126 | 23S | Proposed | P1 | 23 | 3RED_GUM! | VH |  |  |  |  | 1.0618 | 1.0282 | 0.92 | 1.05 | 368 | P1_2-116 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203127 | 23S | Proposed | P1 | 23 | 3METROPOLIS | VH |  |  |  |  | 1.0575 | 1.0306 | 0.92 | 1.05 | 368 | P1_2-116 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203128 | 23S | Proposed | P1 | 23 | 3WISNER | VH |  |  |  |  | 1.0574 | 1.031 | 0.92 | 1.05 | 368 | P1_2-116 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! |  |  | VH
203129 | 23S | Proposed | P1 | 23 | 2CALVERT! | VH |  |  |  |  | 1.0503 | 1.003 | 0.92 | 1.05 | 376 | P1_2-124 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
203130 | 23S | Proposed | P1 | 23 | 2SINHERN | VH |  |  |  |  | 1.0616 | 1.0163 | 0.92 | 1.05 | 376 | P1_2-124 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
203131 | 23S | Proposed | P1 | 23 | 2HEARNE! | VH |  |  |  |  | 1.0734 | 1.0298 | 0.92 | 1.05 | 376 | P1_2-124 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
203132 | 23S | Proposed | P1 | 23 | 2TXHEARN | VH |  |  |  |  | 1.072 | 1.0298 | 0.92 | 1.05 | 376 | P1_2-124 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
203133 | 23S | Proposed | P1 | 23 | 2APLHERN | VH |  |  |  |  | 1.0683 | 1.0297 | 0.92 | 1.05 | 376 | P1_2-124 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-124 |  |  | VH
203134 | 23S | Proposed | P1 | 23 | 2PINELND | VL |  |  |  |  | 0.8889 | 0.9297 | 0.92 | 1.05 | 487 | P1_2-237 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203135 | 23S | Proposed | P1 | 23 | 2TEMPL1* | VL |  |  |  |  | 0.8868 | 0.9277 | 0.92 | 1.05 | 487 | P1_2-237 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203136 | 23S | Proposed | P1 | 23 | 2TEMPLE1 | VL |  |  |  |  | 0.8865 | 0.9273 | 0.92 | 1.05 | 487 | P1_2-237 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203137 | 23S | Proposed | P1 | 23 | 2TEMPL2* | VL |  |  |  |  | 0.8865 | 0.9274 | 0.92 | 1.05 | 487 | P1_2-237 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203138 | 23S | Proposed | P1 | 23 | 2TEMPLE2 | VL |  |  |  |  | 0.8863 | 0.9272 | 0.92 | 1.05 | 487 | P1_2-237 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203139 | 23S | Proposed | P1 | 23 | 2TMPLSWC | VL |  |  |  |  | 0.8864 | 0.9273 | 0.92 | 1.05 | 487 | P1_2-237 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203140 | 23S | Proposed | P1 | 23 | 2WEIRGAT | VL |  |  |  |  | 0.8738 | 0.9153 | 0.92 | 1.05 | 487 | P1_2-237 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203141 | 23S | Proposed | P1 | 23 | 4PINELND | VL |  |  |  |  | 0.9181 | 0.9883 | 0.92 | 1.05 | 489 | P1_2-239 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203142 | 23S | Proposed | P1 | 23 | 4HRTNHIL | VL |  |  |  |  | 0.9162 | 0.9911 | 0.92 | 1.05 | 489 | P1_2-239 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203143 | 23S | Proposed | P1 | 23 | 2PINELND | VL |  |  |  |  | 0.8614 | 0.9297 | 0.92 | 1.05 | 489 | P1_2-239 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203144 | 23S | Proposed | P1 | 23 | 2TEMPL1* | VL |  |  |  |  | 0.8592 | 0.9277 | 0.92 | 1.05 | 489 | P1_2-239 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203145 | 23S | Proposed | P1 | 23 | 2TEMPLE1 | VL |  |  |  |  | 0.8588 | 0.9273 | 0.92 | 1.05 | 489 | P1_2-239 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203146 | 23S | Proposed | P1 | 23 | 2TEMPL2* | VL |  |  |  |  | 0.8589 | 0.9274 | 0.92 | 1.05 | 489 | P1_2-239 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203147 | 23S | Proposed | P1 | 23 | 2TEMPLE2 | VL |  |  |  |  | 0.8587 | 0.9272 | 0.92 | 1.05 | 489 | P1_2-239 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203148 | 23S | Proposed | P1 | 23 | 2TMPLSWC | VL |  |  |  |  | 0.8588 | 0.9273 | 0.92 | 1.05 | 489 | P1_2-239 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203149 | 23S | Proposed | P1 | 23 | 2WEIRGAT | VL |  |  |  |  | 0.8458 | 0.9153 | 0.92 | 1.05 | 489 | P1_2-239 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203150 | 23S | Proposed | P1 | 23 | 2CARTER! | VH |  |  |  |  | 1.0534 | 1.0206 | 0.92 | 1.05 | 767 | P1_2-518 | 335254 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-518 |  |  | VH
203151 | 23S | Proposed | P1 | 23 | 2PARKS | VL |  |  |  |  | 0.9185 | 0.9973 | 0.92 | 1.05 | 829 | P1_2-581 | 335425 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-581 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
203152 | 23S | Proposed | P1 | 23 | 2ST_JOHN | VL |  |  |  |  | 0.9189 | 0.9901 | 0.92 | 1.05 | 829 | P1_2-581 | 335426 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-581 |  | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
203153 | 23S | Proposed | P1 | 23 | 3PVILLE! | VH |  |  |  |  | 1.0507 | 1.0155 | 0.92 | 1.05 | 1038 | P1_2-793 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-793 |  |  | VH
203154 | 23S | Proposed | P1 | 23 | 3HOUMA! | VH |  |  |  |  | 1.0526 | 1.0145 | 0.92 | 1.05 | 1047 | P1_2-802 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
203155 | 23S | Proposed | P1 | 23 | HOUMA 3 | VH |  |  |  |  | 1.0526 | 1.0145 | 0.92 | 1.05 | 1047 | P1_2-802 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! |  |  | VH
203156 | 23S | Proposed | P1 | 23 | 3CHAVIN! | VH |  |  |  |  | 1.0512 | 1.0254 | 0.92 | 1.05 | 1050 | P1_2-805 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-805 |  |  | VH
203157 | 23S | Proposed | P1 | 23 | 3GMEADW! | VH |  |  |  |  | 1.1482 | 1.0153 | 0.92 | 1.05 | 1052 | P1_2-807 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
203158 | 23S | Proposed | P1 | 23 | 3LEEVLL | VH |  |  |  |  | 1.1664 | 1.003 | 0.92 | 1.05 | 1052 | P1_2-807 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
203159 | 23S | Proposed | P1 | 23 | 3FOURCHN | VH |  |  |  |  | 1.1651 | 0.9927 | 0.92 | 1.05 | 1052 | P1_2-807 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! |  |  | VH
203160 | 23S | Proposed | P1 | 23 | 3GILBERT | VH |  |  |  |  | 1.0848 | 1.0235 | 0.92 | 1.05 | 1423 | P1_2-1178 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  |  | VH
203161 | 23S | Proposed | P1 | 23 | 3METROPOLIS | VH |  |  |  |  | 1.0813 | 1.0306 | 0.92 | 1.05 | 1423 | P1_2-1178 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  |  | VH
203162 | 23S | Proposed | P1 | 23 | 3WISNER | VH |  |  |  |  | 1.0843 | 1.031 | 0.92 | 1.05 | 1423 | P1_2-1178 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  |  | VH
203163 | 23S | Proposed | P1 | 23 | 3WINNSBORO! | VH |  |  |  |  | 1.0896 | 1.0129 | 0.92 | 1.05 | 1423 | P1_2-1178 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! |  |  | VH
203164 | 23S | Proposed | P1 | 23 | 3JNCTN CITY! | VH |  |  |  |  | 1.0571 | 1.0269 | 0.92 | 1.05 | 1522 | P1_2-1277 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1277 |  |  | VH
203165 | 23S | Proposed | P1 | 23 | 3MT PINE.S% | VL |  |  |  |  | 0.8313 | 0.9921 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203166 | 23S | Proposed | P1 | 23 | 3ROYAL | VL |  |  |  |  | 0.8425 | 0.989 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203167 | 23S | Proposed | P1 | 23 | 3MILTON | VL |  |  |  |  | 0.8692 | 0.9852 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203168 | 23S | Proposed | P1 | 23 | 3HS.W | VL |  |  |  |  | 0.8181 | 0.9872 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203169 | 23S | Proposed | P1 | 23 | 3HS.S | VL |  |  |  |  | 0.8103 | 0.9854 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203170 | 23S | Proposed | P1 | 23 | 3ALBRIGHT | VL |  |  |  |  | 0.904 | 0.9854 | 0.92 | 1.05 | 1584 | P1_2-1341 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1341 |  |  | Contingency: invalid after Albright
203171 | 23S | Proposed | P1 | 23 | 8SANS SOUCI% | VH |  |  |  |  | 1.0524 | 1.0352 | 0.92 | 1.05 | 1756 | P1_2-1519 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1519 |  |  | VH
203172 | 23S | Proposed | P1 | 23 | 2THAYER.S! | VL |  |  |  |  | 0.9187 | 1.0156 | 0.92 | 1.05 | 1771 | P1_2-1534 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!,3WALNUT RDG! |  | Turn on switch shunt at Couch 69 kV sub
203173 | 23S | Proposed | P1 | 23 | 8DANIEL | VH |  |  |  |  | 1.0762 | 1.0426 | 0.92 | 1.05 | 1841 | P1_2-1604 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! |  |  | VH
203174 | 23S | Proposed | P1 | 23 | CLARN 2 | VH |  |  |  |  | 1.1547 | 1.0318 | 0.92 | 1.05 | 1871 | P1_2-1634 | 500165 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1634_CARROLL6!,MESSICK6! |  |  | VH
203175 | 23S | Proposed | P1 | 23 | 4CANEY | VL |  |  |  |  | 0.8633 | 0.9926 | 0.92 | 1.05 | 1890 | P1_2-1653 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
203176 | 23S | Proposed | P1 | 23 | CENTNL 4 | VL |  |  |  |  | 0.9119 | 0.9889 | 0.92 | 1.05 | 1890 | P1_2-1653 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
203177 | 23S | Proposed | P1 | 23 | OAKDALE4 | VL |  |  |  |  | 0.8653 | 0.9906 | 0.92 | 1.05 | 1890 | P1_2-1653 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
203178 | 23S | Proposed | P1 | 23 | PNPRARIE 4 | VL |  |  |  |  | 0.8561 | 1.0056 | 0.92 | 1.05 | 1890 | P1_2-1653 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
203179 | 23S | Proposed | P1 | 23 | WSTBAY 4 | VL |  |  |  |  | 0.8772 | 0.9887 | 0.92 | 1.05 | 1890 | P1_2-1653 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4%
203180 | 23S | Proposed | P1 | 23 | 4VEAZIE | VL |  |  |  |  | 0.9007 | 0.9812 | 0.92 | 1.05 | 1891 | P1_2-1654 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203181 | 23S | Proposed | P1 | 23 | GROLEE 2 | VL |  |  |  |  | 0.9123 | 1.0009 | 0.92 | 1.05 | 1891 | P1_2-1654 | 500370 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203182 | 23S | Proposed | P1 | 23 | GUIDRY 4 | VL |  |  |  |  | 0.8994 | 0.9799 | 0.92 | 1.05 | 1891 | P1_2-1654 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203183 | 23S | Proposed | P1 | 23 | GUIDRY 2 | VL |  |  |  |  | 0.9131 | 1.0017 | 0.92 | 1.05 | 1891 | P1_2-1654 | 500390 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203184 | 23S | Proposed | P1 | 23 | PLAISAN4 | VL |  |  |  |  | 0.9151 | 0.9942 | 0.92 | 1.05 | 1891 | P1_2-1654 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203185 | 23S | Proposed | P1 | 23 | S PARK 2 | VL |  |  |  |  | 0.9094 | 0.9983 | 0.92 | 1.05 | 1891 | P1_2-1654 | 500810 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! |  | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
203186 | 23S | Proposed | P1 | 23 | TENRUSK7 | VH |  |  |  |  | 1.0503 | 1.0147 | 0.92 | 1.05 | 2100 | P1_2-1863 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
203187 | 23S | Proposed | P1 | 23 | TENGEN 7 | VH |  |  |  |  | 1.0503 | 1.0147 | 0.92 | 1.05 | 2100 | P1_2-1863 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863 |  |  | VH
203188 | 23S | Proposed | P0 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.9153 | 0.9153 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203189 | 23S | Proposed | P0 | 24 | 5HORN LAKE% | VH |  |  |  |  | 1.0567 | 1.0567 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
203190 | 23S | Proposed | P0 | 24 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203191 | 23S | Proposed | P0 | 24 | 8CENTRLAL | VH |  |  |  |  | 1.05 | 1.05 | 0.92 | 1.05 | 0 | ** Base Case ** | 385337 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203192 | 23S | Proposed | P1 | 24 | 3FAYETTE | VH |  |  |  |  | 1.0834 | 1.0408 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203193 | 23S | Proposed | P1 | 24 | 3LORMAN+ | VH |  |  |  |  | 1.0725 | 1.0351 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203194 | 23S | Proposed | P1 | 24 | 3LORMAN | VH |  |  |  |  | 1.0723 | 1.0349 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203195 | 23S | Proposed | P1 | 24 | 3PORTGIBSON! | VH |  |  |  |  | 1.0681 | 1.0356 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203196 | 23S | Proposed | P1 | 24 | 3GGNS | VH |  |  |  |  | 1.0671 | 1.0345 | 0.975 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203197 | 23S | Proposed | P1 | 24 | 3S.VICKSBURG | VH |  |  |  |  | 1.05 | 1.0327 | 0.92 | 1.05 | 4 | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336500 3NATCHEZSES% 115 336785 3FAYETTE 115 1 |  |  | VH
203198 | 23S | Proposed | P1 | 24 | 3CHATAWA+ | VH |  |  |  |  | 1.0612 | 1.0286 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
203199 | 23S | Proposed | P1 | 24 | 3COLNIAL P/L | VH |  |  |  |  | 1.0707 | 1.0306 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
203200 | 23S | Proposed | P1 | 24 | 3FERNWOOD MS | VH |  |  |  |  | 1.0753 | 1.0283 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
203201 | 23S | Proposed | P1 | 24 | 3PROGRESS+ | VH |  |  |  |  | 1.0625 | 1.015 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
203202 | 23S | Proposed | P1 | 24 | 3PLANT.P/L | VH |  |  |  |  | 1.0624 | 1.0149 | 0.92 | 1.05 | 34 | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336537 3FERNWOOD MS 115 336539 3OAKDALE+ 115 1 |  |  | VH
203203 | 23S | Proposed | P1 | 24 | 3NATCHEZSES% | VH |  |  |  |  | 1.0571 | 1.0321 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203204 | 23S | Proposed | P1 | 24 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0564 | 1.0317 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203205 | 23S | Proposed | P1 | 24 | 3PINE RIDGE | VH |  |  |  |  | 1.056 | 1.0314 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203206 | 23S | Proposed | P1 | 24 | 3NATCHEZ! | VH |  |  |  |  | 1.055 | 1.0314 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203207 | 23S | Proposed | P1 | 24 | 3J.MANVILLE | VH |  |  |  |  | 1.052 | 1.0288 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203208 | 23S | Proposed | P1 | 24 | 3INTL PAPER | VH |  |  |  |  | 1.0507 | 1.028 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203209 | 23S | Proposed | P1 | 24 | 3WASHINGTON+ | VH |  |  |  |  | 1.051 | 1.0287 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203210 | 23S | Proposed | P1 | 24 | 3FAYETTE | VH |  |  |  |  | 1.0904 | 1.0408 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203211 | 23S | Proposed | P1 | 24 | 3LORMAN+ | VH |  |  |  |  | 1.1035 | 1.0351 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203212 | 23S | Proposed | P1 | 24 | 3LORMAN | VH |  |  |  |  | 1.1033 | 1.0349 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203213 | 23S | Proposed | P1 | 24 | 3PORTGIBSON! | VH |  |  |  |  | 1.1197 | 1.0356 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203214 | 23S | Proposed | P1 | 24 | 3GGNS | VH |  |  |  |  | 1.1187 | 1.0345 | 0.975 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203215 | 23S | Proposed | P1 | 24 | 3S.VICKSBURG | VH |  |  |  |  | 1.1461 | 1.0327 | 0.92 | 1.05 | 93 | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 | 336790 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336790 3S.VICKSBURG 115 336800 3BXTRWILSON% 115 1 |  |  | VH
203216 | 23S | Proposed | P2 | 24 | 3S.REDWOOD+ | VL |  |  |  |  | 0.9183 | 1.0048 | 0.92 | 1.05 | 215 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 336965 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | None
203217 | 23S | Proposed | P2 | 24 | 3REDWOOD+ | VL |  |  |  |  | 0.9191 | 1.0031 | 0.92 | 1.05 | 215 | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 | 336966 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | 336963 3N.VICKSBRG! 115 336965 3S.REDWOOD+ 115 1 |  | None
203218 | 23S | Proposed | P1 | 24 | 3JNCTN CITY! | VH |  |  |  |  | 1.0567 | 1.0269 | 0.92 | 1.05 | 470 | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 | 337549 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337547 3UPLAND+ 115 337549 3JNCTN CITY! 115 1 |  |  | VH
203219 | 23S | Proposed | P2 | 24 | 3BRYANT | VL |  |  |  |  | 0.9191 | 0.9909 | 0.92 | 1.05 | 641 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 337803 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
203220 | 23S | Proposed | P2 | 24 | 3BRYANT.S# | VL |  |  |  |  | 0.9194 | 0.9878 | 0.92 | 1.05 | 641 | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 | 338757 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | 337799 3MABLVALE-W! 115 337803 3BRYANT 115 1 |  | Project Horizon |  | 13-EAI-005-HZ | 2021-06-01 | Bryant: Install 21.6 Mvar capacitor bank
203221 | 23S | Proposed | P1 | 24 | 2HARRISON.S | VH |  |  |  |  | 1.0504 | 1.0347 | 0.92 | 1.05 | 843 | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 | 338552 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338100 5BERRYVILLE 161 338682 5OSAGE CRK#! 161 1 |  |  | VH
203222 | 23S | Proposed | P1 | 24 | 8SANS SOUCI% | VH |  |  |  |  | 1.0524 | 1.0352 | 0.92 | 1.05 | 914 | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 338187 8DELL% 500 338188 8SANS SOUCI% 500 1 |  |  | VH
203223 | 23S | Proposed | P1 | 24 | 2THAYER.S! | VL |  |  |  |  | 0.9187 | 1.0156 | 0.92 | 1.05 | 942 | 338215 5THAYER.S! 161 338216 2THAYER.S! 69.0 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | 338215 5THAYER.S! 161 338216 2THAYER.S! 69.0 1 |  | Turn on switch shunt at Couch 69 kV sub
203224 | 23S | Proposed | P1 | 24 | 2CALVERT! | VH |  |  |  |  | 1.0508 | 1.003 | 0.92 | 1.05 | 1122 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
203225 | 23S | Proposed | P1 | 24 | 2SINHERN | VH |  |  |  |  | 1.062 | 1.0163 | 0.92 | 1.05 | 1122 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
203226 | 23S | Proposed | P1 | 24 | 2HEARNE! | VH |  |  |  |  | 1.0738 | 1.0298 | 0.92 | 1.05 | 1122 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
203227 | 23S | Proposed | P1 | 24 | 2TXHEARN | VH |  |  |  |  | 1.0724 | 1.0298 | 0.92 | 1.05 | 1122 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
203228 | 23S | Proposed | P1 | 24 | 2APLHERN | VH |  |  |  |  | 1.0687 | 1.0297 | 0.92 | 1.05 | 1122 | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334002 2HEARNE! 69.0 334006 2HUMBHRN 69.0 1 |  |  | VH
203229 | 23S | Proposed | P1 | 24 | 2CALVERT! | VH |  |  |  |  | 1.0511 | 1.003 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203230 | 23S | Proposed | P1 | 24 | 2SINHERN | VH |  |  |  |  | 1.0623 | 1.0163 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203231 | 23S | Proposed | P1 | 24 | 2HEARNE! | VH |  |  |  |  | 1.0741 | 1.0298 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203232 | 23S | Proposed | P1 | 24 | 2TXHEARN | VH |  |  |  |  | 1.0727 | 1.0298 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203233 | 23S | Proposed | P1 | 24 | 2APLHERN | VH |  |  |  |  | 1.0689 | 1.0297 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203234 | 23S | Proposed | P1 | 24 | 2HUMBHRN | VH |  |  |  |  | 1.0741 | 1.0294 | 0.92 | 1.05 | 1126 | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334006 2HUMBHRN 69.0 334007 2TESCO 69.0 1 |  |  | VH
203235 | 23S | Proposed | P1 | 24 | 2CALVERT! | VH |  |  |  |  | 1.0534 | 1.003 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334000 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203236 | 23S | Proposed | P1 | 24 | 2SINHERN | VH |  |  |  |  | 1.0645 | 1.0163 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334001 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203237 | 23S | Proposed | P1 | 24 | 2HEARNE! | VH |  |  |  |  | 1.0762 | 1.0298 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334002 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203238 | 23S | Proposed | P1 | 24 | 2TXHEARN | VH |  |  |  |  | 1.0747 | 1.0298 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334003 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203239 | 23S | Proposed | P1 | 24 | 2APLHERN | VH |  |  |  |  | 1.0708 | 1.0297 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334004 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203240 | 23S | Proposed | P1 | 24 | 2HUMBHRN | VH |  |  |  |  | 1.0763 | 1.0294 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334006 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203241 | 23S | Proposed | P1 | 24 | 2TESCO | VH |  |  |  |  | 1.0764 | 1.028 | 0.92 | 1.05 | 1127 | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 | 334007 |  |  |  | 69 | 69 | 351 | EES |  |  | 334007 2TESCO 69.0 334008 2BRYAN B! 69.0 1 |  |  | VH
203242 | 23S | Proposed | P1 | 24 | 4MAGROVE | VH |  |  |  |  | 1.0865 | 1.0106 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203243 | 23S | Proposed | P1 | 24 | 4L111T411 | VH |  |  |  |  | 1.0754 | 1.0083 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203244 | 23S | Proposed | P1 | 24 | 4KICKAPO | VH |  |  |  |  | 1.0753 | 1.0081 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203245 | 23S | Proposed | P1 | 24 | 4CORIGAN! | VH |  |  |  |  | 1.0647 | 1.008 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203246 | 23S | Proposed | P1 | 24 | 4SHECORR | VH |  |  |  |  | 1.0633 | 1.0075 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203247 | 23S | Proposed | P1 | 24 | 4CAMDEN | VH |  |  |  |  | 1.057 | 1.006 | 0.92 | 1.05 | 1239 | 334125 4STALEY! 138 334126 4MAGROVE 138 1 | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | 334125 4STALEY! 138 334126 4MAGROVE 138 1 |  |  | VH
203248 | 23S | Proposed | P1 | 24 | 26L594TAP | VL |  |  |  |  | 0.9193 | 0.9537 | 0.92 | 1.05 | 1282 | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 | 334252 |  |  |  | 69 | 69 | 351 | EES |  |  | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203249 | 23S | Proposed | P1 | 24 | 2HARDIN | VL |  |  |  |  | 0.9151 | 0.9497 | 0.92 | 1.05 | 1282 | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 | 334253 |  |  |  | 69 | 69 | 351 | EES |  |  | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203250 | 23S | Proposed | P1 | 24 | 2QUALTY | VL |  |  |  |  | 0.9173 | 0.9519 | 0.92 | 1.05 | 1282 | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 | 334254 |  |  |  | 69 | 69 | 351 | EES |  |  | 334210 4ADAYTON! 138 334212 4LIBERTY-SR 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203251 | 23S | Proposed | P1 | 24 | 26L594TAP | VL |  |  |  |  | 0.9193 | 0.9537 | 0.92 | 1.05 | 1289 | 334214 4DEVERS 138 334215 4CHINA% 138 1 | 334252 |  |  |  | 69 | 69 | 351 | EES |  |  | 334214 4DEVERS 138 334215 4CHINA% 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203252 | 23S | Proposed | P1 | 24 | 2HARDIN | VL |  |  |  |  | 0.9151 | 0.9497 | 0.92 | 1.05 | 1289 | 334214 4DEVERS 138 334215 4CHINA% 138 1 | 334253 |  |  |  | 69 | 69 | 351 | EES |  |  | 334214 4DEVERS 138 334215 4CHINA% 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203253 | 23S | Proposed | P1 | 24 | 2QUALTY | VL |  |  |  |  | 0.9174 | 0.9519 | 0.92 | 1.05 | 1289 | 334214 4DEVERS 138 334215 4CHINA% 138 1 | 334254 |  |  |  | 69 | 69 | 351 | EES |  |  | 334214 4DEVERS 138 334215 4CHINA% 138 1 |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
203254 | 23S | Proposed | P1 | 24 | 2PINELND | VL |  |  |  |  | 0.8889 | 0.9297 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203255 | 23S | Proposed | P1 | 24 | 2TEMPL1* | VL |  |  |  |  | 0.8868 | 0.9277 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203256 | 23S | Proposed | P1 | 24 | 2TEMPLE1 | VL |  |  |  |  | 0.8865 | 0.9273 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203257 | 23S | Proposed | P1 | 24 | 2TEMPL2* | VL |  |  |  |  | 0.8865 | 0.9274 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203258 | 23S | Proposed | P1 | 24 | 2TEMPLE2 | VL |  |  |  |  | 0.8863 | 0.9272 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203259 | 23S | Proposed | P1 | 24 | 2TMPLSWC | VL |  |  |  |  | 0.8864 | 0.9273 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203260 | 23S | Proposed | P1 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.8738 | 0.9153 | 0.92 | 1.05 | 1334 | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334282 4RAYBURN% 138 334283 4MILLCR! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203261 | 23S | Proposed | P1 | 24 | 4PINELND | VL |  |  |  |  | 0.9181 | 0.9883 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203262 | 23S | Proposed | P1 | 24 | 4HRTNHIL | VL |  |  |  |  | 0.9162 | 0.9911 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203263 | 23S | Proposed | P1 | 24 | 2PINELND | VL |  |  |  |  | 0.8614 | 0.9297 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203264 | 23S | Proposed | P1 | 24 | 2TEMPL1* | VL |  |  |  |  | 0.8592 | 0.9277 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203265 | 23S | Proposed | P1 | 24 | 2TEMPLE1 | VL |  |  |  |  | 0.8588 | 0.9273 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203266 | 23S | Proposed | P1 | 24 | 2TEMPL2* | VL |  |  |  |  | 0.8589 | 0.9274 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203267 | 23S | Proposed | P1 | 24 | 2TEMPLE2 | VL |  |  |  |  | 0.8587 | 0.9272 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203268 | 23S | Proposed | P1 | 24 | 2TMPLSWC | VL |  |  |  |  | 0.8588 | 0.9273 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203269 | 23S | Proposed | P1 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.8458 | 0.9153 | 0.92 | 1.05 | 1336 | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334283 4MILLCR! 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203270 | 23S | Proposed | P1 | 24 | 2PINELND | VL |  |  |  |  | 0.889 | 0.9297 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203271 | 23S | Proposed | P1 | 24 | 2TEMPL1* | VL |  |  |  |  | 0.8869 | 0.9277 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203272 | 23S | Proposed | P1 | 24 | 2TEMPLE1 | VL |  |  |  |  | 0.8865 | 0.9273 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203273 | 23S | Proposed | P1 | 24 | 2TEMPL2* | VL |  |  |  |  | 0.8866 | 0.9274 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203274 | 23S | Proposed | P1 | 24 | 2TEMPLE2 | VL |  |  |  |  | 0.8864 | 0.9272 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203275 | 23S | Proposed | P1 | 24 | 2TMPLSWC | VL |  |  |  |  | 0.8865 | 0.9273 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203276 | 23S | Proposed | P1 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.8739 | 0.9153 | 0.92 | 1.05 | 1339 | 334284 4PINELND 138 334287 4HRTNHIL 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334284 4PINELND 138 334287 4HRTNHIL 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203277 | 23S | Proposed | P1 | 24 | 2PINELND | VL |  |  |  |  | 0.9168 | 0.9297 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203278 | 23S | Proposed | P1 | 24 | 2TEMPL1* | VL |  |  |  |  | 0.9147 | 0.9277 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203279 | 23S | Proposed | P1 | 24 | 2TEMPLE1 | VL |  |  |  |  | 0.9144 | 0.9273 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203280 | 23S | Proposed | P1 | 24 | 2TEMPL2* | VL |  |  |  |  | 0.9144 | 0.9274 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203281 | 23S | Proposed | P1 | 24 | 2TEMPLE2 | VL |  |  |  |  | 0.9143 | 0.9272 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203282 | 23S | Proposed | P1 | 24 | 2TMPLSWC | VL |  |  |  |  | 0.9143 | 0.9273 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203283 | 23S | Proposed | P1 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.9021 | 0.9153 | 0.92 | 1.05 | 1357 | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | 334308 4JNE EVA 138 334309 4EVADALE! 138 1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203284 | 23S | Proposed | P1 | 24 | 2CARTER! | VH |  |  |  |  | 1.0534 | 1.0206 | 0.92 | 1.05 | 1772 | 335254 2CARTER! 69.0 335255 2SERPENT 69.0 1 | 335254 |  |  |  | 69 | 69 | 351 | EES |  |  | 335254 2CARTER! 69.0 335255 2SERPENT 69.0 1 |  |  | VH
203285 | 23S | Proposed | P1 | 24 | 3PVILLE! | VH |  |  |  |  | 1.0507 | 1.0155 | 0.92 | 1.05 | 2136 | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | 336017 3PVILLE! 115 336018 3NAPOLN 115 1 |  |  | VH
203286 | 23S | Proposed | P1 | 24 | 3HOUMA! | VH |  |  |  |  | 1.0526 | 1.0145 | 0.92 | 1.05 | 2146 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203287 | 23S | Proposed | P1 | 24 | HOUMA 3 | VH |  |  |  |  | 1.0526 | 1.0145 | 0.92 | 1.05 | 2146 | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | 336034 3COTEAU! 115 336035 3HOUMA! 115 1 |  |  | VH
203288 | 23S | Proposed | P1 | 24 | 3CHAVIN! | VH |  |  |  |  | 1.0512 | 1.0254 | 0.92 | 1.05 | 2147 | 336036 3CHAVIN! 115 336037 3VLNTIN! 115 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | 336036 3CHAVIN! 115 336037 3VLNTIN! 115 1 |  |  | VH
203289 | 23S | Proposed | P1 | 24 | 3GMEADW! | VH |  |  |  |  | 1.0505 | 1.0153 | 0.92 | 1.05 | 2149 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 |  |  | VH
203290 | 23S | Proposed | P1 | 24 | 3LEEVLL | VH |  |  |  |  | 1.0608 | 1.003 | 0.92 | 1.05 | 2149 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 |  |  | VH
203291 | 23S | Proposed | P1 | 24 | 3FOURCHN | VH |  |  |  |  | 1.0579 | 0.9927 | 0.92 | 1.05 | 2149 | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336037 3VLNTIN! 115 336080 3CLOVEL 115 1 |  |  | VH
203292 | 23S | Proposed | P1 | 24 | 3GMEADW! | VH |  |  |  |  | 1.1482 | 1.0153 | 0.92 | 1.05 | 2175 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203293 | 23S | Proposed | P1 | 24 | 3LEEVLL | VH |  |  |  |  | 1.1664 | 1.003 | 0.92 | 1.05 | 2175 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203294 | 23S | Proposed | P1 | 24 | 3FOURCHN | VH |  |  |  |  | 1.1651 | 0.9927 | 0.92 | 1.05 | 2175 | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | 336080 3CLOVEL 115 336081 3GMEADW! 115 1 |  |  | VH
203295 | 23S | Proposed | P1 | 24 | 3CARLSL | VL |  |  |  |  | 0.8663 | 0.9822 | 0.92 | 1.05 | 2185 | 336092 3CARLSL 115 336293 3PTNICK! 115 1 | 336092 |  |  |  | 115 | 115 | 351 | EES |  |  | 336092 3CARLSL 115 336293 3PTNICK! 115 1 |  |  | Contingency: Trip bus as result of con
203296 | 23S | Proposed | P1 | 24 | 3LUCKY | VH |  |  |  |  | 1.0561 | 1.0238 | 0.92 | 1.05 | 2339 | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 | 337349 |  |  |  | 115 | 115 | 351 | EES |  |  | 337347 3HODGE_LA! 115 337349 3LUCKY 115 1 |  |  | VH
203297 | 23S | Proposed | P1 | 24 | 2PINELND | VL |  |  |  |  | 0.9144 | 0.9297 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203298 | 23S | Proposed | P1 | 24 | 2TEMPL1* | VL |  |  |  |  | 0.9124 | 0.9277 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203299 | 23S | Proposed | P1 | 24 | 2TEMPLE1 | VL |  |  |  |  | 0.912 | 0.9273 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203300 | 23S | Proposed | P1 | 24 | 2TEMPL2* | VL |  |  |  |  | 0.9121 | 0.9274 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203301 | 23S | Proposed | P1 | 24 | 2TEMPLE2 | VL |  |  |  |  | 0.9119 | 0.9272 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203302 | 23S | Proposed | P1 | 24 | 2TMPLSWC | VL |  |  |  |  | 0.912 | 0.9273 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203303 | 23S | Proposed | P1 | 24 | 2WEIRGAT | VL |  |  |  |  | 0.8997 | 0.9153 | 0.92 | 1.05 | 2415 | Unit:334282 4RAYBURN% 138 Id:1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | Unit:334282 4RAYBURN% 138 Id:1 |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203304 | 23S | Proposed | P1 | 24 | 3GILBERT | VH |  |  |  |  | 1.0846 | 1.0235 | 0.92 | 1.05 | 2550 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203305 | 23S | Proposed | P2 | 24 | 3METROPOLIS | VH |  |  |  |  | 1.0811 | 1.0306 | 0.92 | 1.05 | 2550 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203306 | 23S | Proposed | P2 | 24 | 3WISNER | VH |  |  |  |  | 1.0842 | 1.031 | 0.92 | 1.05 | 2550 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203307 | 23S | Proposed | P2 | 24 | 3WINNSBORO! | VH |  |  |  |  | 1.0894 | 1.0129 | 0.92 | 1.05 | 2550 | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | 303325 3BASKIN 115 337330 3WINNSBORO! 115 1 |  |  | VH
203308 | 23S | Proposed | P1 | 24 | 4CANEY | VL |  |  |  |  | 0.9128 | 0.9926 | 0.92 | 1.05 | 2649 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
203309 | 23S | Proposed | P1 | 24 | OAKDALE4 | VL |  |  |  |  | 0.9133 | 0.9906 | 0.92 | 1.05 | 2649 | 303137 4CANEY 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 303137 4CANEY 138 500675 PNPRARIE 4 138 1
203310 | 23S | Proposed | P1 | 24 | CLARN 2 | VH |  |  |  |  | 1.1547 | 1.0318 | 0.92 | 1.05 | 2693 | 500165 CLARN 2 69.0 500565 MAURICE2 69.0 1 | 500165 |  |  |  | 69 | 69 | 502 | CLEC |  |  | 500165 CLARN 2 69.0 500565 MAURICE2 69.0 1 |  |  | VH
203311 | 23S | Proposed | P1 | 24 | 4CANEY | VL |  |  |  |  | 0.8633 | 0.9926 | 0.92 | 1.05 | 2709 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203312 | 23S | Proposed | P1 | 24 | CENTNL 4 | VL |  |  |  |  | 0.9119 | 0.9889 | 0.92 | 1.05 | 2709 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203313 | 23S | Proposed | P1 | 24 | OAKDALE4 | VL |  |  |  |  | 0.8653 | 0.9906 | 0.92 | 1.05 | 2709 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203314 | 23S | Proposed | P1 | 24 | PNPRARIE 4 | VL |  |  |  |  | 0.8561 | 1.0056 | 0.92 | 1.05 | 2709 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203315 | 23S | Proposed | P1 | 24 | WSTBAY 4 | VL |  |  |  |  | 0.8772 | 0.9887 | 0.92 | 1.05 | 2709 | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | 500230 COUGH 4 138 500675 PNPRARIE 4 138 1
203322 | 23S | Proposed | P1 | 24 | 8THALMANN | VH |  |  |  |  | 1.056 | 1.0418 | 0.92 | 1.05 | 2921 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 380015 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
203323 | 23S | Proposed | P1 | 24 | 8MCCALL RD | VH |  |  |  |  | 1.0708 | 1.0282 | 0.92 | 1.05 | 2921 | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 | 382158 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380009 8W MCINTOSH 500 382158 8MCCALL RD 500 1 |  |  | VH
203324 | 23S | Proposed | P1 | 24 | 8N TIFTON | VH |  |  |  |  | 1.0514 | 1.0385 | 0.92 | 1.05 | 2953 | 380024 8N TIFTON 500 380222 6N TIFTON 230 1 | 380024 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 380024 8N TIFTON 500 380222 6N TIFTON 230 1 |  |  | VH
203325 | 23S | Proposed | P1 | 24 | 8DANIEL | VH |  |  |  |  | 1.0762 | 1.0426 | 0.92 | 1.05 | 3660 | 388700 8DANIEL 500 388702 6DANIEL 230 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | 388700 8DANIEL 500 388702 6DANIEL 230 1 |  |  | VH
203326 | 23S | Proposed | P1 | 24 | 7SHAWNEE FP | VH |  |  |  |  | 1.051 | 1.0385 | 0.92 | 1.05 | 4001 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | VH
203327 | 23S | Proposed | P1 | 24 | 8RUTHERFORD | VL |  |  |  |  | 0.9096 | 0.9669 | 0.92 | 1.05 | 4003 | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1 | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | 360010 8RUTHERFORD 500 360050 8MAURY TN 500 1
203328 | 23S | Proposed | P1 | 24 | TENRUSK7 | VH |  |  |  |  | 1.0503 | 1.0147 | 0.92 | 1.05 | 4711 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
203329 | 23S | Proposed | P1 | 24 | TENGEN 7 | VH |  |  |  |  | 1.0503 | 1.0147 | 0.92 | 1.05 | 4711 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 |  |  | VH
203330 | 23S | Proposed | P1 | 24 | ELKCITY7 | VH |  |  |  |  | 1.0513 | 1.0246 | 0.92 | 1.05 | 4752 | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 | 511553 |  |  |  | 345 | 345 | 520 | AEPW |  |  | 511490 ELKCITY6 230 511553 ELKCITY7 345 1 |  |  | VH
203331 | 23S | Proposed | P0 | 25 | 2WEIRGAT | VL |  |  |  |  | 0.9153 | 0.9153 | 0.92 | 1.05 | 0 | ** Base Case ** | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203332 | 23S | Proposed | P0 | 25 | 5HORN LAKE% | VH |  |  |  |  | 1.0567 | 1.0567 | 0.92 | 1.05 | 0 | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
203333 | 23S | Proposed | P0 | 25 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 | 0 | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203334 | 23S | Proposed | P0 | 25 | 8CENTRLAL | VH |  |  |  |  | 1.05 | 1.05 | 0.92 | 1.05 | 0 | ** Base Case ** | 385337 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203335 | 18S | Approved | P0 | 31 | 5HORN LAKE% | VH |  |  |  |  | 1.057 | 1.057 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
203336 | 18S | Approved | P0 | 31 | 8E POINT AL | VH |  |  |  |  | 1.0537 | 1.0537 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203337 | 18S | Approved | P0 | 31 | 8WID CRK FP | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
203338 | 18S | Approved | P0 | 31 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 |  | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
203339 | 18S | Approved | P3 | 31 | 4LEBLANC! | VL |  |  |  |  | 0.9127 | 0.9679 | 0.92 | 1.05 | 75 | P1_2-113_4LEBLANC!,4MORIL!+G_1WAT U3! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
203340 | 18S | Approved | P3 | 31 | 4LEBLANC! | VL |  |  |  |  | 0.9062 | 0.9679 | 0.92 | 1.05 | 183 | P1_2-113_4LEBLANC!,4MORIL!+G_G3TECHE! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
203341 | 18S | Approved | P3 | 31 | 4LEBLANC! | VL |  |  |  |  | 0.9125 | 0.9679 | 0.92 | 1.05 | 185 | P1_2-113_4LEBLANC!,4MORIL!+G_G1 ACAD! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G1 ACAD! ID 1 | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
203342 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9172 | 0.9721 | 0.92 | 1.05 | 255 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203342 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9172 | 0.9721 | 0.92 | 1.05 | 255 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203343 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9088 | 0.9714 | 0.92 | 1.05 | 255 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203343 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9088 | 0.9714 | 0.92 | 1.05 | 255 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203344 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9173 | 0.9721 | 0.92 | 1.05 | 256 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203344 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9173 | 0.9721 | 0.92 | 1.05 | 256 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203345 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9089 | 0.9714 | 0.92 | 1.05 | 256 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203345 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9089 | 0.9714 | 0.92 | 1.05 | 256 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203346 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9121 | 0.9721 | 0.92 | 1.05 | 264 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203346 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9121 | 0.9721 | 0.92 | 1.05 | 264 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203347 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9036 | 0.9714 | 0.92 | 1.05 | 264 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203347 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9036 | 0.9714 | 0.92 | 1.05 | 264 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203348 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9151 | 0.9721 | 0.92 | 1.05 | 268 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203348 | 18S | Approved | P3 | 31 | 4HICKORY | VL |  |  |  |  | 0.9151 | 0.9721 | 0.92 | 1.05 | 268 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203349 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9067 | 0.9714 | 0.92 | 1.05 | 268 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
203349 | 18S | Approved | P3 | 31 | 4NEWCANY! | VL |  |  |  |  | 0.9067 | 0.9714 | 0.92 | 1.05 | 268 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
203350 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9114 | 0.9937 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203351 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9023 | 0.9951 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203352 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.895 | 0.9785 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203353 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8907 | 0.9749 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203354 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.889 | 0.9734 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203355 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8975 | 0.9858 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203356 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9101 | 0.9871 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203357 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9083 | 0.9855 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203358 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203359 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.908 | 0.9853 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203360 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9078 | 0.9851 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203361 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203362 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8971 | 0.9758 | 0.92 | 1.05 | 723 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203363 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9114 | 0.9937 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203364 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9023 | 0.9951 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203365 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.895 | 0.9785 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203366 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8907 | 0.9749 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203367 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.889 | 0.9734 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203368 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8975 | 0.9858 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203369 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9101 | 0.9871 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203370 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9083 | 0.9855 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203371 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203372 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.908 | 0.9853 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203373 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9078 | 0.9851 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203374 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203375 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8971 | 0.9758 | 0.92 | 1.05 | 724 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203376 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9014 | 0.9951 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203377 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8944 | 0.9785 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203378 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8901 | 0.9749 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203379 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8885 | 0.9734 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203380 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8967 | 0.9858 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203381 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9096 | 0.9871 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203382 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9078 | 0.9855 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203383 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9074 | 0.9852 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203384 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9075 | 0.9853 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203385 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9073 | 0.9851 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203386 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9074 | 0.9852 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203387 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9758 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203388 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9104 | 0.9937 | 0.92 | 1.05 | 725 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203389 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9014 | 0.9951 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203390 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8944 | 0.9785 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203391 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8902 | 0.9749 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203392 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8885 | 0.9734 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203393 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8968 | 0.9858 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203394 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9096 | 0.9871 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203395 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9078 | 0.9855 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203396 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9075 | 0.9852 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203397 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9076 | 0.9853 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203398 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9074 | 0.9851 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203399 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9075 | 0.9852 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203400 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9758 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203401 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9105 | 0.9937 | 0.92 | 1.05 | 726 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203402 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.903 | 0.9951 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203403 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8957 | 0.9785 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203404 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8914 | 0.9749 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203405 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8897 | 0.9734 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203406 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8982 | 0.9858 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203407 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9087 | 0.9852 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203408 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9088 | 0.9853 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203409 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9086 | 0.9851 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203410 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9087 | 0.9852 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203411 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.912 | 0.9937 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203412 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9108 | 0.9871 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203413 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.909 | 0.9855 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203414 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8979 | 0.9758 | 0.92 | 1.05 | 728 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203415 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.903 | 0.9951 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203416 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8957 | 0.9785 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203417 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8914 | 0.9749 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203418 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8897 | 0.9734 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203419 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8982 | 0.9858 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203420 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9087 | 0.9852 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203421 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9088 | 0.9853 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203422 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9086 | 0.9851 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203423 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9087 | 0.9852 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203424 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.912 | 0.9937 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203425 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9108 | 0.9871 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203426 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.909 | 0.9855 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203427 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8979 | 0.9758 | 0.92 | 1.05 | 729 | P1_2-237_4RAYBURN%,4MILLCR!+G_1PELCNRD U2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1PELCNRD U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203428 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9114 | 0.9937 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203429 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9023 | 0.9951 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203430 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.895 | 0.9785 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203431 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8907 | 0.9749 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203432 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.889 | 0.9734 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203433 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8975 | 0.9858 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203434 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9101 | 0.9871 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203435 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9082 | 0.9855 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203436 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203437 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.908 | 0.9853 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203438 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9078 | 0.9851 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203439 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9852 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203440 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8971 | 0.9758 | 0.92 | 1.05 | 730 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203441 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.8913 | 0.9951 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203442 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8834 | 0.9785 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203443 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.879 | 0.9749 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203444 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8773 | 0.9734 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203445 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8862 | 0.9858 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203446 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.8981 | 0.9871 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203447 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.8962 | 0.9855 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203448 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.8959 | 0.9852 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203449 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.896 | 0.9853 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203450 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.8958 | 0.9851 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203451 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.8959 | 0.9852 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203452 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8849 | 0.9758 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203453 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9007 | 0.9937 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203454 | 18S | Approved | P3 | 31 | 4UNONGSU! | VL |  |  |  |  | 0.9142 | 0.9928 | 0.92 | 1.05 | 734 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203455 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.8984 | 0.9951 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203456 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8913 | 0.9785 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203457 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.887 | 0.9749 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203458 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8854 | 0.9734 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203459 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8937 | 0.9858 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203460 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9064 | 0.9871 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203461 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9046 | 0.9855 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203462 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9043 | 0.9852 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203463 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9043 | 0.9853 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203464 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9042 | 0.9851 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203465 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9043 | 0.9852 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203466 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8937 | 0.9758 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203467 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9075 | 0.9937 | 0.92 | 1.05 | 738 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203468 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9021 | 0.9951 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203469 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8949 | 0.9785 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203470 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8906 | 0.9749 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203471 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8889 | 0.9734 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203472 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8974 | 0.9858 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203473 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9099 | 0.9871 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203474 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9081 | 0.9855 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203475 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9078 | 0.9852 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203476 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9079 | 0.9853 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203477 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9077 | 0.9851 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203478 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9078 | 0.9852 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203479 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.897 | 0.9758 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203480 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9112 | 0.9937 | 0.92 | 1.05 | 739 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203481 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9027 | 0.9951 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203482 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8979 | 0.9858 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203483 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9118 | 0.9937 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203484 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8955 | 0.9785 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203485 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8912 | 0.9749 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203486 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8895 | 0.9734 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203487 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9105 | 0.9871 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203488 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9087 | 0.9855 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203489 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.9084 | 0.9852 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203490 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9085 | 0.9853 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203491 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9083 | 0.9851 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203492 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.9084 | 0.9852 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203493 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8976 | 0.9758 | 0.92 | 1.05 | 885 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203494 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9033 | 0.9951 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203495 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.8961 | 0.9785 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203496 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8918 | 0.9749 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203497 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.8901 | 0.9734 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203498 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8985 | 0.9858 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203499 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9112 | 0.9871 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203500 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9093 | 0.9855 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203501 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203502 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9091 | 0.9853 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203503 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9089 | 0.9851 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203504 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203505 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9123 | 0.9937 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203506 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8982 | 0.9758 | 0.92 | 1.05 | 906 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203507 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9032 | 0.9951 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203508 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.896 | 0.9785 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203509 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8917 | 0.9749 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203510 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.89 | 0.9734 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203511 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8985 | 0.9858 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203512 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9111 | 0.9871 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203513 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9093 | 0.9855 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203514 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203515 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.9091 | 0.9853 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203516 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9089 | 0.9851 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203517 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203518 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9123 | 0.9937 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203519 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8982 | 0.9758 | 0.92 | 1.05 | 936 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203520 | 18S | Approved | P3 | 31 | 4MILLCR! | VL |  |  |  |  | 0.9032 | 0.9951 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203521 | 18S | Approved | P3 | 31 | 4PINELND | VL |  |  |  |  | 0.896 | 0.9785 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203522 | 18S | Approved | P3 | 31 | 4BROADUS | VL |  |  |  |  | 0.8917 | 0.9749 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203523 | 18S | Approved | P3 | 31 | 4ETOIL | VL |  |  |  |  | 0.89 | 0.9734 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203524 | 18S | Approved | P3 | 31 | 4HRTNHIL | VL |  |  |  |  | 0.8985 | 0.9858 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203525 | 18S | Approved | P3 | 31 | 2PINELND | VL |  |  |  |  | 0.9111 | 0.9871 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203526 | 18S | Approved | P3 | 31 | 2TEMPL1* | VL |  |  |  |  | 0.9093 | 0.9855 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203527 | 18S | Approved | P3 | 31 | 2TEMPLE1 | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203528 | 18S | Approved | P3 | 31 | 2TEMPL2* | VL |  |  |  |  | 0.909 | 0.9853 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203529 | 18S | Approved | P3 | 31 | 2TEMPLE2 | VL |  |  |  |  | 0.9089 | 0.9851 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203530 | 18S | Approved | P3 | 31 | 2TMPLSWC | VL |  |  |  |  | 0.909 | 0.9852 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203531 | 18S | Approved | P3 | 31 | 4PEACH! | VL |  |  |  |  | 0.9123 | 0.9937 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203532 | 18S | Approved | P3 | 31 | 2WEIRGAT | VL |  |  |  |  | 0.8982 | 0.9758 | 0.92 | 1.05 | 941 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
203533 | 18S | Approved | P3 | 31 | 3ASHLAND | VL |  |  |  |  | 0.8975 | 1.0017 | 0.92 | 1.05 | 1906 | P1_2-802_3COTEAU!,3HOUMA!+G_1G4SABIN! ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1G4SABIN! ID 1 |  | Solution: Adjust caps
203534 | 18S | Approved | P3 | 31 | 3HOUMA! | VL |  |  |  |  | 0.8928 | 1.0062 | 0.92 | 1.05 | 1906 | P1_2-802_3COTEAU!,3HOUMA!+G_1G4SABIN! ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1G4SABIN! ID 1 |  | Solution: Adjust caps
203535 | 18S | Approved | P3 | 31 | HOUMA 3 | VL |  |  |  |  | 0.8928 | 1.0062 | 0.92 | 1.05 | 1906 | P1_2-802_3COTEAU!,3HOUMA!+G_1G4SABIN! ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1G4SABIN! ID 1 |  | Solution: Adjust caps
203536 | 18S | Approved | P3 | 31 | 3ASHLAND | VL |  |  |  |  | 0.8974 | 1.0017 | 0.92 | 1.05 | 1941 | P1_2-802_3COTEAU!,3HOUMA!+G_1WILL_GL_G4! ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1WILL_GL_G4! ID 1 |  | Solution: Adjust caps
203537 | 18S | Approved | P3 | 31 | 3HOUMA! | VL |  |  |  |  | 0.8927 | 1.0062 | 0.92 | 1.05 | 1941 | P1_2-802_3COTEAU!,3HOUMA!+G_1WILL_GL_G4! ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1WILL_GL_G4! ID 1 |  | Solution: Adjust caps
203538 | 18S | Approved | P3 | 31 | HOUMA 3 | VL |  |  |  |  | 0.8927 | 1.0062 | 0.92 | 1.05 | 1941 | P1_2-802_3COTEAU!,3HOUMA!+G_1WILL_GL_G4! ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1WILL_GL_G4! ID 1 |  | Solution: Adjust caps
203539 | 18S | Approved | P3 | 31 | 3ASHLAND | VL |  |  |  |  | 0.8976 | 1.0017 | 0.92 | 1.05 | 1970 | P1_2-802_3COTEAU!,3HOUMA!+G_1GGNS U1 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | Solution: Adjust caps
203540 | 18S | Approved | P3 | 31 | 3HOUMA! | VL |  |  |  |  | 0.893 | 1.0062 | 0.92 | 1.05 | 1970 | P1_2-802_3COTEAU!,3HOUMA!+G_1GGNS U1 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | Solution: Adjust caps
203541 | 18S | Approved | P3 | 31 | HOUMA 3 | VL |  |  |  |  | 0.893 | 1.0062 | 0.92 | 1.05 | 1970 | P1_2-802_3COTEAU!,3HOUMA!+G_1GGNS U1 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | Solution: Adjust caps
203542 | 18S | Approved | P3 | 31 | 3GMEADW! | VH |  |  |  |  | 1.1572 | 1.0067 | 0.92 | 1.05 | 2120 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NRG_G1! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NRG_G1! ID 1 |  | VH
203543 | 18S | Approved | P3 | 31 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 0.9959 | 0.92 | 1.05 | 2120 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NRG_G1! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NRG_G1! ID 1 |  | VH
203544 | 18S | Approved | P3 | 31 | 3FOURCHN | VH |  |  |  |  | 1.1773 | 0.9861 | 0.92 | 1.05 | 2120 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NRG_G1! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NRG_G1! ID 1 |  | VH
203545 | 18S | Approved | P3 | 31 | 3GMEADW! | VH |  |  |  |  | 1.1572 | 1.0067 | 0.92 | 1.05 | 2169 | P1_2-807_3VLNTIN!,3GMEADW!+G_1CARVLE_C1! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1CARVLE_C1! ID 1 |  | VH
203546 | 18S | Approved | P3 | 31 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 0.9959 | 0.92 | 1.05 | 2169 | P1_2-807_3VLNTIN!,3GMEADW!+G_1CARVLE_C1! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1CARVLE_C1! ID 1 |  | VH
203547 | 18S | Approved | P3 | 31 | 3FOURCHN | VH |  |  |  |  | 1.1773 | 0.9861 | 0.92 | 1.05 | 2169 | P1_2-807_3VLNTIN!,3GMEADW!+G_1CARVLE_C1! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1CARVLE_C1! ID 1 |  | VH
203548 | 18S | Approved | P3 | 31 | 3GMEADW! | VL |  |  |  |  | 0.918 | 1.0067 | 0.92 | 1.05 | 2198 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL6 ST1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL6 ST1 ID 1 | None | Delta: No worse than P1
203549 | 18S | Approved | P3 | 31 | 3LEEVLL | VL |  |  |  |  | 0.883 | 0.9959 | 0.92 | 1.05 | 2198 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL6 ST1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL6 ST1 ID 1 | None | Delta: No worse than P1
203550 | 18S | Approved | P3 | 31 | 3FOURCHN | VL |  |  |  |  | 0.8719 | 0.9861 | 0.92 | 1.05 | 2198 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL6 ST1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL6 ST1 ID 1 | None | Delta: No worse than P1
203551 | 18S | Approved | P3 | 31 | 3GMEADW! | VL |  |  |  |  | 0.9177 | 1.0067 | 0.92 | 1.05 | 2199 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U4! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U4! ID 1 | None | Delta: No worse than P1
203552 | 18S | Approved | P3 | 31 | 3LEEVLL | VL |  |  |  |  | 0.8827 | 0.9959 | 0.92 | 1.05 | 2199 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U4! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U4! ID 1 | None | Delta: No worse than P1
203553 | 18S | Approved | P3 | 31 | 3FOURCHN | VL |  |  |  |  | 0.8716 | 0.9861 | 0.92 | 1.05 | 2199 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U4! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U4! ID 1 | None | Delta: No worse than P1
203554 | 18S | Approved | P3 | 31 | 3GMEADW! | VL |  |  |  |  | 0.9177 | 1.0067 | 0.92 | 1.05 | 2200 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U5! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U5! ID 1 | None | Delta: No worse than P1
203555 | 18S | Approved | P3 | 31 | 3LEEVLL | VL |  |  |  |  | 0.8827 | 0.9959 | 0.92 | 1.05 | 2200 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U5! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U5! ID 1 | None | Delta: No worse than P1
203556 | 18S | Approved | P3 | 31 | 3FOURCHN | VL |  |  |  |  | 0.8716 | 0.9861 | 0.92 | 1.05 | 2200 | P1_2-807_3VLNTIN!,3GMEADW!+G_1NMIL U5! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1NMIL U5! ID 1 | None | Delta: No worse than P1
203557 | 18S | Approved | P3 | 31 | 3GMEADW! | VL |  |  |  |  | 0.9177 | 1.0067 | 0.92 | 1.05 | 2202 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U2! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U2! ID 1 | None | Delta: No worse than P1
203558 | 18S | Approved | P3 | 31 | 3LEEVLL | VL |  |  |  |  | 0.8828 | 0.9959 | 0.92 | 1.05 | 2202 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U2! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U2! ID 1 | None | Delta: No worse than P1
203559 | 18S | Approved | P3 | 31 | 3FOURCHN | VL |  |  |  |  | 0.8717 | 0.9861 | 0.92 | 1.05 | 2202 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U2! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U2! ID 1 | None | Delta: No worse than P1
203560 | 18S | Approved | P3 | 31 | 3GMEADW! | VL |  |  |  |  | 0.9158 | 1.0067 | 0.92 | 1.05 | 2203 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U3! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U3! ID 1 | None | Delta: No worse than P1
203561 | 18S | Approved | P3 | 31 | 3LEEVLL | VL |  |  |  |  | 0.8808 | 0.9959 | 0.92 | 1.05 | 2203 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U3! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U3! ID 1 | None | Delta: No worse than P1
203562 | 18S | Approved | P3 | 31 | 3FOURCHN | VL |  |  |  |  | 0.8696 | 0.9861 | 0.92 | 1.05 | 2203 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MICH U3! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MICH U3! ID 1 | None | Delta: No worse than P1
203563 | 18S | Approved | P3 | 31 | 3GMEADW! | VH |  |  |  |  | 1.1572 | 1.0067 | 0.92 | 1.05 | 2262 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MCCLELAN U1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MCCLELAN U1 ID 1 |  | VH
203564 | 18S | Approved | P3 | 31 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 0.9959 | 0.92 | 1.05 | 2262 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MCCLELAN U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MCCLELAN U1 ID 1 |  | VH
203565 | 18S | Approved | P3 | 31 | 3FOURCHN | VH |  |  |  |  | 1.1773 | 0.9861 | 0.92 | 1.05 | 2262 | P1_2-807_3VLNTIN!,3GMEADW!+G_1MCCLELAN U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1MCCLELAN U1 ID 1 |  | VH
203566 | 18S | Approved | P3 | 31 | 3GMEADW! | VH |  |  |  |  | 1.1572 | 1.0067 | 0.92 | 1.05 | 2278 | P1_2-807_3VLNTIN!,3GMEADW!+G_1BAILEY U1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1BAILEY U1 ID 1 |  | VH
203567 | 18S | Approved | P3 | 31 | 3LEEVLL | VH |  |  |  |  | 1.1779 | 0.9959 | 0.92 | 1.05 | 2278 | P1_2-807_3VLNTIN!,3GMEADW!+G_1BAILEY U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1BAILEY U1 ID 1 |  | VH
203568 | 18S | Approved | P3 | 31 | 3FOURCHN | VH |  |  |  |  | 1.1773 | 0.9861 | 0.92 | 1.05 | 2278 | P1_2-807_3VLNTIN!,3GMEADW!+G_1BAILEY U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-807_3VLNTIN!,3GMEADW! | G_1BAILEY U1 ID 1 |  | VH
203569 | 18S | Approved | P3 | 31 | 3GILBERT | VL |  |  |  |  | 0.8892 | 1.0225 | 0.92 | 1.05 | 3277 | P1_2-1178_3WINNSBORO!,3SWARTZ!+G_1NM G1 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! | G_1NM G1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
203570 | 18S | Approved | P3 | 31 | 3METROPOLIS | VL |  |  |  |  | 0.9038 | 1.0293 | 0.92 | 1.05 | 3277 | P1_2-1178_3WINNSBORO!,3SWARTZ!+G_1NM G1 ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! | G_1NM G1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
203571 | 18S | Approved | P3 | 31 | 3WISNER | VL |  |  |  |  | 0.9 | 1.0298 | 0.92 | 1.05 | 3277 | P1_2-1178_3WINNSBORO!,3SWARTZ!+G_1NM G1 ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! | G_1NM G1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
203572 | 18S | Approved | P3 | 31 | 3WINNSBORO! | VL |  |  |  |  | 0.8729 | 1.0121 | 0.92 | 1.05 | 3277 | P1_2-1178_3WINNSBORO!,3SWARTZ!+G_1NM G1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1178_3WINNSBORO!,3SWARTZ! | G_1NM G1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
203573 | 18S | Approved | P3 | 31 | 3ULM | VL |  |  |  |  | 0.9159 | 0.9875 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203574 | 18S | Approved | P3 | 31 | 3STUTGART.N+ | VL |  |  |  |  | 0.9088 | 0.9884 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203575 | 18S | Approved | P3 | 31 | 3STUTGART.N | VL |  |  |  |  | 0.9067 | 0.9865 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203576 | 18S | Approved | P3 | 31 | 3RICUSKEY! | VL |  |  |  |  | 0.909 | 0.9934 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203577 | 18S | Approved | P3 | 31 | 3STUTGART IN | VL |  |  |  |  | 0.9084 | 0.9883 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203578 | 18S | Approved | P3 | 31 | 3ALMYRA | VL |  |  |  |  | 0.9068 | 0.977 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203579 | 18S | Approved | P3 | 31 | 3DEWITT | VL |  |  |  |  | 0.9085 | 0.9678 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203580 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9193 | 0.9663 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203581 | 18S | Approved | P3 | 31 | 3HUMPHREY# | VL |  |  |  |  | 0.9136 | 0.9791 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203582 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9138 | 0.9648 | 0.92 | 1.05 | 4732 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203583 | 18S | Approved | P3 | 31 | 3STUTGART.N+ | VL |  |  |  |  | 0.9077 | 0.9884 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203584 | 18S | Approved | P3 | 31 | 3STUTGART.N | VL |  |  |  |  | 0.9056 | 0.9865 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203585 | 18S | Approved | P3 | 31 | 3RICUSKEY! | VL |  |  |  |  | 0.9079 | 0.9934 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203586 | 18S | Approved | P3 | 31 | 3STUTGART IN | VL |  |  |  |  | 0.9072 | 0.9883 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203587 | 18S | Approved | P3 | 31 | 3ULM | VL |  |  |  |  | 0.9145 | 0.9875 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203588 | 18S | Approved | P3 | 31 | 3ALMYRA | VL |  |  |  |  | 0.9057 | 0.977 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203589 | 18S | Approved | P3 | 31 | 3DEWITT | VL |  |  |  |  | 0.9075 | 0.9678 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203590 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9183 | 0.9663 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203591 | 18S | Approved | P3 | 31 | 3HUMPHREY# | VL |  |  |  |  | 0.9128 | 0.9791 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203592 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9127 | 0.9648 | 0.92 | 1.05 | 4787 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203593 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.912 | 0.9663 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203594 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8842 | 0.9668 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203595 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8758 | 0.9689 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203596 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8729 | 0.9695 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203597 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8683 | 0.9707 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203598 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8665 | 0.9711 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203599 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9169 | 0.9648 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203600 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8662 | 0.9734 | 0.92 | 1.05 | 4855 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NM G1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NM G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203601 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203602 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203603 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203604 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203605 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203606 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203607 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203608 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4866 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G3INTHB ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G3INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203609 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203610 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203611 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203612 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203613 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203614 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203615 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203616 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4868 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G4INTHB ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G4INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203617 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203618 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203619 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203620 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203621 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203622 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203623 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203624 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4870 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1INTHB ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1INTHB ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203625 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203626 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203627 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203628 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203629 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203630 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203631 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203632 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4882 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1EXXONGT1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203633 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9124 | 0.9663 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203634 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203635 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203636 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203637 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203638 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203639 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203640 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4883 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G1SABIN! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G1SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203641 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9124 | 0.9663 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203642 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203643 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203644 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203645 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203646 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203647 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203648 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4884 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1G2SABIN! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1G2SABIN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203649 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203650 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203651 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203652 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203653 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203654 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203655 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203656 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4898 | P1_2-1448_3RITCHIE!,3HELENA IN#!+44 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1RS_CGN_R5! ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203657 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203658 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203659 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203660 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203661 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203662 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203663 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203664 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4900 | P1_2-1448_3RITCHIE!,3HELENA IN#!+46 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203665 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203666 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203667 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203668 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203669 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203670 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203671 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203672 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4901 | P1_2-1448_3RITCHIE!,3HELENA IN#!+47 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203673 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203674 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203675 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203676 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203677 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203678 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203679 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203680 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4902 | P1_2-1448_3RITCHIE!,3HELENA IN#!+48 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203681 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9126 | 0.9663 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203682 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8849 | 0.9668 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203683 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8765 | 0.9689 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203684 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8736 | 0.9695 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203685 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.869 | 0.9707 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203686 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8672 | 0.9711 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203687 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9175 | 0.9648 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203688 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8669 | 0.9734 | 0.92 | 1.05 | 4903 | P1_2-1448_3RITCHIE!,3HELENA IN#!+49 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NELSON_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203689 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203690 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203691 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203692 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203693 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203694 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203695 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203696 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4905 | P1_2-1448_3RITCHIE!,3HELENA IN#!+51 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_S26! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203697 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203698 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203699 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203700 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203701 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203702 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203703 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203704 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4906 | P1_2-1448_3RITCHIE!,3HELENA IN#!+52 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C25! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203705 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203706 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203707 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203708 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203709 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203710 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203711 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203712 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4907 | P1_2-1448_3RITCHIE!,3HELENA IN#!+53 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ACADIA_C24! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203713 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203714 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203715 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203716 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203717 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203718 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203719 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203720 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4914 | P1_2-1448_3RITCHIE!,3HELENA IN#!+60 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203721 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203722 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203723 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203724 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203725 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203726 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203727 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203728 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4915 | P1_2-1448_3RITCHIE!,3HELENA IN#!+61 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203729 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203730 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203731 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203732 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203733 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203734 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203735 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203736 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4916 | P1_2-1448_3RITCHIE!,3HELENA IN#!+62 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CARVLE_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203737 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203738 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203739 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203740 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203741 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203742 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203743 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203744 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4920 | P1_2-1448_3RITCHIE!,3HELENA IN#!+66 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203745 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203746 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203747 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203748 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203749 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203750 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203751 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203752 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4921 | P1_2-1448_3RITCHIE!,3HELENA IN#!+67 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WILL_GL_G4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203753 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203754 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203755 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203756 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203757 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203758 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203759 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203760 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4923 | P1_2-1448_3RITCHIE!,3HELENA IN#!+69 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U5A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203761 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203762 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203763 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203764 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203765 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203766 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203767 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203768 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4924 | P1_2-1448_3RITCHIE!,3HELENA IN#!+70 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LA_STA_U4A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203769 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203770 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203771 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203772 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203773 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203774 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203775 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203776 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4927 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203777 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203778 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203779 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203780 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203781 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203782 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203783 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203784 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4928 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1WAT U2! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WAT U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203785 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203786 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203787 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203788 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203789 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203790 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203791 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203792 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4930 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203793 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203794 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203795 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203796 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203797 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203798 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203799 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203800 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4931 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U2! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203801 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203802 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203803 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203804 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203805 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203806 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203807 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203808 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4932 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GOXY U3! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GOXY U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203809 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203810 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203811 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203812 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203813 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203814 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203815 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203816 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4933 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SOXY U1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SOXY U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203817 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203818 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203819 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203820 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203821 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203822 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203823 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203824 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4934 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203825 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203826 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203827 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203828 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203829 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203830 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203831 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203832 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4935 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1UCARBGT2! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1UCARBGT2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203833 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203834 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203835 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203836 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203837 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203838 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203839 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203840 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4939 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U1! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203841 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9124 | 0.9663 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203842 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203843 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203844 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203845 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203846 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203847 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203848 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4940 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1GYP U2! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1GYP U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203849 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203850 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203851 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203852 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203853 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203854 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203855 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203856 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4941 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203857 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203858 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203859 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203860 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203861 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203862 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203863 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203864 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 4942 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 CT2 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 CT2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203865 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203866 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203867 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203868 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203869 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203870 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203871 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203872 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4943 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL6 ST1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL6 ST1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203873 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9125 | 0.9663 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203874 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8848 | 0.9668 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203875 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8764 | 0.9689 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203876 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8735 | 0.9695 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203877 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8689 | 0.9707 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203878 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8671 | 0.9711 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203879 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9174 | 0.9648 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203880 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8668 | 0.9734 | 0.92 | 1.05 | 4944 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U4! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U4! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203881 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9125 | 0.9663 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203882 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8848 | 0.9668 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203883 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8764 | 0.9689 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203884 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8735 | 0.9695 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203885 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8689 | 0.9707 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203886 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8671 | 0.9711 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203887 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9174 | 0.9648 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203888 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8668 | 0.9734 | 0.92 | 1.05 | 4945 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1NMIL U5! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1NMIL U5! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203889 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203890 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203891 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203892 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203893 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203894 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203895 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203896 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4947 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U2! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203897 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9124 | 0.9663 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203898 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8847 | 0.9668 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203899 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8763 | 0.9689 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203900 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8734 | 0.9695 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203901 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8688 | 0.9707 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203902 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.867 | 0.9711 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203903 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9173 | 0.9648 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203904 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8667 | 0.9734 | 0.92 | 1.05 | 4948 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1MICH U3! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1MICH U3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203905 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203906 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203907 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203908 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203909 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203910 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203911 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203912 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4949 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203913 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9124 | 0.9663 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203914 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203915 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203916 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203917 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203918 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203919 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203920 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4951 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1B.WLSN U2 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203921 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203922 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203923 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203924 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203925 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203926 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203927 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203928 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4952 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G2 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203929 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203930 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203931 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203932 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203933 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203934 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203935 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203936 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4953 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS G1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203937 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203938 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203939 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203940 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203941 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203942 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203943 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203944 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4954 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1HINDS S1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1HINDS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203945 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203946 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203947 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203948 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203949 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203950 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203951 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203952 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4955 | P1_2-1448_3RITCHIE!,3HELENA IN#!+101 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1REX BRWN U4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203953 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203954 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203955 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203956 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203957 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203958 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203959 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9169 | 0.9648 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203960 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4957 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203961 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203962 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203963 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203964 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203965 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203966 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203967 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9169 | 0.9648 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203968 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4958 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA G2 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203969 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203970 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203971 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203972 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203973 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203974 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203975 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9169 | 0.9648 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203976 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4959 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ATTALA S1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ATTALA S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203977 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203978 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.884 | 0.9668 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203979 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8756 | 0.9689 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203980 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8727 | 0.9695 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203981 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203982 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203983 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203984 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 4961 | P1_2-1448_3RITCHIE!,3HELENA IN#!+107 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_3GREENWOOD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203985 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9113 | 0.9663 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203986 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8834 | 0.9668 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203987 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.875 | 0.9689 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203988 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8721 | 0.9695 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203989 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8675 | 0.9707 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203990 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8657 | 0.9711 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203991 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9161 | 0.9648 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203992 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8654 | 0.9734 | 0.92 | 1.05 | 4967 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203993 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9105 | 0.9663 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203994 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8825 | 0.9668 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203995 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8741 | 0.9689 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203996 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8712 | 0.9695 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203997 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8666 | 0.9707 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203998 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8648 | 0.9711 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
203999 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9154 | 0.9648 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204000 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8645 | 0.9734 | 0.92 | 1.05 | 4968 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204001 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204002 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204003 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204004 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204005 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204006 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204007 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204008 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4974 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7A! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7A! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204009 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204010 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204011 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204012 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204013 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204014 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204015 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204016 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 4975 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1STERL_7B! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1STERL_7B! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204017 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204018 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204019 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204020 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204021 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204022 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204023 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204024 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4977 | P1_2-1448_3RITCHIE!,3HELENA IN#!+123 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204025 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204026 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204027 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204028 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204029 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204030 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204031 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204032 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4978 | P1_2-1448_3RITCHIE!,3HELENA IN#!+124 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204033 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204034 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204035 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204036 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204037 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204038 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204039 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204040 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4979 | P1_2-1448_3RITCHIE!,3HELENA IN#!+125 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204041 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204042 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204043 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204044 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204045 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204046 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204047 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204048 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4980 | P1_2-1448_3RITCHIE!,3HELENA IN#!+126 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204049 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204050 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204051 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204052 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204053 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204054 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204055 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204056 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4981 | P1_2-1448_3RITCHIE!,3HELENA IN#!+127 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_G3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204057 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204058 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204059 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204060 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204061 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204062 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204063 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204064 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4982 | P1_2-1448_3RITCHIE!,3HELENA IN#!+128 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1OUACHI_S3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204065 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204066 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204067 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204068 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204069 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204070 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204071 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204072 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4983 | P1_2-1448_3RITCHIE!,3HELENA IN#!+129 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204073 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204074 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204075 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204076 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204077 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204078 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204079 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204080 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 4984 | P1_2-1448_3RITCHIE!,3HELENA IN#!+130 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C2! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204081 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204082 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204083 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204084 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204085 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204086 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204087 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204088 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4985 | P1_2-1448_3RITCHIE!,3HELENA IN#!+131 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_C3! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204089 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204090 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204091 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204092 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204093 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204094 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204095 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204096 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 4986 | P1_2-1448_3RITCHIE!,3HELENA IN#!+132 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PERRYV_S1! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204097 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.913 | 0.9663 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204098 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8853 | 0.9668 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204099 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8769 | 0.9689 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204100 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.874 | 0.9695 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204101 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8694 | 0.9707 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204102 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8676 | 0.9711 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204103 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9178 | 0.9648 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204104 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8673 | 0.9734 | 0.92 | 1.05 | 4997 | P1_2-1448_3RITCHIE!,3HELENA IN#!+143 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204105 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9126 | 0.9663 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204106 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8849 | 0.9668 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204107 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8765 | 0.9689 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204108 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8736 | 0.9695 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204109 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.869 | 0.9707 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204110 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8672 | 0.9711 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204111 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9175 | 0.9648 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204112 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8669 | 0.9734 | 0.92 | 1.05 | 4998 | P1_2-1448_3RITCHIE!,3HELENA IN#!+144 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204113 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9126 | 0.9663 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204114 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8849 | 0.9668 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204115 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8765 | 0.9689 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204116 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8736 | 0.9695 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204117 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.869 | 0.9707 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204118 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8672 | 0.9711 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204119 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9175 | 0.9648 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204120 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8669 | 0.9734 | 0.92 | 1.05 | 4999 | P1_2-1448_3RITCHIE!,3HELENA IN#!+145 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1DUKE HS C2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204121 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204122 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204123 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8758 | 0.9689 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204124 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204125 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204126 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204127 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9169 | 0.9648 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204128 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5006 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1M.HYD U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1M.HYD U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204129 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204130 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204131 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204132 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204133 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204134 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204135 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204136 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 5020 | P1_2-1448_3RITCHIE!,3HELENA IN#!+166 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204137 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204138 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204139 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204140 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204141 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204142 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204143 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204144 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5021 | P1_2-1448_3RITCHIE!,3HELENA IN#!+167 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS C7 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204145 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204146 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204147 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204148 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204149 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204150 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204151 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204152 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 5022 | P1_2-1448_3RITCHIE!,3HELENA IN#!+168 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1WRIGHTS S2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204153 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9107 | 0.9663 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204154 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8828 | 0.9668 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204155 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8744 | 0.9689 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204156 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8715 | 0.9695 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204157 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8669 | 0.9707 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204158 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8651 | 0.9711 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204159 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9156 | 0.9648 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204160 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8648 | 0.9734 | 0.92 | 1.05 | 5023 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204161 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204162 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.884 | 0.9668 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204163 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8755 | 0.9689 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204164 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8727 | 0.9695 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204165 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204166 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204167 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204168 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 5025 | P1_2-1448_3RITCHIE!,3HELENA IN#!+171 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204169 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204170 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.884 | 0.9668 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204171 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8755 | 0.9689 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204172 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8727 | 0.9695 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204173 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204174 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204175 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204176 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 5026 | P1_2-1448_3RITCHIE!,3HELENA IN#!+172 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204177 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204178 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.884 | 0.9668 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204179 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8755 | 0.9689 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204180 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8727 | 0.9695 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204181 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204182 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204183 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204184 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 5027 | P1_2-1448_3RITCHIE!,3HELENA IN#!+173 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204185 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204186 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.884 | 0.9668 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204187 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8756 | 0.9689 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204188 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8727 | 0.9695 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204189 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204190 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204191 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204192 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 5028 | P1_2-1448_3RITCHIE!,3HELENA IN#!+174 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204193 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204194 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204195 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204196 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204197 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204198 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204199 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204200 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 5032 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1WKRAFT! ID 3 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1WKRAFT! ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204201 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204202 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204203 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204204 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204205 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204206 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204207 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204208 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5034 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1NESBIT! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1NESBIT! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204209 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9126 | 0.9663 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204210 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8849 | 0.9668 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204211 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8765 | 0.9689 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204212 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8736 | 0.9695 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204213 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.869 | 0.9707 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204214 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8672 | 0.9711 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204215 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9175 | 0.9648 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204216 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8669 | 0.9734 | 0.92 | 1.05 | 5035 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G2RODEMR! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G2RODEMR! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204217 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9127 | 0.9663 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204218 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.885 | 0.9668 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204219 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8766 | 0.9689 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204220 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8737 | 0.9695 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204221 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8691 | 0.9707 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204222 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8673 | 0.9711 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204223 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9176 | 0.9648 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204224 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.867 | 0.9734 | 0.92 | 1.05 | 5036 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G3MADISN! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G3MADISN! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204225 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204226 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8846 | 0.9668 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204227 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8762 | 0.9689 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204228 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8733 | 0.9695 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204229 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8687 | 0.9707 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204230 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8669 | 0.9711 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204231 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9172 | 0.9648 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204232 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8666 | 0.9734 | 0.92 | 1.05 | 5039 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1 ACAD! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1 ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204233 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204234 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204235 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204236 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204237 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204238 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204239 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204240 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5040 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-1ACAD! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-1ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204241 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204242 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204243 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204244 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204245 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204246 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204247 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204248 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5041 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G1-2ACAD! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G1-2ACAD! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204249 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9122 | 0.9663 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204250 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8844 | 0.9668 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204251 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.876 | 0.9689 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204252 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8731 | 0.9695 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204253 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8685 | 0.9707 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204254 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8667 | 0.9711 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204255 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204256 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8664 | 0.9734 | 0.92 | 1.05 | 5042 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7COUGH! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204257 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204258 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204259 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204260 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204261 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204262 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204263 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204264 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5043 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-1COUGH! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-1COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204265 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204266 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204267 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204268 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204269 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204270 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204271 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204272 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5044 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_G7-2COUGH! ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_G7-2COUGH! ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204273 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9119 | 0.9663 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204274 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8841 | 0.9668 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204275 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8757 | 0.9689 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204276 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8728 | 0.9695 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204277 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8682 | 0.9707 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204278 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8664 | 0.9711 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204279 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9168 | 0.9648 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204280 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8661 | 0.9734 | 0.92 | 1.05 | 5055 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204281 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9119 | 0.9663 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204282 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8841 | 0.9668 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204283 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8757 | 0.9689 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204284 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8728 | 0.9695 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204285 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8682 | 0.9707 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204286 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8664 | 0.9711 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204287 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9168 | 0.9648 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204288 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8661 | 0.9734 | 0.92 | 1.05 | 5056 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGA&B1 ID 2 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGA&B1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204289 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9119 | 0.9663 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204290 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8841 | 0.9668 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204291 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8756 | 0.9689 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204292 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8728 | 0.9695 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204293 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8681 | 0.9707 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204294 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8663 | 0.9711 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204295 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9167 | 0.9648 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204296 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.866 | 0.9734 | 0.92 | 1.05 | 5057 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204297 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9118 | 0.9663 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204298 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8839 | 0.9668 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204299 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8755 | 0.9689 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204300 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8726 | 0.9695 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204301 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.868 | 0.9707 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204302 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8662 | 0.9711 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204303 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9166 | 0.9648 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204304 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8659 | 0.9734 | 0.92 | 1.05 | 5058 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_JBOGENC1 ID C | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_JBOGENC1 ID C | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204305 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9123 | 0.9663 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204306 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8845 | 0.9668 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204307 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8761 | 0.9689 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204308 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8732 | 0.9695 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204309 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8686 | 0.9707 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204310 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8668 | 0.9711 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204311 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9171 | 0.9648 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204312 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8665 | 0.9734 | 0.92 | 1.05 | 5074 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_BVR #1 1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_BVR #1 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204313 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204314 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204315 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204316 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204317 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204318 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204319 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204320 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5079 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204321 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204322 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204323 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204324 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204325 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204326 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204327 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204328 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5080 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK1&2 1 ID 2 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK1&2 1 ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204329 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204330 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204331 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204332 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204333 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204334 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204335 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204336 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5081 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 3 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 3 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204337 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204338 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204339 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204340 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204341 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204342 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204343 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204344 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5082 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 4 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 4 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204345 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9121 | 0.9663 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204346 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.8843 | 0.9668 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204347 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8759 | 0.9689 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204348 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.873 | 0.9695 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204349 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8684 | 0.9707 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204350 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8666 | 0.9711 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204351 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.917 | 0.9648 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204352 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8663 | 0.9734 | 0.92 | 1.05 | 5083 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_OZK345 1 ID 5 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_OZK345 1 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204353 | 18S | Approved | P3 | 31 | 3GILLETT! | VL |  |  |  |  | 0.9128 | 0.9663 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204354 | 18S | Approved | P3 | 31 | 3ELAINE | VL |  |  |  |  | 0.885 | 0.9668 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204355 | 18S | Approved | P3 | 31 | 3MARVELL | VL |  |  |  |  | 0.8766 | 0.9689 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204356 | 18S | Approved | P3 | 31 | 3BARTON | VL |  |  |  |  | 0.8738 | 0.9695 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204357 | 18S | Approved | P3 | 31 | 3HELENA.W+ | VL |  |  |  |  | 0.8692 | 0.9707 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204358 | 18S | Approved | P3 | 31 | 3HELENA.C | VL |  |  |  |  | 0.8674 | 0.9711 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204359 | 18S | Approved | P3 | 31 | 3DELUCE# | VL |  |  |  |  | 0.9176 | 0.9648 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204360 | 18S | Approved | P3 | 31 | 3HELENA IN#! | VL |  |  |  |  | 0.8671 | 0.9734 | 0.92 | 1.05 | 5089 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_MUSKOG4G ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_MUSKOG4G ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
204361 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0766 | 1.0432 | 0.92 | 1.05 | 5652 | P1_2-1604_8DANIEL%,6DANIEL!+G_1B.WLSN U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1B.WLSN U1 ID 1 |  | VH
204362 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0775 | 1.0432 | 0.92 | 1.05 | 5653 | P1_2-1604_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
204363 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5660 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ATTALA G1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ATTALA G1 ID 1 |  | VH
204364 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5661 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ATTALA G2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ATTALA G2 ID 1 |  | VH
204365 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5662 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ATTALA S1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ATTALA S1 ID 1 |  | VH
204366 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5663 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ANDRUS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ANDRUS U1 ID 1 |  | VH
204367 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5680 | P1_2-1604_8DANIEL%,6DANIEL!+G_1OUACHI_G1! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1OUACHI_G1! ID 1 |  | VH
204368 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5682 | P1_2-1604_8DANIEL%,6DANIEL!+G_1OUACHI_G2! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1OUACHI_G2! ID 1 |  | VH
204369 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5684 | P1_2-1604_8DANIEL%,6DANIEL!+G_1OUACHI_G3! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1OUACHI_G3! ID 1 |  | VH
204370 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5686 | P1_2-1604_8DANIEL%,6DANIEL!+G_1PERRYV_C1! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1PERRYV_C1! ID 1 |  | VH
204371 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5687 | P1_2-1604_8DANIEL%,6DANIEL!+G_1PERRYV_C2! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1PERRYV_C2! ID 1 |  | VH
204372 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5688 | P1_2-1604_8DANIEL%,6DANIEL!+G_1PERRYV_C3! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1PERRYV_C3! ID 1 |  | VH
204373 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5689 | P1_2-1604_8DANIEL%,6DANIEL!+G_1PERRYV_S1! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1PERRYV_S1! ID 1 |  | VH
204374 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5690 | P1_2-1604_8DANIEL%,6DANIEL!+G_1WHT BLUF U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1WHT BLUF U1 ID 1 |  | VH
204375 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5691 | P1_2-1604_8DANIEL%,6DANIEL!+G_1WHT BLUF U2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1WHT BLUF U2 ID 1 |  | VH
204376 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5694 | P1_2-1604_8DANIEL%,6DANIEL!+G_1CATHRINE U4 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1CATHRINE U4 ID 1 |  | VH
204377 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5703 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ANO U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ANO U1 ID 1 |  | VH
204378 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5704 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ANO U2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ANO U2 ID 1 |  | VH
204379 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5705 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ISES U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ISES U1 ID 1 |  | VH
204380 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5706 | P1_2-1604_8DANIEL%,6DANIEL!+G_1ISES U2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1ISES U2 ID 1 |  | VH
204381 | 18S | Approved | P3 | 31 | 8DANIEL | VH |  |  |  |  | 1.0764 | 1.0432 | 0.92 | 1.05 | 5707 | P1_2-1604_8DANIEL%,6DANIEL!+G_1PLUM PT U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1604_8DANIEL%,6DANIEL! | G_1PLUM PT U1 ID 1 |  | VH
204382 | 18S | Approved | P3 | 31 | 4CANEY | VL |  |  |  |  | 0.8675 | 0.995 | 0.92 | 1.05 | 5817 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204383 | 18S | Approved | P3 | 31 | CENTNL 4 | VL |  |  |  |  | 0.9156 | 0.9928 | 0.92 | 1.05 | 5817 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204384 | 18S | Approved | P3 | 31 | OAKDALE4 | VL |  |  |  |  | 0.8695 | 0.9932 | 0.92 | 1.05 | 5817 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204385 | 18S | Approved | P3 | 31 | PNPRARIE 4 | VL |  |  |  |  | 0.8603 | 1.0072 | 0.92 | 1.05 | 5817 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204386 | 18S | Approved | P3 | 31 | WSTBAY 4 | VL |  |  |  |  | 0.8814 | 0.9918 | 0.92 | 1.05 | 5817 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204387 | 18S | Approved | P3 | 31 | 4CANEY | VL |  |  |  |  | 0.8696 | 0.995 | 0.92 | 1.05 | 5972 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204388 | 18S | Approved | P3 | 31 | CENTNL 4 | VL |  |  |  |  | 0.9175 | 0.9928 | 0.92 | 1.05 | 5972 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204389 | 18S | Approved | P3 | 31 | OAKDALE4 | VL |  |  |  |  | 0.8715 | 0.9932 | 0.92 | 1.05 | 5972 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204390 | 18S | Approved | P3 | 31 | PNPRARIE 4 | VL |  |  |  |  | 0.8624 | 1.0072 | 0.92 | 1.05 | 5972 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204391 | 18S | Approved | P3 | 31 | WSTBAY 4 | VL |  |  |  |  | 0.8834 | 0.9918 | 0.92 | 1.05 | 5972 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204392 | 18S | Approved | P3 | 31 | 4CANEY | VL |  |  |  |  | 0.8702 | 0.995 | 0.92 | 1.05 | 5975 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G3MADISN! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G3MADISN! ID 1
204393 | 18S | Approved | P3 | 31 | CENTNL 4 | VL |  |  |  |  | 0.9181 | 0.9928 | 0.92 | 1.05 | 5975 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G3MADISN! ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G3MADISN! ID 1
204394 | 18S | Approved | P3 | 31 | OAKDALE4 | VL |  |  |  |  | 0.8722 | 0.9932 | 0.92 | 1.05 | 5975 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G3MADISN! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G3MADISN! ID 1
204395 | 18S | Approved | P3 | 31 | PNPRARIE 4 | VL |  |  |  |  | 0.8631 | 1.0072 | 0.92 | 1.05 | 5975 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G3MADISN! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G3MADISN! ID 1
204396 | 18S | Approved | P3 | 31 | WSTBAY 4 | VL |  |  |  |  | 0.884 | 0.9918 | 0.92 | 1.05 | 5975 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_G3MADISN! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_G3MADISN! ID 1
204397 | 18S | Approved | P3 | 31 | 4VEAZIE | VL |  |  |  |  | 0.8871 | 0.9781 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204398 | 18S | Approved | P3 | 31 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9192 | 0.9643 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204399 | 18S | Approved | P3 | 31 | 4BOBCAT | VL |  |  |  |  | 0.9181 | 0.9707 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204400 | 18S | Approved | P3 | 31 | 4CHAMPAGNE! | VL |  |  |  |  | 0.919 | 0.9744 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204401 | 18S | Approved | P3 | 31 | 4LINE-642_TP | VL |  |  |  |  | 0.9193 | 0.9644 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204402 | 18S | Approved | P3 | 31 | 4COL_SPRINGS | VL |  |  |  |  | 0.9193 | 0.9643 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204403 | 18S | Approved | P3 | 31 | GUIDRY 4 | VL |  |  |  |  | 0.8857 | 0.9769 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204404 | 18S | Approved | P3 | 31 | PLAISAN4 | VL |  |  |  |  | 0.9012 | 0.9908 | 0.92 | 1.05 | 6095 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204405 | 18S | Approved | P3 | 31 | 4VEAZIE | VL |  |  |  |  | 0.8882 | 0.9781 | 0.92 | 1.05 | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204406 | 18S | Approved | P3 | 31 | GUIDRY 4 | VL |  |  |  |  | 0.8868 | 0.9769 | 0.92 | 1.05 | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204407 | 18S | Approved | P3 | 31 | PLAISAN4 | VL |  |  |  |  | 0.9023 | 0.9908 | 0.92 | 1.05 | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204408 | 18S | Approved | P3 | 31 | 4BOBCAT | VL |  |  |  |  | 0.9196 | 0.9707 | 0.92 | 1.05 | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204409 | 18S | Approved | P3 | 31 | 4CHAMPAGNE! | VL |  |  |  |  | 0.92 | 0.9744 | 0.92 | 1.05 | 6104 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
204410 | 18S | Approved | P3 | 31 | ELKS 6 | VL |  |  |  |  | 0.9142 | 0.9827 | 0.92 | 1.05 | 6915 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+192 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
204411 | 18S | Approved | P3 | 31 | BEADLE 6 | VL |  |  |  |  | 0.9147 | 0.9844 | 0.92 | 1.05 | 6915 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+192 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
204412 | 18S | Approved | P3 | 31 | ELKS 6 | VL |  |  |  |  | 0.9142 | 0.9827 | 0.92 | 1.05 | 6916 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+193 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
204413 | 18S | Approved | P3 | 31 | BEADLE 6 | VL |  |  |  |  | 0.9147 | 0.9844 | 0.92 | 1.05 | 6916 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+193 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
204414 | 18S | Approved | P3 | 31 | ELKS 6 | VL |  |  |  |  | 0.8934 | 0.9827 | 0.92 | 1.05 | 7151 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+192 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
204415 | 18S | Approved | P3 | 31 | ELKS 6 | VL |  |  |  |  | 0.8934 | 0.9827 | 0.92 | 1.05 | 7152 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+193 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
204416 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0548 | 1.0225 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204417 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.0557 | 1.0273 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204418 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0552 | 1.027 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204419 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0548 | 1.0266 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204420 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0544 | 1.0267 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204421 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0522 | 1.0244 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204422 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.0511 | 1.0238 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204423 | 18S | Approved | P3 | 31 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0503 | 1.0233 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204424 | 18S | Approved | P3 | 31 | 3WASHINGTON+ | VH |  |  |  |  | 1.0506 | 1.0238 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204425 | 18S | Approved | P3 | 31 | 3FAYETTE | VH |  |  |  |  | 1.0509 | 1.0272 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204426 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.0637 | 1.0251 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204427 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0632 | 1.0293 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204428 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0634 | 1.0298 | 0.92 | 1.05 | 7196 | G_1BCAJUN2_U1% ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U1% ID 1 |  | VH
204429 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0548 | 1.0225 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204430 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.0557 | 1.0273 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204431 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0552 | 1.027 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204432 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0548 | 1.0266 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204433 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0544 | 1.0267 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204434 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0522 | 1.0244 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204435 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.0511 | 1.0238 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204436 | 18S | Approved | P3 | 31 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0503 | 1.0233 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204437 | 18S | Approved | P3 | 31 | 3WASHINGTON+ | VH |  |  |  |  | 1.0506 | 1.0238 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204438 | 18S | Approved | P3 | 31 | 3FAYETTE | VH |  |  |  |  | 1.0509 | 1.0272 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204439 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.0637 | 1.0251 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204440 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0632 | 1.0293 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204441 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0634 | 1.0298 | 0.92 | 1.05 | 7198 | G_1BCAJUN2_U3% ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1BCAJUN2_U3% ID 1 |  | VH
204442 | 18S | Approved | P3 | 31 | 4STALEY! | VL |  |  |  |  | 0.9097 | 0.9871 | 0.92 | 1.05 | 7211 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
204443 | 18S | Approved | P3 | 31 | 4MAGROVE | VL |  |  |  |  | 0.9196 | 0.9875 | 0.92 | 1.05 | 7211 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
204444 | 18S | Approved | P3 | 31 | 4UNONGSU! | VL |  |  |  |  | 0.9108 | 0.9928 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204445 | 18S | Approved | P3 | 31 | 4KIRBY | VL |  |  |  |  | 0.9033 | 0.993 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204446 | 18S | Approved | P3 | 31 | 4CALL! | VL |  |  |  |  | 0.8992 | 0.9938 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204447 | 18S | Approved | P3 | 31 | 4NBUNA | VL |  |  |  |  | 0.8933 | 0.9975 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334304 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204448 | 18S | Approved | P3 | 31 | 4BUNASW | VL |  |  |  |  | 0.8933 | 0.9975 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334305 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204449 | 18S | Approved | P3 | 31 | 4TEMPLE | VL |  |  |  |  | 0.8933 | 0.9975 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334306 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204450 | 18S | Approved | P3 | 31 | 4BUNA! | VL |  |  |  |  | 0.8926 | 0.9993 | 0.92 | 1.05 | 7212 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334307 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204451 | 18S | Approved | P3 | 31 | 2DEWEYVL! | VL |  |  |  |  | 0.9116 | 0.9816 | 0.92 | 1.05 | 7213 | G_4RAYBURN% ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204452 | 18S | Approved | P3 | 31 | 2SKBVREG | VL |  |  |  |  | 0.9133 | 0.9833 | 0.92 | 1.05 | 7213 | G_4RAYBURN% ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204453 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.9182 | 0.9414 | 0.92 | 1.05 | 7214 | G_1EXXONGT1! ID 1+P1_2-259_8CYPRESS%,8HARTBRG% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-259_8CYPRESS%,8HARTBRG% | G_1EXXONGT1! ID 1 |  | Facility: Radial
204454 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.9123 | 0.9414 | 0.92 | 1.05 | 7217 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
204455 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.912 | 0.9414 | 0.92 | 1.05 | 7218 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
204456 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.9157 | 0.9414 | 0.92 | 1.05 | 7219 | G_1EXXONGT1! ID 1+P1_2-298_4CENTRAL-TX!,4UNION! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-298_4CENTRAL-TX!,4UNION! | G_1EXXONGT1! ID 1 |  | Facility: Radial
204457 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.913 | 0.9414 | 0.92 | 1.05 | 7220 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 |  | Facility: Radial
204458 | 18S | Approved | P3 | 31 | 2NECHESO | VL |  |  |  |  | 0.9107 | 0.9414 | 0.92 | 1.05 | 7221 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
204459 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0543 | 1.0225 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204460 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.0548 | 1.0273 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204461 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0543 | 1.027 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204462 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0539 | 1.0266 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204463 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0535 | 1.0267 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204464 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0513 | 1.0244 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204465 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.0502 | 1.0238 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204466 | 18S | Approved | P3 | 31 | 3FAYETTE | VH |  |  |  |  | 1.0502 | 1.0272 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204467 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.063 | 1.0251 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204468 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0627 | 1.0293 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204469 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0629 | 1.0298 | 0.92 | 1.05 | 7238 | G_1GYP U3! ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U3! ID 1 |  | VH
204470 | 18S | Approved | P3 | 31 | 3CLAYTN! | VL |  |  |  |  | 0.9167 | 0.9854 | 0.92 | 1.05 | 7239 | G_1GYP U3! ID 1+P1_2-924_3GYPSY%,3CLAYTN! | 336230 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1GYP U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
204471 | 18S | Approved | P3 | 31 | 3NORCO% | VL |  |  |  |  | 0.9175 | 0.9827 | 0.92 | 1.05 | 7239 | G_1GYP U3! ID 1+P1_2-924_3GYPSY%,3CLAYTN! | 336231 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1GYP U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
204472 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0549 | 1.0225 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204473 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.0556 | 1.0273 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204474 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0551 | 1.027 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204475 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0548 | 1.0266 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204476 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0543 | 1.0267 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204477 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0521 | 1.0244 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204478 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.051 | 1.0238 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204479 | 18S | Approved | P3 | 31 | 3S.NATCHEZ! | VH |  |  |  |  | 1.0503 | 1.0233 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204480 | 18S | Approved | P3 | 31 | 3WASHINGTON+ | VH |  |  |  |  | 1.0506 | 1.0238 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204481 | 18S | Approved | P3 | 31 | 3FAYETTE | VH |  |  |  |  | 1.051 | 1.0272 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204482 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.0637 | 1.0251 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204483 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0633 | 1.0293 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204484 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0635 | 1.0298 | 0.92 | 1.05 | 7240 | G_1GYP U2! ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1GYP U2! ID 1 |  | VH
204485 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0542 | 1.0225 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204486 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.0546 | 1.0273 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204487 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0541 | 1.027 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204488 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0538 | 1.0266 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204489 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0534 | 1.0267 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204490 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0511 | 1.0244 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204491 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.0501 | 1.0238 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204492 | 18S | Approved | P3 | 31 | 3FAYETTE | VH |  |  |  |  | 1.0501 | 1.0272 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204493 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.0628 | 1.0251 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204494 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0626 | 1.0293 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204495 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0628 | 1.0298 | 0.92 | 1.05 | 7247 | G_1MICH U3! ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1MICH U3! ID 1 |  | VH
204496 | 18S | Approved | P3 | 31 | 3GILBERT | VH |  |  |  |  | 1.0546 | 1.0225 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204497 | 18S | Approved | P3 | 31 | 3NATCHEZSES% | VH |  |  |  |  | 1.055 | 1.0273 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204498 | 18S | Approved | P3 | 31 | 3PINE RIDGE+ | VH |  |  |  |  | 1.0545 | 1.027 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204499 | 18S | Approved | P3 | 31 | 3PINE RIDGE | VH |  |  |  |  | 1.0542 | 1.0266 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204500 | 18S | Approved | P3 | 31 | 3NATCHEZ! | VH |  |  |  |  | 1.0537 | 1.0267 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204501 | 18S | Approved | P3 | 31 | 3J.MANVILLE | VH |  |  |  |  | 1.0515 | 1.0244 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204502 | 18S | Approved | P3 | 31 | 3INTL PAPER | VH |  |  |  |  | 1.0504 | 1.0238 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204503 | 18S | Approved | P3 | 31 | 3RED_GUM! | VH |  |  |  |  | 1.063 | 1.0251 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204504 | 18S | Approved | P3 | 31 | 3METROPOLIS | VH |  |  |  |  | 1.0629 | 1.0293 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204505 | 18S | Approved | P3 | 31 | 3WISNER | VH |  |  |  |  | 1.0631 | 1.0298 | 0.92 | 1.05 | 7256 | G_1B.WLSN U2 ID 1+352 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-116_3BLACK_RIV,3PLANTATION!,3RED_GUM! | G_1B.WLSN U2 ID 1 |  | VH
204506 | 18S | Approved | P3 | 31 | 5HUGHES | VL |  |  |  |  | 0.9191 | 0.9887 | 0.92 | 1.05 | 7287 | G_1BAILEY U1 ID 1+1736 | 338028 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
204507 | 18S | Approved | P3 | 31 | 5WM GATEWAY | VL |  |  |  |  | 0.9187 | 0.9976 | 0.92 | 1.05 | 7287 | G_1BAILEY U1 ID 1+1736 | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
204508 | 18S | Approved | P3 | 31 | MAURICE2 | VL |  |  |  |  | 0.9169 | 1.0094 | 0.92 | 1.05 | 7288 | G_G1WKRAFT! ID 3+P1_2-1171_6MONTGOMERY!,CLARN 6! | 500565 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1171_6MONTGOMERY!,CLARN 6! | G_G1WKRAFT! ID 3 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204509 | 18S | Approved | P3 | 31 | 3MINDEN_LG | VL |  |  |  |  | 0.9132 | 0.9854 | 0.92 | 1.05 | 7291 | G_G1DOLHIL! ID 1+P1_2-1192_3MINDEN_LA!,3SAREPTA! | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204510 | 18S | Approved | P3 | 31 | 3MINDEN_LA! | VL |  |  |  |  | 0.9162 | 0.9933 | 0.92 | 1.05 | 7291 | G_G1DOLHIL! ID 1+P1_2-1192_3MINDEN_LA!,3SAREPTA! | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204511 | 18S | Approved | P3 | 31 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9147 | 0.992 | 0.92 | 1.05 | 7291 | G_G1DOLHIL! ID 1+P1_2-1192_3MINDEN_LA!,3SAREPTA! | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204512 | 18W | Approved | P0 | 32 | 5HORN LAKE% | VH |  |  |  |  | 1.0601 | 1.0601 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
204513 | 18W | Approved | P0 | 32 | 8UNION MS | VH |  |  |  |  | 1.0502 | 1.0502 | 0.92 | 1.05 |  | ** Base Case ** | 360033 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204514 | 18W | Approved | P0 | 32 | 8E POINT AL | VH |  |  |  |  | 1.0519 | 1.0519 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204515 | 18W | Approved | P0 | 32 | 8WID CRK FP | VH |  |  |  |  | 1.0507 | 1.0507 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204516 | 18W | Approved | P0 | 32 | 8PLEASANT HL | VH |  |  |  |  | 1.0508 | 1.0508 | 0.92 | 1.05 |  | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204517 | 18W | Approved | P0 | 32 | 8BENTON MS | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 |  | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204518 | 18W | Approved | P0 | 32 | 8LINDSYHILL | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 |  | ** Base Case ** | 385336 |  |  |  | 500 | 500 | 346 | SOCO |  |  | ** Base Case ** |  |  | VH
204519 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0574 | 1.037 | 0.92 | 1.05 | 1925 | P1_2-233_2WINSHIR!,2PANSY!+G_1BCAJUN2_U1% ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1BCAJUN2_U1% ID 1 |  | VH
204520 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0574 | 1.037 | 0.92 | 1.05 | 1927 | P1_2-233_2WINSHIR!,2PANSY!+G_1BCAJUN2_U3% ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1BCAJUN2_U3% ID 1 |  | VH
204521 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0586 | 1.037 | 0.92 | 1.05 | 1950 | P1_2-233_2WINSHIR!,2PANSY!+G_1G1SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G1SABIN! ID 1 |  | VH
204522 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0586 | 1.037 | 0.92 | 1.05 | 1951 | P1_2-233_2WINSHIR!,2PANSY!+G_1G2SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G2SABIN! ID 1 |  | VH
204523 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0599 | 1.037 | 0.92 | 1.05 | 1952 | P1_2-233_2WINSHIR!,2PANSY!+G_1G3SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G3SABIN! ID 1 |  | VH
204524 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0578 | 1.037 | 0.92 | 1.05 | 1953 | P1_2-233_2WINSHIR!,2PANSY!+G_1G5SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G5SABIN! ID 1 |  | VH
204525 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0575 | 1.037 | 0.92 | 1.05 | 1955 | P1_2-233_2WINSHIR!,2PANSY!+G_1DUPONTU! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1DUPONTU! ID 1 |  | VH
204526 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0575 | 1.037 | 0.92 | 1.05 | 1962 | P1_2-233_2WINSHIR!,2PANSY!+G_1RS_CGN_R5! ID 5 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1RS_CGN_R5! ID 5 |  | VH
204527 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0581 | 1.037 | 0.92 | 1.05 | 1967 | P1_2-233_2WINSHIR!,2PANSY!+G_1NELSON_G4! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1NELSON_G4! ID 1 |  | VH
204528 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0583 | 1.037 | 0.92 | 1.05 | 1968 | P1_2-233_2WINSHIR!,2PANSY!+G_1NELSON_G6! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1NELSON_G6! ID 1 |  | VH
204529 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1972 | P1_2-233_2WINSHIR!,2PANSY!+G_6DOW_COGEN% ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_6DOW_COGEN% ID 1 |  | VH
204530 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1973 | P1_2-233_2WINSHIR!,2PANSY!+G_6DOW_COGEN% ID 2 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_6DOW_COGEN% ID 2 |  | VH
204531 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1975 | P1_2-233_2WINSHIR!,2PANSY!+G_6DOW_COGEN% ID 4 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_6DOW_COGEN% ID 4 |  | VH
204532 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1976 | P1_2-233_2WINSHIR!,2PANSY!+G_6DOW_COGEN% ID 5 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_6DOW_COGEN% ID 5 |  | VH
204533 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 1977 | P1_2-233_2WINSHIR!,2PANSY!+G_6DOW_COGEN% ID 6 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_6DOW_COGEN% ID 6 |  | VH
204534 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.057 | 1.037 | 0.92 | 1.05 | 1979 | P1_2-233_2WINSHIR!,2PANSY!+G_1CARVLE_C2! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1CARVLE_C2! ID 1 |  | VH
204535 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0578 | 1.037 | 0.92 | 1.05 | 1986 | P1_2-233_2WINSHIR!,2PANSY!+G_1RVR_BND_G1! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1RVR_BND_G1! ID 1 |  | VH
204536 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0579 | 1.037 | 0.92 | 1.05 | 1989 | P1_2-233_2WINSHIR!,2PANSY!+G_1WAT U3! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1WAT U3! ID 1 |  | VH
204537 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0574 | 1.037 | 0.92 | 1.05 | 2001 | P1_2-233_2WINSHIR!,2PANSY!+G_1NMIL U4! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1NMIL U4! ID 1 |  | VH
204538 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0574 | 1.037 | 0.92 | 1.05 | 2002 | P1_2-233_2WINSHIR!,2PANSY!+G_1NMIL U5! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1NMIL U5! ID 1 |  | VH
204539 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0576 | 1.037 | 0.92 | 1.05 | 2007 | P1_2-233_2WINSHIR!,2PANSY!+G_1GGNS U1 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1GGNS U1 ID 1 |  | VH
204540 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0568 | 1.037 | 0.92 | 1.05 | 2051 | P1_2-233_2WINSHIR!,2PANSY!+G_1ANO U1 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1ANO U1 ID 1 |  | VH
204541 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0568 | 1.037 | 0.92 | 1.05 | 2052 | P1_2-233_2WINSHIR!,2PANSY!+G_1ANO U2 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1ANO U2 ID 1 |  | VH
204542 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0569 | 1.037 | 0.92 | 1.05 | 2101 | P1_2-233_2WINSHIR!,2PANSY!+G_HOUMA 3 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_HOUMA 3 ID 1 |  | VH
204543 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9137 | 1.0012 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204544 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.912 | 0.9891 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204545 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9092 | 0.9868 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204546 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.908 | 0.9858 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204547 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.912 | 0.9945 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204548 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.911 | 0.983 | 0.92 | 1.05 | 2157 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204549 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9138 | 1.0012 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204550 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.912 | 0.9891 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204551 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9092 | 0.9868 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204552 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.908 | 0.9858 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204553 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.912 | 0.9945 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204554 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9111 | 0.983 | 0.92 | 1.05 | 2158 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204555 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9141 | 1.0012 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204556 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9122 | 0.9891 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204557 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9093 | 0.9868 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204558 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9081 | 0.9858 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204559 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9123 | 0.9945 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204560 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9107 | 0.983 | 0.92 | 1.05 | 2162 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204561 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9005 | 1.0012 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204562 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.8983 | 0.9891 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204563 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.8954 | 0.9868 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204564 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.8942 | 0.9858 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204565 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.8985 | 0.9945 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204566 | 18W | Approved | P3 | 32 | 2PINELND | VL |  |  |  |  | 0.9151 | 0.9994 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204567 | 18W | Approved | P3 | 32 | 2TEMPL1* | VL |  |  |  |  | 0.9133 | 0.9978 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204568 | 18W | Approved | P3 | 32 | 2TEMPLE1 | VL |  |  |  |  | 0.913 | 0.9975 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204569 | 18W | Approved | P3 | 32 | 2TEMPL2* | VL |  |  |  |  | 0.913 | 0.9975 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204570 | 18W | Approved | P3 | 32 | 2TEMPLE2 | VL |  |  |  |  | 0.9128 | 0.9974 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204571 | 18W | Approved | P3 | 32 | 2TMPLSWC | VL |  |  |  |  | 0.9129 | 0.9974 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204572 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.8966 | 0.983 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204573 | 18W | Approved | P3 | 32 | 4PEACH! | VL |  |  |  |  | 0.9081 | 0.9998 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204574 | 18W | Approved | P3 | 32 | 4UNONGSU! | VL |  |  |  |  | 0.9196 | 0.9988 | 0.92 | 1.05 | 2167 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204575 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9139 | 1.0012 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204576 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9122 | 0.9891 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204577 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9094 | 0.9868 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204578 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9082 | 0.9858 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204579 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9122 | 0.9945 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204580 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9113 | 0.983 | 0.92 | 1.05 | 2168 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204581 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9139 | 1.0012 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204582 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9122 | 0.9891 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204583 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9094 | 0.9868 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204584 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9082 | 0.9858 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204585 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9122 | 0.9945 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204586 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9113 | 0.983 | 0.92 | 1.05 | 2169 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204587 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.913 | 1.0012 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204588 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9113 | 0.9891 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204589 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9084 | 0.9868 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204590 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9073 | 0.9858 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204591 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9113 | 0.9945 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204592 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9103 | 0.983 | 0.92 | 1.05 | 2170 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204593 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9089 | 1.0012 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204594 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.907 | 0.9891 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204595 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9042 | 0.9868 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204596 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.903 | 0.9858 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204597 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9071 | 0.9945 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204598 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9059 | 0.983 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204599 | 18W | Approved | P3 | 32 | 4PEACH! | VL |  |  |  |  | 0.9163 | 0.9998 | 0.92 | 1.05 | 2171 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204600 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.913 | 1.0012 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204601 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9112 | 0.9891 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204602 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9084 | 0.9868 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204603 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9072 | 0.9858 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204604 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9113 | 0.9945 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204605 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9102 | 0.983 | 0.92 | 1.05 | 2172 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204606 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204607 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204608 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9099 | 0.9868 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204609 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204610 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204611 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2191 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204612 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204613 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204614 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.91 | 0.9868 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204615 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204616 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9128 | 0.9945 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204617 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2194 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 4 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204618 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204619 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204620 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.91 | 0.9868 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204621 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204622 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9128 | 0.9945 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204623 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2195 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 5 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204624 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204625 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204626 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9099 | 0.9868 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204627 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204628 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204629 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2196 | P1_2-237_4RAYBURN%,4MILLCR!+G_6DOW_COGEN% ID 6 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204630 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9145 | 1.0012 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204631 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204632 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.91 | 0.9868 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204633 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204634 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9128 | 0.9945 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204635 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2198 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CARVLE_C2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204636 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9148 | 1.0012 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204637 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9131 | 0.9891 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204638 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9103 | 0.9868 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204639 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9092 | 0.9858 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204640 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9131 | 0.9945 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204641 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9124 | 0.983 | 0.92 | 1.05 | 2208 | P1_2-237_4RAYBURN%,4MILLCR!+G_1WAT U3! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1WAT U3! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204642 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204643 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9127 | 0.9891 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204644 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9099 | 0.9868 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204645 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204646 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204647 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9119 | 0.983 | 0.92 | 1.05 | 2270 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204648 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204649 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9127 | 0.9891 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204650 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9099 | 0.9868 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204651 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9087 | 0.9858 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204652 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204653 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9119 | 0.983 | 0.92 | 1.05 | 2271 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204654 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9145 | 1.0012 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204655 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9126 | 0.9891 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204656 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9097 | 0.9868 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204657 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9085 | 0.9858 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204658 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204659 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.9111 | 0.983 | 0.92 | 1.05 | 2303 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204660 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204661 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204662 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.91 | 0.9868 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204663 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204664 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9128 | 0.9945 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204665 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2320 | P1_2-237_4RAYBURN%,4MILLCR!+G_HOUMA 3 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_HOUMA 3 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204666 | 18W | Approved | P3 | 32 | 4MILLCR! | VL |  |  |  |  | 0.9144 | 1.0012 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204667 | 18W | Approved | P3 | 32 | 4PINELND | VL |  |  |  |  | 0.9128 | 0.9891 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204668 | 18W | Approved | P3 | 32 | 4BROADUS | VL |  |  |  |  | 0.9099 | 0.9868 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204669 | 18W | Approved | P3 | 32 | 4ETOIL | VL |  |  |  |  | 0.9088 | 0.9858 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204670 | 18W | Approved | P3 | 32 | 4HRTNHIL | VL |  |  |  |  | 0.9127 | 0.9945 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204671 | 18W | Approved | P3 | 32 | 2WEIRGAT | VL |  |  |  |  | 0.912 | 0.983 | 0.92 | 1.05 | 2356 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
204672 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.8933 | 0.9827 | 0.92 | 1.05 | 2381 | P1_2-414_2ECHO!,2DEWEYVL!+G_4RAYBURN% ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204673 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.8949 | 0.9844 | 0.92 | 1.05 | 2381 | P1_2-414_2ECHO!,2DEWEYVL!+G_4RAYBURN% ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204674 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.902 | 0.9827 | 0.92 | 1.05 | 2410 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204675 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9036 | 0.9844 | 0.92 | 1.05 | 2410 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204676 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.902 | 0.9827 | 0.92 | 1.05 | 2413 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 4 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204677 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9036 | 0.9844 | 0.92 | 1.05 | 2413 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 4 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 4 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204678 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.902 | 0.9827 | 0.92 | 1.05 | 2414 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 5 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204679 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9036 | 0.9844 | 0.92 | 1.05 | 2414 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 5 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 5 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204680 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.902 | 0.9827 | 0.92 | 1.05 | 2415 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 6 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204681 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9036 | 0.9844 | 0.92 | 1.05 | 2415 | P1_2-414_2ECHO!,2DEWEYVL!+G_6DOW_COGEN% ID 6 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_6DOW_COGEN% ID 6 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204682 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.9021 | 0.9827 | 0.92 | 1.05 | 2417 | P1_2-414_2ECHO!,2DEWEYVL!+G_1CARVLE_C2! ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204683 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9037 | 0.9844 | 0.92 | 1.05 | 2417 | P1_2-414_2ECHO!,2DEWEYVL!+G_1CARVLE_C2! ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1CARVLE_C2! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204684 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.903 | 0.9827 | 0.92 | 1.05 | 2427 | P1_2-414_2ECHO!,2DEWEYVL!+G_1WAT U3! ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1WAT U3! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204685 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9046 | 0.9844 | 0.92 | 1.05 | 2427 | P1_2-414_2ECHO!,2DEWEYVL!+G_1WAT U3! ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1WAT U3! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204686 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.9018 | 0.9827 | 0.92 | 1.05 | 2489 | P1_2-414_2ECHO!,2DEWEYVL!+G_1ANO U1 ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1ANO U1 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204687 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9034 | 0.9844 | 0.92 | 1.05 | 2489 | P1_2-414_2ECHO!,2DEWEYVL!+G_1ANO U1 ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1ANO U1 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204688 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.9018 | 0.9827 | 0.92 | 1.05 | 2490 | P1_2-414_2ECHO!,2DEWEYVL!+G_1ANO U2 ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1ANO U2 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204689 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9034 | 0.9844 | 0.92 | 1.05 | 2490 | P1_2-414_2ECHO!,2DEWEYVL!+G_1ANO U2 ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1ANO U2 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204690 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.8959 | 0.9827 | 0.92 | 1.05 | 2522 | P1_2-414_2ECHO!,2DEWEYVL!+G_G1DOLHIL! ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_G1DOLHIL! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204691 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.8975 | 0.9844 | 0.92 | 1.05 | 2522 | P1_2-414_2ECHO!,2DEWEYVL!+G_G1DOLHIL! ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_G1DOLHIL! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204692 | 18W | Approved | P3 | 32 | 2DEWEYVL! | VL |  |  |  |  | 0.902 | 0.9827 | 0.92 | 1.05 | 2539 | P1_2-414_2ECHO!,2DEWEYVL!+G_HOUMA 3 ID 1 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_HOUMA 3 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204693 | 18W | Approved | P3 | 32 | 2SKBVREG | VL |  |  |  |  | 0.9036 | 0.9844 | 0.92 | 1.05 | 2539 | P1_2-414_2ECHO!,2DEWEYVL!+G_HOUMA 3 ID 1 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_HOUMA 3 ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
204694 | 18W | Approved | P3 | 32 | 3LEEVLL | VL |  |  |  |  | 0.9057 | 1.0053 | 0.92 | 1.05 | 3015 | P1_2-808_3VLNTIN!,3GMEADW!+G_1RVR_BND_G1! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1RVR_BND_G1! ID 1 | None
204695 | 18W | Approved | P3 | 32 | 3FOURCHN | VL |  |  |  |  | 0.8949 | 0.9956 | 0.92 | 1.05 | 3015 | P1_2-808_3VLNTIN!,3GMEADW!+G_1RVR_BND_G1! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1RVR_BND_G1! ID 1 | None
204696 | 18W | Approved | P3 | 32 | 3LEEVLL | VL |  |  |  |  | 0.9059 | 1.0053 | 0.92 | 1.05 | 3016 | P1_2-808_3VLNTIN!,3GMEADW!+G_1WAT U3! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1WAT U3! ID 1 | None
204697 | 18W | Approved | P3 | 32 | 3FOURCHN | VL |  |  |  |  | 0.8951 | 0.9956 | 0.92 | 1.05 | 3016 | P1_2-808_3VLNTIN!,3GMEADW!+G_1WAT U3! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1WAT U3! ID 1 | None
204698 | 18W | Approved | P3 | 32 | 3LEEVLL | VL |  |  |  |  | 0.9056 | 1.0053 | 0.92 | 1.05 | 3017 | P1_2-808_3VLNTIN!,3GMEADW!+G_1GGNS U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1GGNS U1 ID 1 | None
204699 | 18W | Approved | P3 | 32 | 3FOURCHN | VL |  |  |  |  | 0.8947 | 0.9956 | 0.92 | 1.05 | 3017 | P1_2-808_3VLNTIN!,3GMEADW!+G_1GGNS U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1GGNS U1 ID 1 | None
204700 | 18W | Approved | P3 | 32 | 3LEEVLL | VL |  |  |  |  | 0.9055 | 1.0053 | 0.92 | 1.05 | 3018 | P1_2-808_3VLNTIN!,3GMEADW!+G_1ISES U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U1 ID 1 | None
204701 | 18W | Approved | P3 | 32 | 3FOURCHN | VL |  |  |  |  | 0.8947 | 0.9956 | 0.92 | 1.05 | 3018 | P1_2-808_3VLNTIN!,3GMEADW!+G_1ISES U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U1 ID 1 | None
204702 | 18W | Approved | P3 | 32 | 3LEEVLL | VL |  |  |  |  | 0.9055 | 1.0053 | 0.92 | 1.05 | 3019 | P1_2-808_3VLNTIN!,3GMEADW!+G_1ISES U2 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 | None
204703 | 18W | Approved | P3 | 32 | 3FOURCHN | VL |  |  |  |  | 0.8947 | 0.9956 | 0.92 | 1.05 | 3019 | P1_2-808_3VLNTIN!,3GMEADW!+G_1ISES U2 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 | None
204704 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0529 | 0.994 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204705 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.064 | 0.9932 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204706 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0704 | 0.994 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204707 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.061 | 0.9838 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204708 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0706 | 0.9969 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204709 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.0609 | 0.9837 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204710 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.0568 | 1.0013 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204711 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0546 | 0.999 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204712 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0641 | 1.0001 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204713 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0712 | 1 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204714 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0673 | 0.9957 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204715 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0665 | 0.9949 | 0.92 | 1.05 | 3677 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U1% ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U1% ID 1 |  | VH
204716 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0529 | 0.994 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204717 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.064 | 0.9932 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204718 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0704 | 0.994 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204719 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.061 | 0.9838 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204720 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0706 | 0.9969 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204721 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.0609 | 0.9837 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204722 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.0568 | 1.0013 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204723 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0546 | 0.999 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204724 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0641 | 1.0001 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204725 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0712 | 1 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204726 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0673 | 0.9957 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204727 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0665 | 0.9949 | 0.92 | 1.05 | 3679 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1BCAJUN2_U3% ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1BCAJUN2_U3% ID 1 |  | VH
204728 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0538 | 0.994 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204729 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.0651 | 0.9932 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204730 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0716 | 0.994 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204731 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.0621 | 0.9838 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204732 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0718 | 0.9969 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204733 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.062 | 0.9837 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204734 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.0581 | 1.0013 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204735 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0559 | 0.999 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204736 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0654 | 1.0001 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204737 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0725 | 1 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204738 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0685 | 0.9957 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204739 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0677 | 0.9949 | 0.92 | 1.05 | 3705 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1G4SABIN! ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1G4SABIN! ID 1 |  | VH
204740 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0527 | 0.994 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204741 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.0639 | 0.9932 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204742 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0704 | 0.994 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204743 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.0609 | 0.9838 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204744 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0706 | 0.9969 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204745 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.0608 | 0.9837 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204746 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.057 | 1.0013 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204747 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0548 | 0.999 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204748 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0642 | 1.0001 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204749 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0713 | 1 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204750 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0673 | 0.9957 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204751 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0665 | 0.9949 | 0.92 | 1.05 | 3739 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U1! ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U1! ID 1 |  | VH
204752 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0527 | 0.994 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204753 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.0639 | 0.9932 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204754 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0704 | 0.994 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204755 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.0609 | 0.9838 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204756 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0706 | 0.9969 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204757 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.0608 | 0.9837 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204758 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.057 | 1.0013 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204759 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0548 | 0.999 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204760 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0642 | 1.0001 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204761 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0713 | 1 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204762 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0673 | 0.9957 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204763 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0665 | 0.9949 | 0.92 | 1.05 | 3740 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1WAT U2! ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1WAT U2! ID 1 |  | VH
204764 | 18W | Approved | P3 | 32 | 3CHATAWA+ | VH |  |  |  |  | 1.0543 | 0.994 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336535 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204765 | 18W | Approved | P3 | 32 | 3COLNIAL P/L | VH |  |  |  |  | 1.0657 | 0.9932 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336536 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204766 | 18W | Approved | P3 | 32 | 3FERNWOOD MS | VH |  |  |  |  | 1.0723 | 0.994 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336537 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204767 | 18W | Approved | P3 | 32 | 3PROGRESS+ | VH |  |  |  |  | 1.0628 | 0.9838 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336538 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204768 | 18W | Approved | P3 | 32 | 3OAKDALE+ | VH |  |  |  |  | 1.0726 | 0.9969 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336539 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204769 | 18W | Approved | P3 | 32 | 3PLANT.P/L | VH |  |  |  |  | 1.0627 | 0.9837 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336540 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204770 | 18W | Approved | P3 | 32 | 3JAYESS+ | VH |  |  |  |  | 1.059 | 1.0013 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336548 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204771 | 18W | Approved | P3 | 32 | 3JAYESS | VH |  |  |  |  | 1.0568 | 0.999 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336549 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204772 | 18W | Approved | P3 | 32 | 3FRIENDSHIP+ | VH |  |  |  |  | 1.0662 | 1.0001 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336550 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204773 | 18W | Approved | P3 | 32 | 3MCCOMB! | VH |  |  |  |  | 1.0733 | 1 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336551 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204774 | 18W | Approved | P3 | 32 | 3PISGAH MS+ | VH |  |  |  |  | 1.0693 | 0.9957 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336560 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204775 | 18W | Approved | P3 | 32 | 3W.MCCOMB | VH |  |  |  |  | 1.0685 | 0.9949 | 0.92 | 1.05 | 3821 | P1_2-998_3MCB!,3BROOKHAVEN!+G_1CAL G1 ID 1 | 336561 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-998_3MCB!,3BROOKHAVEN! | G_1CAL G1 ID 1 |  | VH
204776 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6270 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1NM G1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1NM G1 ID 1 |  | VH
204777 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6274 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1BCAJUN2_U1% ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1BCAJUN2_U1% ID 1 |  | VH
204778 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6276 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1BCAJUN2_U3% ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1BCAJUN2_U3% ID 1 |  | VH
204779 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6302 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1G4SABIN! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1G4SABIN! ID 1 |  | VH
204780 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6318 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1NELSON_G6! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1NELSON_G6! ID 1 |  | VH
204781 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6322 | P1_2-1522_8DELL%,8SANS SOUCI%+G_6DOW_COGEN% ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_6DOW_COGEN% ID 1 |  | VH
204782 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6323 | P1_2-1522_8DELL%,8SANS SOUCI%+G_6DOW_COGEN% ID 2 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_6DOW_COGEN% ID 2 |  | VH
204783 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6325 | P1_2-1522_8DELL%,8SANS SOUCI%+G_6DOW_COGEN% ID 4 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_6DOW_COGEN% ID 4 |  | VH
204784 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6326 | P1_2-1522_8DELL%,8SANS SOUCI%+G_6DOW_COGEN% ID 5 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_6DOW_COGEN% ID 5 |  | VH
204785 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6327 | P1_2-1522_8DELL%,8SANS SOUCI%+G_6DOW_COGEN% ID 6 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_6DOW_COGEN% ID 6 |  | VH
204786 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0621 | 1.0489 | 0.92 | 1.05 | 6329 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1CARVLE_C2! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1CARVLE_C2! ID 1 |  | VH
204787 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0626 | 1.0489 | 0.92 | 1.05 | 6336 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1RVR_BND_G1! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1RVR_BND_G1! ID 1 |  | VH
204788 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0627 | 1.0489 | 0.92 | 1.05 | 6339 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1WAT U3! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1WAT U3! ID 1 |  | VH
204789 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6351 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1NMIL U4! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1NMIL U4! ID 1 |  | VH
204790 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6352 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1NMIL U5! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1NMIL U5! ID 1 |  | VH
204791 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0628 | 1.0489 | 0.92 | 1.05 | 6357 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1GGNS U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1GGNS U1 ID 1 |  | VH
204792 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0629 | 1.0489 | 0.92 | 1.05 | 6389 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1WHT BLUF U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1WHT BLUF U1 ID 1 |  | VH
204793 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0629 | 1.0489 | 0.92 | 1.05 | 6390 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1WHT BLUF U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1WHT BLUF U2 ID 1 |  | VH
204794 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0629 | 1.0489 | 0.92 | 1.05 | 6401 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1ANO U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1ANO U1 ID 1 |  | VH
204795 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0631 | 1.0489 | 0.92 | 1.05 | 6402 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1ANO U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1ANO U2 ID 1 |  | VH
204796 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0628 | 1.0489 | 0.92 | 1.05 | 6403 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1ISES U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1ISES U1 ID 1 |  | VH
204797 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0629 | 1.0489 | 0.92 | 1.05 | 6404 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1ISES U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1ISES U2 ID 1 |  | VH
204798 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0627 | 1.0489 | 0.92 | 1.05 | 6425 | P1_2-1522_8DELL%,8SANS SOUCI%+G_1CAL G1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1CAL G1 ID 1 |  | VH
204799 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0626 | 1.0489 | 0.92 | 1.05 | 6434 | P1_2-1522_8DELL%,8SANS SOUCI%+G_G1DOLHIL! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_G1DOLHIL! ID 1 |  | VH
204800 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6436 | P1_2-1522_8DELL%,8SANS SOUCI%+G_G2RODEMR! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_G2RODEMR! ID 1 |  | VH
204801 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0625 | 1.0489 | 0.92 | 1.05 | 6437 | P1_2-1522_8DELL%,8SANS SOUCI%+G_G3MADISN! ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_G3MADISN! ID 1 |  | VH
204802 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.062 | 1.0489 | 0.92 | 1.05 | 6451 | P1_2-1522_8DELL%,8SANS SOUCI%+G_HOUMA 3 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_HOUMA 3 ID 1 |  | VH
204803 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6482 | P1_2-1522_8DELL%,8SANS SOUCI%+G_FLINTCR1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_FLINTCR1 ID 1 |  | VH
204804 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0625 | 1.0489 | 0.92 | 1.05 | 6483 | P1_2-1522_8DELL%,8SANS SOUCI%+G_PIRKEY 1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_PIRKEY 1 ID 1 |  | VH
204805 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6484 | P1_2-1522_8DELL%,8SANS SOUCI%+G_WELSH2-1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_WELSH2-1 ID 1 |  | VH
204806 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6485 | P1_2-1522_8DELL%,8SANS SOUCI%+G_WELSH3-1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_WELSH3-1 ID 1 |  | VH
204807 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6486 | P1_2-1522_8DELL%,8SANS SOUCI%+G_TURKCOAL ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_TURKCOAL ID 1 |  | VH
204808 | 18W | Approved | P3 | 32 | 8SANS SOUCI% | VH |  |  |  |  | 1.0624 | 1.0489 | 0.92 | 1.05 | 6487 | P1_2-1522_8DELL%,8SANS SOUCI%+G_MUSKOG4G ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_MUSKOG4G ID 1 |  | VH
204809 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0539 | 1.0424 | 0.92 | 1.05 | 6707 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1NM G1 ID 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1NM G1 ID 1 |  | VH
204810 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0577 | 1.0411 | 0.92 | 1.05 | 6707 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1NM G1 ID 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1NM G1 ID 1 |  | VH
204811 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0538 | 1.0436 | 0.92 | 1.05 | 6707 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1NM G1 ID 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1NM G1 ID 1 |  | VH
204812 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 6759 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+53 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 1 |  | VH
204813 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0525 | 1.0424 | 0.92 | 1.05 | 6762 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+56 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 4 |  | VH
204814 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 6762 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+56 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 4 |  | VH
204815 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0525 | 1.0424 | 0.92 | 1.05 | 6763 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+57 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 5 |  | VH
204816 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 6763 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+57 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 5 |  | VH
204817 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 6764 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+58 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_6DOW_COGEN% ID 6 |  | VH
204818 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0526 | 1.0424 | 0.92 | 1.05 | 6766 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+60 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1CARVLE_C2! ID 1 |  | VH
204819 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0566 | 1.0411 | 0.92 | 1.05 | 6766 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+60 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1CARVLE_C2! ID 1 |  | VH
204820 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0532 | 1.0424 | 0.92 | 1.05 | 6773 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+67 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1RVR_BND_G1! ID 1 |  | VH
204821 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0575 | 1.0411 | 0.92 | 1.05 | 6773 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+67 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1RVR_BND_G1! ID 1 |  | VH
204822 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0533 | 1.0424 | 0.92 | 1.05 | 6776 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+70 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WAT U3! ID 1 |  | VH
204823 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0576 | 1.0411 | 0.92 | 1.05 | 6776 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+70 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WAT U3! ID 1 |  | VH
204824 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0535 | 1.0424 | 0.92 | 1.05 | 6794 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+88 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1GGNS U1 ID 1 |  | VH
204825 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0578 | 1.0411 | 0.92 | 1.05 | 6794 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+88 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1GGNS U1 ID 1 |  | VH
204826 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0542 | 1.0424 | 0.92 | 1.05 | 6826 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+120 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U1 ID 1 |  | VH
204827 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0583 | 1.0411 | 0.92 | 1.05 | 6826 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+120 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U1 ID 1 |  | VH
204828 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0541 | 1.0436 | 0.92 | 1.05 | 6826 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+120 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U1 ID 1 |  | VH
204829 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0542 | 1.0424 | 0.92 | 1.05 | 6827 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+121 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U2 ID 1 |  | VH
204830 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0584 | 1.0411 | 0.92 | 1.05 | 6827 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+121 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U2 ID 1 |  | VH
204831 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0541 | 1.0436 | 0.92 | 1.05 | 6827 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+121 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1WHT BLUF U2 ID 1 |  | VH
204832 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0543 | 1.0424 | 0.92 | 1.05 | 6838 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U1 ID 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U1 ID 1 |  | VH
204833 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0584 | 1.0411 | 0.92 | 1.05 | 6838 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U1 ID 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U1 ID 1 |  | VH
204834 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0542 | 1.0436 | 0.92 | 1.05 | 6838 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U1 ID 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U1 ID 1 |  | VH
204835 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0546 | 1.0424 | 0.92 | 1.05 | 6839 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U2 ID 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U2 ID 1 |  | VH
204836 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0587 | 1.0411 | 0.92 | 1.05 | 6839 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U2 ID 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U2 ID 1 |  | VH
204837 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0545 | 1.0436 | 0.92 | 1.05 | 6839 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_1ANO U2 ID 1 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1ANO U2 ID 1 |  | VH
204838 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0533 | 1.0424 | 0.92 | 1.05 | 6865 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+160 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1CUMBRL F2HL ID 2 |  | VH
204839 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0566 | 1.0411 | 0.92 | 1.05 | 6865 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+160 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1CUMBRL F2HL ID 2 |  | VH
204840 | 18W | Approved | P3 | 32 | 8GLEASON CT | VH |  |  |  |  | 1.0536 | 1.0436 | 0.92 | 1.05 | 6865 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+160 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_1CUMBRL F2HL ID 2 |  | VH
204841 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0535 | 1.0424 | 0.92 | 1.05 | 6870 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+165 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_G1DOLHIL! ID 1 |  | VH
204842 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0576 | 1.0411 | 0.92 | 1.05 | 6870 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+165 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_G1DOLHIL! ID 1 |  | VH
204843 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0524 | 1.0424 | 0.92 | 1.05 | 6887 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_HOUMA 3 ID 1 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_HOUMA 3 ID 1 |  | VH
204844 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0411 | 0.92 | 1.05 | 6887 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+G_HOUMA 3 ID 1 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_HOUMA 3 ID 1 |  | VH
204845 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0536 | 1.0424 | 0.92 | 1.05 | 6918 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+213 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_FLINTCR1 ID 1 |  | VH
204846 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0575 | 1.0411 | 0.92 | 1.05 | 6918 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+213 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_FLINTCR1 ID 1 |  | VH
204847 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0534 | 1.0424 | 0.92 | 1.05 | 6919 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+214 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_PIRKEY 1 ID 1 |  | VH
204848 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0574 | 1.0411 | 0.92 | 1.05 | 6919 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+214 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_PIRKEY 1 ID 1 |  | VH
204849 | 18W | Approved | P3 | 32 | 8WEAKLEY TN | VH |  |  |  |  | 1.0535 | 1.0424 | 0.92 | 1.05 | 6923 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+218 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_MUSKOG4G ID 1 |  | VH
204850 | 18W | Approved | P3 | 32 | 8LAG CRK CT | VH |  |  |  |  | 1.0575 | 1.0411 | 0.92 | 1.05 | 6923 | P1_2-1585_8LAG CRK CT%,8LAG CRK CC!+218 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1585_8LAG CRK CT%,8LAG CRK CC! | G_MUSKOG4G ID 1 |  | VH
204851 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0753 | 1.042 | 0.92 | 1.05 | 7415 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 1 |  | VH
204852 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.075 | 1.042 | 0.92 | 1.05 | 7416 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 2 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 2 |  | VH
204853 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0749 | 1.042 | 0.92 | 1.05 | 7417 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 3 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 3 |  | VH
204854 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0753 | 1.042 | 0.92 | 1.05 | 7418 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 4 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 4 |  | VH
204855 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0751 | 1.042 | 0.92 | 1.05 | 7419 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 5 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 5 |  | VH
204856 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0752 | 1.042 | 0.92 | 1.05 | 7420 | P1_2-1607_8DANIEL%,6DANIEL!+G_6DOW_COGEN% ID 6 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_6DOW_COGEN% ID 6 |  | VH
204857 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0743 | 1.042 | 0.92 | 1.05 | 7422 | P1_2-1607_8DANIEL%,6DANIEL!+G_1CARVLE_C2! ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1CARVLE_C2! ID 1 |  | VH
204858 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0769 | 1.042 | 0.92 | 1.05 | 7450 | P1_2-1607_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
204859 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0758 | 1.042 | 0.92 | 1.05 | 7494 | P1_2-1607_8DANIEL%,6DANIEL!+G_1ANO U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1ANO U1 ID 1 |  | VH
204860 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0758 | 1.042 | 0.92 | 1.05 | 7495 | P1_2-1607_8DANIEL%,6DANIEL!+G_1ANO U2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1ANO U2 ID 1 |  | VH
204861 | 18W | Approved | P3 | 32 | 8DANIEL | VH |  |  |  |  | 1.0755 | 1.042 | 0.92 | 1.05 | 7544 | P1_2-1607_8DANIEL%,6DANIEL!+G_HOUMA 3 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_HOUMA 3 ID 1 |  | VH
204862 | 18W | Approved | P3 | 32 | CLARN 4 | VH |  |  |  |  | 1.0546 | 1.0444 | 0.92 | 1.05 | 7965 | P1_2-1640_CLARN 4!,NATCH 4!+G_G2RODEMR! ID 1 | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_G2RODEMR! ID 1 |  | VH
204863 | 18W | Approved | P3 | 32 | CLARN 4 | VH |  |  |  |  | 1.0544 | 1.0444 | 0.92 | 1.05 | 7966 | P1_2-1640_CLARN 4!,NATCH 4!+G_G3MADISN! ID 1 | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_G3MADISN! ID 1 |  | VH
204864 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8854 | 1 | 0.92 | 1.05 | 8037 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204865 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8873 | 0.9986 | 0.92 | 1.05 | 8037 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204866 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8783 | 1.0097 | 0.92 | 1.05 | 8037 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204867 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8971 | 0.997 | 0.92 | 1.05 | 8037 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
204868 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8853 | 1 | 0.92 | 1.05 | 8062 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
204869 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8872 | 0.9986 | 0.92 | 1.05 | 8062 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
204870 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8782 | 1.0097 | 0.92 | 1.05 | 8062 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
204871 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8969 | 0.997 | 0.92 | 1.05 | 8062 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
204872 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8066 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 1
204873 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8066 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 1
204874 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8066 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 1
204875 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8066 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 1
204876 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8067 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 2 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 2
204877 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8067 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 2 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 2
204878 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8067 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 2 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 2
204879 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8067 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 2 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 2
204880 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8069 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 4 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 4
204881 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8069 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 4 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 4
204882 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8069 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 4 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 4
204883 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8069 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 4 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 4
204884 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8070 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 5 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 5
204885 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8070 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 5 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 5
204886 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8070 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 5 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 5
204887 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8070 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 5 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 5
204888 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8071 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 6 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 6
204889 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8071 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 6 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 6
204890 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8071 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 6 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 6
204891 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8071 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_6DOW_COGEN% ID 6 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_6DOW_COGEN% ID 6
204892 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8884 | 1 | 0.92 | 1.05 | 8073 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1CARVLE_C2! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1CARVLE_C2! ID 1
204893 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8903 | 0.9986 | 0.92 | 1.05 | 8073 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1CARVLE_C2! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1CARVLE_C2! ID 1
204894 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8814 | 1.0097 | 0.92 | 1.05 | 8073 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1CARVLE_C2! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1CARVLE_C2! ID 1
204895 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.9 | 0.997 | 0.92 | 1.05 | 8073 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1CARVLE_C2! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1CARVLE_C2! ID 1
204896 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8892 | 1 | 0.92 | 1.05 | 8083 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1WAT U3! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1WAT U3! ID 1
204897 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8911 | 0.9986 | 0.92 | 1.05 | 8083 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1WAT U3! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1WAT U3! ID 1
204898 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8821 | 1.0097 | 0.92 | 1.05 | 8083 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1WAT U3! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1WAT U3! ID 1
204899 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.9008 | 0.997 | 0.92 | 1.05 | 8083 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1WAT U3! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1WAT U3! ID 1
204900 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8882 | 1 | 0.92 | 1.05 | 8145 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U1 ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1
204901 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8901 | 0.9986 | 0.92 | 1.05 | 8145 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U1 ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1
204902 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8811 | 1.0097 | 0.92 | 1.05 | 8145 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U1 ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1
204903 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8998 | 0.997 | 0.92 | 1.05 | 8145 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U1 ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1
204904 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8881 | 1 | 0.92 | 1.05 | 8146 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U2 ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U2 ID 1
204905 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.89 | 0.9986 | 0.92 | 1.05 | 8146 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U2 ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U2 ID 1
204906 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8811 | 1.0097 | 0.92 | 1.05 | 8146 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U2 ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U2 ID 1
204907 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8998 | 0.997 | 0.92 | 1.05 | 8146 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_1ANO U2 ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U2 ID 1
204908 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8845 | 1 | 0.92 | 1.05 | 8178 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204909 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8864 | 0.9986 | 0.92 | 1.05 | 8178 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204910 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8774 | 1.0097 | 0.92 | 1.05 | 8178 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204911 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8962 | 0.997 | 0.92 | 1.05 | 8178 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230 |  | Construct Messick 500 kV SS at Messick 230 and install transformer
204912 | 18W | Approved | P3 | 32 | 4CANEY | VL |  |  |  |  | 0.8883 | 1 | 0.92 | 1.05 | 8195 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_HOUMA 3 ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_HOUMA 3 ID 1
204913 | 18W | Approved | P3 | 32 | OAKDALE4 | VL |  |  |  |  | 0.8902 | 0.9986 | 0.92 | 1.05 | 8195 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_HOUMA 3 ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_HOUMA 3 ID 1
204914 | 18W | Approved | P3 | 32 | PNPRARIE 4 | VL |  |  |  |  | 0.8813 | 1.0097 | 0.92 | 1.05 | 8195 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_HOUMA 3 ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_HOUMA 3 ID 1
204915 | 18W | Approved | P3 | 32 | WSTBAY 4 | VL |  |  |  |  | 0.8999 | 0.997 | 0.92 | 1.05 | 8195 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_HOUMA 3 ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_HOUMA 3 ID 1
204916 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8501 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 1 |  | VH
204917 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8501 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 1 |  | VH
204918 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8504 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 4 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 4 |  | VH
204919 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8504 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 4 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 4 |  | VH
204920 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8505 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 5 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 5 |  | VH
204921 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8505 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 5 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 5 |  | VH
204922 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8506 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 6 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 6 |  | VH
204923 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8506 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_6DOW_COGEN% ID 6 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_6DOW_COGEN% ID 6 |  | VH
204924 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8508 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1CARVLE_C2! ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1CARVLE_C2! ID 1 |  | VH
204925 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8508 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1CARVLE_C2! ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1CARVLE_C2! ID 1 |  | VH
204926 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0515 | 1.0185 | 0.92 | 1.05 | 8518 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1WAT U3! ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1WAT U3! ID 1 |  | VH
204927 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0515 | 1.0185 | 0.92 | 1.05 | 8518 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1WAT U3! ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1WAT U3! ID 1 |  | VH
204928 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8580 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1ANO U1 ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U1 ID 1 |  | VH
204929 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8580 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1ANO U1 ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U1 ID 1 |  | VH
204930 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8581 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1ANO U2 ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U2 ID 1 |  | VH
204931 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8581 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_1ANO U2 ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U2 ID 1 |  | VH
204932 | 18W | Approved | P3 | 32 | TENRUSK7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8629 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_HOUMA 3 ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_HOUMA 3 ID 1 |  | VH
204933 | 18W | Approved | P3 | 32 | TENGEN 7 | VH |  |  |  |  | 1.0514 | 1.0185 | 0.92 | 1.05 | 8629 | P1_2-1866_LEBROCK7!,TENRUSK7!+G_HOUMA 3 ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_HOUMA 3 ID 1 |  | VH
204934 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8925 | 0.9965 | 0.92 | 1.05 | 8715 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+53 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_6DOW_COGEN% ID 1 |  | Facility: Radial
204935 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8925 | 0.9965 | 0.92 | 1.05 | 8718 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+56 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_6DOW_COGEN% ID 4 |  | Facility: Radial
204936 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8924 | 0.9965 | 0.92 | 1.05 | 8719 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+57 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_6DOW_COGEN% ID 5 |  | Facility: Radial
204937 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8925 | 0.9965 | 0.92 | 1.05 | 8720 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+58 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_6DOW_COGEN% ID 6 |  | Facility: Radial
204938 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8922 | 0.9965 | 0.92 | 1.05 | 8722 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+60 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1CARVLE_C2! ID 1 |  | Facility: Radial
204939 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8969 | 0.9965 | 0.92 | 1.05 | 8732 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+70 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
204940 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8919 | 0.9965 | 0.92 | 1.05 | 8744 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+82 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1NMIL U4! ID 1 |  | Facility: Radial
204941 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8919 | 0.9965 | 0.92 | 1.05 | 8745 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+83 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1NMIL U5! ID 1 |  | Facility: Radial
204942 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8928 | 0.9965 | 0.92 | 1.05 | 8794 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+132 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ANO U1 ID 1 |  | Facility: Radial
204943 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8928 | 0.9965 | 0.92 | 1.05 | 8795 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+133 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ANO U2 ID 1 |  | Facility: Radial
204944 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.8925 | 0.9965 | 0.92 | 1.05 | 8844 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+182 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HOUMA 3 ID 1 |  | Facility: Radial
204945 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0506 | 1.037 | 0.92 | 1.05 | 9208 | G_1G1SABIN! ID 1+P1_2-234_2PANSY!,2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1G1SABIN! ID 1 |  | VH
204946 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0506 | 1.037 | 0.92 | 1.05 | 9217 | G_1G2SABIN! ID 1+P1_2-234_2PANSY!,2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1G2SABIN! ID 1 |  | VH
204947 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0519 | 1.037 | 0.92 | 1.05 | 9228 | G_1G3SABIN! ID 1+P1_2-234_2PANSY!,2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1G3SABIN! ID 1 |  | VH
204948 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0501 | 1.037 | 0.92 | 1.05 | 9354 | G_1NELSON_G4! ID 1+P1_2-234_2PANSY!,2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1NELSON_G4! ID 1 |  | VH
204949 | 18W | Approved | P3 | 32 | 2HIMEX | VH |  |  |  |  | 1.0504 | 1.037 | 0.92 | 1.05 | 9392 | G_1NELSON_G6! ID 1+P1_2-234_2PANSY!,2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1NELSON_G6! ID 1 |  | VH
204950 | 18W | Approved | P3 | 32 | 3ASHLAND | VH |  |  |  |  | 1.0898 | 1.0073 | 0.92 | 1.05 | 12181 | G_1WAT U3! ID 1+P1_2-803_3COTEAU!,3HOUMA! | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
204951 | 18W | Approved | P3 | 32 | 3HOUMA! | VH |  |  |  |  | 1.0998 | 1.0113 | 0.92 | 1.05 | 12181 | G_1WAT U3! ID 1+P1_2-803_3COTEAU!,3HOUMA! | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
204952 | 18W | Approved | P3 | 32 | 3CHAVIN! | VH |  |  |  |  | 1.0733 | 1.0048 | 0.92 | 1.05 | 12181 | G_1WAT U3! ID 1+P1_2-803_3COTEAU!,3HOUMA! | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
204953 | 18W | Approved | P3 | 32 | HOUMA 3 | VH |  |  |  |  | 1.0998 | 1.0113 | 0.92 | 1.05 | 12181 | G_1WAT U3! ID 1+P1_2-803_3COTEAU!,3HOUMA! | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
204954 | 18W | Approved | P3 | 32 | 8GGNS% | VL |  |  |  |  | 0.981 | 1.0173 | 0.982 | 1.05 | 12405 | G_1WAT U3! ID 1+P1_2-1033_8GGNS%,8BXTRWILSON% | 336820 |  |  |  | 500 | 500 | 326 | EES-EMI |  |  | P1_2-1033_8GGNS%,8BXTRWILSON% | G_1WAT U3! ID 1 |  | Delta: No worse than P0
204955 | 18W | Approved | P3 | 32 | MANDEV 6 | VL |  |  |  |  | 0.9172 | 0.9622 | 0.92 | 1.05 | 13787 | G_1MICH U3! ID 1+P1_2-1686_MADISON6!,MANDEV 6! | 500520 |  |  |  | 230 | 230 | 502 | CLEC |  |  | P1_2-1686_MADISON6!,MANDEV 6! | G_1MICH U3! ID 1 | None
204956 | 18W | Approved | P3 | 32 | 3MCCALL! | VH |  |  |  |  | 1.0562 | 0.9918 | 0.92 | 1.05 | 14585 | G_1GGNS U1 ID 1+P1_2-794_3PVILLE!,3RACLND! | 336016 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-794_3PVILLE!,3RACLND! | G_1GGNS U1 ID 1 |  | VH
204957 | 18W | Approved | P3 | 32 | 3PVILLE! | VH |  |  |  |  | 1.0593 | 0.981 | 0.92 | 1.05 | 14585 | G_1GGNS U1 ID 1+P1_2-794_3PVILLE!,3RACLND! | 336017 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-794_3PVILLE!,3RACLND! | G_1GGNS U1 ID 1 |  | VH
204958 | 18W | Approved | P3 | 32 | ELKS 6 | VL |  |  |  |  | 0.9197 | 0.9965 | 0.92 | 1.05 | 15662 | G_1GGNS U1 ID 1+2117 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_1GGNS U1 ID 1 | turn on switch shunt at BEADLE 230kV sub
204959 | 18W | Approved | P3 | 32 | 2BLACK ROCK | VH |  |  |  |  | 1.0582 | 1.0296 | 0.92 | 1.05 | 16314 | G_1ISES U1 ID 1+P1_2-38_5WPLAIN!,5KOSH! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ISES U1 ID 1 |  | VH
204960 | 18W | Approved | P3 | 32 | 2BLACK ROCK | VH |  |  |  |  | 1.0583 | 1.0296 | 0.92 | 1.05 | 16335 | G_1ISES U1 ID 1+P1_2-59_5KOSH!,5COXCRK% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ISES U1 ID 1 |  | VH
204961 | 18W | Approved | P3 | 32 | 2BLACK ROCK | VH |  |  |  |  | 1.0539 | 1.0296 | 0.92 | 1.05 | 18167 | G_1ISES U2 ID 1+P1_2-38_5WPLAIN!,5KOSH! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ISES U2 ID 1 |  | VH
204962 | 18W | Approved | P3 | 32 | 2BLACK ROCK | VH |  |  |  |  | 1.0541 | 1.0296 | 0.92 | 1.05 | 18188 | G_1ISES U2 ID 1+P1_2-59_5KOSH!,5COXCRK% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ISES U2 ID 1 |  | VH
204963 | 18W | Approved | P3 | 32 | 8ISES-XF | VH |  |  |  |  | 1.0545 | 1.0295 | 0.92 | 1.05 | 19546 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
204964 | 18W | Approved | P3 | 32 | 8ISES% | VH |  |  |  |  | 1.0546 | 1.0296 | 0.92 | 1.05 | 19546 | G_1ISES U2 ID 1+P1_2-1442_8KEO%,8HOLND BTM% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
204965 | 18W | Approved | P3 | 32 | 8ISES-XF | VH |  |  |  |  | 1.0509 | 1.0295 | 0.92 | 1.05 | 19588 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%,8ISES% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%,8ISES% | G_1ISES U2 ID 1 |  | VH
204966 | 18W | Approved | P3 | 32 | 8ISES% | VH |  |  |  |  | 1.051 | 1.0296 | 0.92 | 1.05 | 19588 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%,8ISES% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%,8ISES% | G_1ISES U2 ID 1 |  | VH
204967 | 18W | Approved | P3 | 32 | 8ISES% | VH |  |  |  |  | 1.0512 | 1.0296 | 0.92 | 1.05 | 19589 | G_1ISES U2 ID 1+P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U2 ID 1 |  | VH
204968 | 18W | Approved | P3 | 32 | 2MCCLELLAN | VH |  |  |  |  | 1.0564 | 1.0256 | 0.92 | 1.05 | 20024 | G_1MCCLELAN U1 ID 1+P1_2-1274_3CAMDEN.N!,3FORDYCE! | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1274_3CAMDEN.N!,3FORDYCE! | G_1MCCLELAN U1 ID 1 |  | VH
204969 | 18L | Approved | P0 | 33 | 8GPDELL | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 |  | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
204970 | 18L | Approved | P0 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0512 | 1.0512 | 0.92 | 1.05 |  | ** Base Case ** | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
204971 | 18L | Approved | P0 | 33 | 2BATSON! | VH |  |  |  |  | 1.0536 | 1.0536 | 0.92 | 1.05 |  | ** Base Case ** | 334255 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
204972 | 18L | Approved | P0 | 33 | 26L102TAP | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 |  | ** Base Case ** | 334256 |  |  |  | 69 | 69 | 351 | EES |  |  | ** Base Case ** |  |  | VH
204973 | 18L | Approved | P0 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0667 | 1.0667 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
204974 | 18L | Approved | P0 | 33 | 8DELL% | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 |  | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204975 | 18L | Approved | P0 | 33 | 8SANS SOUCI% | VH |  |  |  |  | 1.0614 | 1.0614 | 0.92 | 1.05 |  | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204976 | 18L | Approved | P0 | 33 | 3PARAGOULD! | VH |  |  |  |  | 1.0589 | 1.0589 | 0.92 | 1.05 |  | ** Base Case ** | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204977 | 18L | Approved | P0 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0691 | 1.0691 | 0.92 | 1.05 |  | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204978 | 18L | Approved | P0 | 33 | 2OPPELLO | VH |  |  |  |  | 1.0526 | 1.0526 | 0.92 | 1.05 |  | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204979 | 18L | Approved | P0 | 33 | 5DELL# | VH |  |  |  |  | 1.0553 | 1.0553 | 0.92 | 1.05 |  | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204980 | 18L | Approved | P0 | 33 | 3LIGHT# | VH |  |  |  |  | 1.0517 | 1.0517 | 0.92 | 1.05 |  | ** Base Case ** | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204981 | 18L | Approved | P0 | 33 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0549 | 1.0549 | 0.92 | 1.05 |  | ** Base Case ** | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
204982 | 18L | Approved | P0 | 33 | 8SHAWNEE FP | VH |  |  |  |  | 1.0839 | 1.0839 | 0.92 | 1.05 |  | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204983 | 18L | Approved | P0 | 33 | 7SHAWNEE FP | VH |  |  |  |  | 1.0765 | 1.0765 | 0.92 | 1.05 |  | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204984 | 18L | Approved | P0 | 33 | 8RUTHERFORD | VH |  |  |  |  | 1.0685 | 1.0685 | 0.92 | 1.05 |  | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204985 | 18L | Approved | P0 | 33 | 8MARSHALL KY | VH |  |  |  |  | 1.0817 | 1.0817 | 0.92 | 1.05 |  | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204986 | 18L | Approved | P0 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0777 | 1.0777 | 0.92 | 1.05 |  | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204987 | 18L | Approved | P0 | 33 | 8JACKSON TN | VH |  |  |  |  | 1.0665 | 1.0665 | 0.92 | 1.05 |  | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204988 | 18L | Approved | P0 | 33 | 8SHELBY TN | VH |  |  |  |  | 1.0602 | 1.0602 | 0.92 | 1.05 |  | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204989 | 18L | Approved | P0 | 33 | 8CORDOVA TN | VH |  |  |  |  | 1.0556 | 1.0556 | 0.92 | 1.05 |  | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204990 | 18L | Approved | P0 | 33 | 8JVILLE FP | VH |  |  |  |  | 1.0824 | 1.0824 | 0.92 | 1.05 |  | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204991 | 18L | Approved | P0 | 33 | 8CUMBERLAND | VH |  |  |  |  | 1.0873 | 1.0873 | 0.92 | 1.05 |  | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204992 | 18L | Approved | P0 | 33 | 8PARADISE FP | VH |  |  |  |  | 1.0869 | 1.0869 | 0.92 | 1.05 |  | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204993 | 18L | Approved | P0 | 33 | 8MONTGOMERY | VH |  |  |  |  | 1.0805 | 1.0805 | 0.92 | 1.05 |  | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204994 | 18L | Approved | P0 | 33 | 8DAVIDSON TN | VH |  |  |  |  | 1.0796 | 1.0796 | 0.92 | 1.05 |  | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204995 | 18L | Approved | P0 | 33 | 8MAURY TN | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 |  | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204996 | 18L | Approved | P0 | 33 | 8FRANKLIN TN | VH |  |  |  |  | 1.0522 | 1.0522 | 0.92 | 1.05 |  | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204997 | 18L | Approved | P0 | 33 | 8WILSON TN | VH |  |  |  |  | 1.0767 | 1.0767 | 0.92 | 1.05 |  | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204998 | 18L | Approved | P0 | 33 | 8PLATEAU TN | VH |  |  |  |  | 1.0611 | 1.0611 | 0.92 | 1.05 |  | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
204999 | 18L | Approved | P0 | 33 | 8BULL RUN FP | VH |  |  |  |  | 1.0509 | 1.0509 | 0.92 | 1.05 |  | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205000 | 18L | Approved | P0 | 33 | 8VOLUNTEER | VH |  |  |  |  | 1.0562 | 1.0562 | 0.92 | 1.05 |  | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205001 | 18L | Approved | P0 | 33 | 8PHIPPS B NP | VH |  |  |  |  | 1.0674 | 1.0674 | 0.92 | 1.05 |  | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205002 | 18L | Approved | P0 | 33 | 8SULLIVAN TN | VH |  |  |  |  | 1.0608 | 1.0608 | 0.92 | 1.05 |  | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205003 | 18L | Approved | P0 | 33 | 8PLEASANT HL | VH |  |  |  |  | 1.0524 | 1.0524 | 0.92 | 1.05 |  | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205004 | 18L | Approved | P0 | 33 | 8HAYWOOD TN | VH |  |  |  |  | 1.0647 | 1.0647 | 0.92 | 1.05 |  | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205005 | 18L | Approved | P0 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 |  | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205006 | 18L | Approved | P0 | 33 | 8PIN HOOK TN | VH |  |  |  |  | 1.0775 | 1.0775 | 0.92 | 1.05 |  | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205007 | 18L | Approved | P0 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0802 | 1.0802 | 0.92 | 1.05 |  | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205008 | 18L | Approved | P0 | 33 | 8BENTON MS | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 |  | ** Base Case ** | 360612 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205009 | 18L | Approved | P0 | 33 | 8MAGNOL CC1 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 |  | ** Base Case ** | 360613 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205010 | 18L | Approved | P0 | 33 | 8MAGNOL CC2 | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 |  | ** Base Case ** | 360614 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205011 | 18L | Approved | P0 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0715 | 1.0715 | 0.92 | 1.05 |  | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
205012 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0617 | 1.0455 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205013 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0615 | 1.046 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205014 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.0608 | 1.0368 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205015 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0658 | 1.047 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205016 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0656 | 1.0512 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205017 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0617 | 1.0455 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205018 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0608 | 1.0369 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205019 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0579 | 1.0691 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1NM G1 ID 1 |  | VH
205020 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0548 | 1.0667 | 0.92 | 1.05 | 110 | P1_2-1_1NM G2, 7NEWMAD%+G_1ANO U1 ID 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ANO U1 ID 1 |  | VH
205021 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0546 | 1.0667 | 0.92 | 1.05 | 111 | P1_2-1_1NM G2, 7NEWMAD%+G_1ANO U2 ID 1 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ANO U2 ID 1 |  | VH
205022 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0598 | 1.0455 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205023 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0569 | 1.046 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205024 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.0552 | 1.0368 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205025 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0614 | 1.047 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205026 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0622 | 1.0512 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205027 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0597 | 1.0455 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205028 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0553 | 1.0369 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205029 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0581 | 1.0439 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205030 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0581 | 1.0439 | 0.92 | 1.05 | 113 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1ISES U2 ID 1 |  | VH
205031 | 18L | Approved | P3 | 33 | 8SANS SOUCI% | VH |  |  |  |  | 1.05 | 1.0614 | 0.92 | 1.05 | 114 | P1_2-1_1NM G2, 7NEWMAD%+G_1PLUM PT U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1PLUM PT U1 ID 1 |  | VH
205032 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205033 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205034 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205035 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205036 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205037 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205038 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205039 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 124 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 1 |  | VH
205040 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205041 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205042 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205043 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205044 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205045 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205046 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205047 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 125 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C1 ID 2 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C1 ID 2 |  | VH
205048 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205049 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205050 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205051 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205052 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205053 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205054 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205055 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 126 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 1 |  | VH
205056 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205057 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205058 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205059 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205060 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205061 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205062 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205063 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 127 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C3 ID 2 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C3 ID 2 |  | VH
205064 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205065 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205066 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205067 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205068 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205069 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205070 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205071 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 128 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 1 |  | VH
205072 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205073 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205074 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.056 | 1.0368 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205075 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.062 | 1.047 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205076 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205077 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0596 | 1.0455 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205078 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.056 | 1.0369 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205079 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 129 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C5 ID 2 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C5 ID 2 |  | VH
205080 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0598 | 1.0455 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205081 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205082 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.0561 | 1.0368 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205083 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0621 | 1.047 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205084 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0628 | 1.0512 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205085 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0597 | 1.0455 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205086 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0561 | 1.0369 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205087 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0591 | 1.0691 | 0.92 | 1.05 | 130 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S1 ID 1 |  | VH
205088 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0575 | 1.0455 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205089 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0565 | 1.046 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205090 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.054 | 1.0368 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205091 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0604 | 1.047 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205092 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0613 | 1.0512 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205093 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0574 | 1.0455 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205094 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0541 | 1.0369 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205095 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0571 | 1.0691 | 0.92 | 1.05 | 131 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS C7 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS C7 ID 1 |  | VH
205096 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0597 | 1.0455 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205097 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.058 | 1.046 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205098 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.0561 | 1.0368 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205099 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0621 | 1.047 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205100 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0628 | 1.0512 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205101 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0597 | 1.0455 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205102 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0561 | 1.0369 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205103 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0591 | 1.0691 | 0.92 | 1.05 | 132 | P1_2-1_1NM G2, 7NEWMAD%+G_1WRIGHTS S2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_1WRIGHTS S2 ID 1 |  | VH
205104 | 18L | Approved | P3 | 33 | 8NEWMAD | VH |  |  |  |  | 1.0593 | 1.0455 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205105 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0577 | 1.046 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205106 | 18L | Approved | P3 | 33 | 7NEWMAD | VH |  |  |  |  | 1.0557 | 1.0368 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205107 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0619 | 1.047 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205108 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0627 | 1.0512 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205109 | 18L | Approved | P3 | 33 | 8WNEWMADRID | VH |  |  |  |  | 1.0592 | 1.0455 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205110 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0557 | 1.0369 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205111 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0583 | 1.0691 | 0.92 | 1.05 | 158 | P1_2-1_1NM G2, 7NEWMAD%+G_JTEC GEN#2 1 ID 2 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2,7NEWMAD% | G_JTEC GEN#2 1 ID 2 |  | VH
205112 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0699 | 1.047 | 0.92 | 1.05 | 268 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U1 ID 1 |  | VH
205113 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0679 | 1.0512 | 0.92 | 1.05 | 268 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U1 ID 1 |  | VH
205114 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0556 | 1.0691 | 0.92 | 1.05 | 268 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U1 ID 1 |  | VH
205115 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0695 | 1.047 | 0.92 | 1.05 | 269 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U2 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U2 ID 1 |  | VH
205116 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0675 | 1.0512 | 0.92 | 1.05 | 269 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U2 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U2 ID 1 |  | VH
205117 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0552 | 1.0691 | 0.92 | 1.05 | 269 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_1ANO U2 ID 1 |  | VH
205118 | 18L | Approved | P3 | 33 | 7FLETCH | VH |  |  |  |  | 1.0573 | 1.0468 | 0.92 | 1.05 | 308 | P1_2-7_7NEWMAD%, 7STFRAN!+G_NFK #1 1 ID 1 | 300040 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_NFK #1 1 ID 1 |  | VH
205119 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0749 | 1.047 | 0.92 | 1.05 | 308 | P1_2-7_7NEWMAD%, 7STFRAN!+G_NFK #1 1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_NFK #1 1 ID 1 |  | VH
205120 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0729 | 1.0512 | 0.92 | 1.05 | 308 | P1_2-7_7NEWMAD%, 7STFRAN!+G_NFK #1 1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_NFK #1 1 ID 1 |  | VH
205121 | 18L | Approved | P3 | 33 | 7FLETCH | VH |  |  |  |  | 1.0573 | 1.0468 | 0.92 | 1.05 | 316 | P1_2-7_7NEWMAD%, 7STFRAN!+G_JTEC GEN#2 1 ID 2 | 300040 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_JTEC GEN#2 1 ID 2 |  | VH
205122 | 18L | Approved | P3 | 33 | 7STFRAN | VH |  |  |  |  | 1.0745 | 1.047 | 0.92 | 1.05 | 316 | P1_2-7_7NEWMAD%, 7STFRAN!+G_JTEC GEN#2 1 ID 2 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_JTEC GEN#2 1 ID 2 |  | VH
205123 | 18L | Approved | P3 | 33 | 7GOBKNOB | VH |  |  |  |  | 1.0726 | 1.0512 | 0.92 | 1.05 | 316 | P1_2-7_7NEWMAD%, 7STFRAN!+G_JTEC GEN#2 1 ID 2 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%,7STFRAN! | G_JTEC GEN#2 1 ID 2 |  | VH
205124 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 317 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1NM G1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1NM G1 ID 1 |  | VH
205125 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.054 | 1.0369 | 0.92 | 1.05 | 317 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1NM G1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1NM G1 ID 1 |  | VH
205126 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 424 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WHT BLUF U1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WHT BLUF U1 ID 1 |  | VH
205127 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0546 | 1.0369 | 0.92 | 1.05 | 424 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WHT BLUF U1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WHT BLUF U1 ID 1 |  | VH
205128 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 425 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WHT BLUF U2 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WHT BLUF U2 ID 1 |  | VH
205129 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0545 | 1.0369 | 0.92 | 1.05 | 425 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WHT BLUF U2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WHT BLUF U2 ID 1 |  | VH
205130 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0522 | 1.0369 | 0.92 | 1.05 | 426 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ANO U1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1ANO U1 ID 1 |  | VH
205131 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0691 | 0.92 | 1.05 | 426 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1ANO U1 ID 1 |  | VH
205132 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0519 | 1.0369 | 0.92 | 1.05 | 427 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ANO U2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1ANO U2 ID 1 |  | VH
205133 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0508 | 1.0691 | 0.92 | 1.05 | 427 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1ANO U2 ID 1 |  | VH
205134 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 446 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS S1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS S1 ID 1 |  | VH
205135 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0544 | 1.0369 | 0.92 | 1.05 | 446 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS S1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS S1 ID 1 |  | VH
205136 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 447 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS C7 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS C7 ID 1 |  | VH
205137 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0545 | 1.0369 | 0.92 | 1.05 | 447 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS C7 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS C7 ID 1 |  | VH
205138 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 448 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS S2 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS S2 ID 1 |  | VH
205139 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0544 | 1.0369 | 0.92 | 1.05 | 448 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1WRIGHTS S2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_1WRIGHTS S2 ID 1 |  | VH
205140 | 18L | Approved | P3 | 33 | 7ESSEX | VH |  |  |  |  | 1.0563 | 1.046 | 0.92 | 1.05 | 466 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_NFK #1 1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_NFK #1 1 ID 1 |  | VH
205141 | 18L | Approved | P3 | 33 | 7WNEWMADRID | VH |  |  |  |  | 1.0544 | 1.0369 | 0.92 | 1.05 | 466 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_NFK #1 1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%,7WNEWMADRID | G_NFK #1 1 ID 1 |  | VH
205142 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0578 | 1.0691 | 0.92 | 1.05 | 584 | P1_2-38_5WPLAIN!, 5KOSH!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ANO U1 ID 1 |  | VH
205143 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0562 | 1.0691 | 0.92 | 1.05 | 585 | P1_2-38_5WPLAIN!, 5KOSH!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!,5KOSH! | G_1ANO U2 ID 1 |  | VH
205144 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0572 | 1.0691 | 0.92 | 1.05 | 742 | P1_2-59_5KOSH!, 5COXCRK%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ANO U1 ID 1 |  | VH
205145 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0554 | 1.0691 | 0.92 | 1.05 | 743 | P1_2-59_5KOSH!, 5COXCRK%+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!,5COXCRK% | G_1ANO U2 ID 1 |  | VH
205146 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 1049 | P1_2-211_4JACINTO%, 4PELCNRD!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-211_4JACINTO%,4PELCNRD! | G_1ANO U1 ID 1 |  | VH
205147 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0585 | 1.0418 | 0.92 | 1.05 | 1267 | P1_2-220_4STOWELL!, 4BIGHILL!+G_1G1LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! | G_1G1LEWIS! ID 1 |  | VH
205148 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0585 | 1.0418 | 0.92 | 1.05 | 1268 | P1_2-220_4STOWELL!, 4BIGHILL!+G_1G2LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! | G_1G2LEWIS! ID 1 |  | VH
205149 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0571 | 1.0418 | 0.92 | 1.05 | 1270 | P1_2-220_4STOWELL!, 4BIGHILL!+G_1PELCNRD U1! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! | G_1PELCNRD U1! ID 1 |  | VH
205150 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0571 | 1.0418 | 0.92 | 1.05 | 1271 | P1_2-220_4STOWELL!, 4BIGHILL!+G_1PELCNRD U2! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-220_4STOWELL!,4BIGHILL! | G_1PELCNRD U2! ID 1 |  | VH
205151 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0646 | 1.0418 | 0.92 | 1.05 | 1434 | P1_2-221_4STOWELL!, 2STOWELL!+G_1G4SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! | G_1G4SABIN! ID 1 |  | VH
205152 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 1518 | P1_2-221_4STOWELL!, 2STOWELL!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-221_4STOWELL!,2STOWELL! | G_1ANO U1 ID 1 |  | VH
205153 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0561 | 1.0418 | 0.92 | 1.05 | 1581 | P1_2-222_4STOWELL!, 2STOWELL!+G_1G1LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1G1LEWIS! ID 1 |  | VH
205154 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0562 | 1.0418 | 0.92 | 1.05 | 1582 | P1_2-222_4STOWELL!, 2STOWELL!+G_1G2LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1G2LEWIS! ID 1 |  | VH
205155 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0556 | 1.0418 | 0.92 | 1.05 | 1584 | P1_2-222_4STOWELL!, 2STOWELL!+G_1PELCNRD U1! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1PELCNRD U1! ID 1 |  | VH
205156 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0556 | 1.0418 | 0.92 | 1.05 | 1585 | P1_2-222_4STOWELL!, 2STOWELL!+G_1PELCNRD U2! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1PELCNRD U2! ID 1 |  | VH
205157 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0546 | 1.0418 | 0.92 | 1.05 | 1674 | P1_2-222_4STOWELL!, 2STOWELL!+G_1ANO U1 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1ANO U1 ID 1 |  | VH
205158 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 1674 | P1_2-222_4STOWELL!, 2STOWELL!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-222_4STOWELL!,2STOWELL! | G_1ANO U1 ID 1 |  | VH
205159 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0582 | 1.0418 | 0.92 | 1.05 | 1737 | P1_2-223_4BIGHILL!, 4MEMORIL!+G_1G1LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G1LEWIS! ID 1 |  | VH
205160 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0582 | 1.0418 | 0.92 | 1.05 | 1738 | P1_2-223_4BIGHILL!, 4MEMORIL!+G_1G2LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_4BIGHILL!,4MEMORIL! | G_1G2LEWIS! ID 1 |  | VH
205161 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0621 | 1.0418 | 0.92 | 1.05 | 1893 | P1_2-229_2STOWELL!, 2WINSHIR!+G_1G1LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! | G_1G1LEWIS! ID 1 |  | VH
205162 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0621 | 1.0418 | 0.92 | 1.05 | 1894 | P1_2-229_2STOWELL!, 2WINSHIR!+G_1G2LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! | G_1G2LEWIS! ID 1 |  | VH
205163 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0596 | 1.0418 | 0.92 | 1.05 | 1987 | P1_2-229_2STOWELL!, 2WINSHIR!+G_1ANO U1 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-229_2STOWELL!,2WINSHIR! | G_1ANO U1 ID 1 |  | VH
205164 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 1987 | P1_2-229_2STOWELL!, 2WINSHIR!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-229_2STOWELL!,2WINSHIR! | G_1ANO U1 ID 1 |  | VH
205165 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0587 | 1.0418 | 0.92 | 1.05 | 2050 | P1_2-233_2WINSHIR!, 2PANSY!+G_1G1LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G1LEWIS! ID 1 |  | VH
205166 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0587 | 1.0418 | 0.92 | 1.05 | 2051 | P1_2-233_2WINSHIR!, 2PANSY!+G_1G2LEWIS! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1G2LEWIS! ID 1 |  | VH
205167 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0562 | 1.0418 | 0.92 | 1.05 | 2144 | P1_2-233_2WINSHIR!, 2PANSY!+G_1ANO U1 ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1ANO U1 ID 1 |  | VH
205168 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2144 | P1_2-233_2WINSHIR!, 2PANSY!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-233_2WINSHIR!,2PANSY! | G_1ANO U1 ID 1 |  | VH
205169 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2296 | P1_2-278_6HELBIG!, 6GEOTOWN!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-278_6HELBIG!,6GEOTOWN! | G_1ANO U1 ID 1 |  | VH
205170 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0537 | 1.0213 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205171 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0575 | 1.0143 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205172 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0601 | 1.0101 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205173 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0561 | 1.0058 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205174 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0557 | 1.0054 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205175 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0561 | 1.0058 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205176 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2454 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-758_2PORT_HUD_A!,2JACKSON! | G_1ANO U1 ID 1 |  | VH
205177 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.0824 | 1.0221 | 0.92 | 1.05 | 2562 | P1_2-803_3COTEAU!, 3HOUMA!+G_1RVR_BND_G1! ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1RVR_BND_G1! ID 1 |  | VH
205178 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2562 | P1_2-803_3COTEAU!, 3HOUMA!+G_1RVR_BND_G1! ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1RVR_BND_G1! ID 1 |  | VH
205179 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0557 | 1.0174 | 0.92 | 1.05 | 2562 | P1_2-803_3COTEAU!, 3HOUMA!+G_1RVR_BND_G1! ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1RVR_BND_G1! ID 1 |  | VH
205180 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2562 | P1_2-803_3COTEAU!, 3HOUMA!+G_1RVR_BND_G1! ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1RVR_BND_G1! ID 1 |  | VH
205181 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.082 | 1.0221 | 0.92 | 1.05 | 2565 | P1_2-803_3COTEAU!, 3HOUMA!+G_1WAT U3! ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
205182 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0941 | 1.0257 | 0.92 | 1.05 | 2565 | P1_2-803_3COTEAU!, 3HOUMA!+G_1WAT U3! ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
205183 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0553 | 1.0174 | 0.92 | 1.05 | 2565 | P1_2-803_3COTEAU!, 3HOUMA!+G_1WAT U3! ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
205184 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0941 | 1.0257 | 0.92 | 1.05 | 2565 | P1_2-803_3COTEAU!, 3HOUMA!+G_1WAT U3! ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1WAT U3! ID 1 |  | VH
205185 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.0824 | 1.0221 | 0.92 | 1.05 | 2585 | P1_2-803_3COTEAU!, 3HOUMA!+G_1GGNS U1 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | VH
205186 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2585 | P1_2-803_3COTEAU!, 3HOUMA!+G_1GGNS U1 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | VH
205187 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0557 | 1.0174 | 0.92 | 1.05 | 2585 | P1_2-803_3COTEAU!, 3HOUMA!+G_1GGNS U1 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | VH
205188 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2585 | P1_2-803_3COTEAU!, 3HOUMA!+G_1GGNS U1 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1GGNS U1 ID 1 |  | VH
205189 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.0824 | 1.0221 | 0.92 | 1.05 | 2612 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U1 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U1 ID 1 |  | VH
205190 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2612 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U1 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U1 ID 1 |  | VH
205191 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0557 | 1.0174 | 0.92 | 1.05 | 2612 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U1 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U1 ID 1 |  | VH
205192 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2612 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U1 ID 1 |  | VH
205193 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2612 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U1 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U1 ID 1 |  | VH
205194 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.0824 | 1.0221 | 0.92 | 1.05 | 2613 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U2 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U2 ID 1 |  | VH
205195 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2613 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U2 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U2 ID 1 |  | VH
205196 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0557 | 1.0174 | 0.92 | 1.05 | 2613 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U2 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U2 ID 1 |  | VH
205197 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2613 | P1_2-803_3COTEAU!, 3HOUMA!+G_1ANO U2 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1ANO U2 ID 1 |  | VH
205198 | 18L | Approved | P3 | 33 | 3ASHLAND | VH |  |  |  |  | 1.0824 | 1.0221 | 0.92 | 1.05 | 2635 | P1_2-803_3COTEAU!, 3HOUMA!+G_1CAL G1 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1CAL G1 ID 1 |  | VH
205199 | 18L | Approved | P3 | 33 | 3HOUMA! | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2635 | P1_2-803_3COTEAU!, 3HOUMA!+G_1CAL G1 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1CAL G1 ID 1 |  | VH
205200 | 18L | Approved | P3 | 33 | 3CHAVIN! | VH |  |  |  |  | 1.0557 | 1.0174 | 0.92 | 1.05 | 2635 | P1_2-803_3COTEAU!, 3HOUMA!+G_1CAL G1 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1CAL G1 ID 1 |  | VH
205201 | 18L | Approved | P3 | 33 | HOUMA 3 | VH |  |  |  |  | 1.0945 | 1.0257 | 0.92 | 1.05 | 2635 | P1_2-803_3COTEAU!, 3HOUMA!+G_1CAL G1 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-803_3COTEAU!,3HOUMA! | G_1CAL G1 ID 1 |  | VH
205202 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2660 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1SLSBAU3 ID 5 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1SLSBAU3 ID 5 |  | VH
205203 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2660 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1SLSBAU3 ID 5 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1SLSBAU3 ID 5 |  | VH
205204 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2660 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1SLSBAU3 ID 5 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1SLSBAU3 ID 5 |  | VH
205205 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2661 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1WHT BLUF U1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1WHT BLUF U1 ID 1 |  | VH
205206 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2661 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1WHT BLUF U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1WHT BLUF U1 ID 1 |  | VH
205207 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2661 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1WHT BLUF U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1WHT BLUF U1 ID 1 |  | VH
205208 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2662 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1PERRYV_C1! ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1PERRYV_C1! ID 1 |  | VH
205209 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2662 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1PERRYV_C1! ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1PERRYV_C1! ID 1 |  | VH
205210 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2662 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1PERRYV_C1! ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1PERRYV_C1! ID 1 |  | VH
205211 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2663 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U1 ID 1 |  | VH
205212 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2663 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U1 ID 1 |  | VH
205213 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2663 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U1 ID 1 |  | VH
205214 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2664 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U2 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 |  | VH
205215 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2664 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U2 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 |  | VH
205216 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2664 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U2 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 |  | VH
205217 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 2664 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 |  | VH
205218 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 2664 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1ISES U2 ID 1 |  | VH
205219 | 18L | Approved | P3 | 33 | 3GMEADW! | VH |  |  |  |  | 1.122 | 1.0185 | 0.92 | 1.05 | 2665 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1LSPWRU1 ID 1 | 336081 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1LSPWRU1 ID 1 |  | VH
205220 | 18L | Approved | P3 | 33 | 3LEEVLL | VH |  |  |  |  | 1.1428 | 1.0114 | 0.92 | 1.05 | 2665 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1LSPWRU1 ID 1 | 336082 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1LSPWRU1 ID 1 |  | VH
205221 | 18L | Approved | P3 | 33 | 3FOURCHN | VH |  |  |  |  | 1.1418 | 1.0018 | 0.92 | 1.05 | 2665 | P1_2-808_3VLNTIN!, 3GMEADW!+G_1LSPWRU1 ID 1 | 336083 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-808_3VLNTIN!,3GMEADW! | G_1LSPWRU1 ID 1 |  | VH
205222 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2773 | P1_2-986_3NATCHEZSES%, 3PORTGIBSON!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-986_3NATCHEZSES%,3PORTGIBSON! | G_1ANO U1 ID 1 |  | VH
205223 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 2776 | P1_2-986_3NATCHEZSES%, 3PORTGIBSON!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-986_3NATCHEZSES%,3PORTGIBSON! | G_1ISES U2 ID 1 |  | VH
205224 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 2776 | P1_2-986_3NATCHEZSES%, 3PORTGIBSON!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-986_3NATCHEZSES%,3PORTGIBSON! | G_1ISES U2 ID 1 |  | VH
205225 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 2925 | P1_2-1001_3BROOKHAVEN!, 3WYNNDALE%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1001_3BROOKHAVEN!,3WYNNDALE% | G_1ANO U1 ID 1 |  | VH
205226 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 3061 | P1_2-1030_3VICKSBURG!, 3R.BRASWELL%+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1030_3VICKSBURG!,3R.BRASWELL% | G_1ISES U2 ID 1 |  | VH
205227 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 3061 | P1_2-1030_3VICKSBURG!, 3R.BRASWELL%+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1030_3VICKSBURG!,3R.BRASWELL% | G_1ISES U2 ID 1 |  | VH
205228 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 3333 | P1_2-1060_6S.CANTON!, 6PICKENS!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1060_6S.CANTON!,6PICKENS! | G_1ANO U1 ID 1 |  | VH
205229 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 3487 | P1_2-1065_3S.JACKSON!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1065_3S.JACKSON! | G_1ANO U1 ID 1 |  | VH
205230 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 3642 | P1_2-1069_3RANKIN!, 3PELAHTCHIE!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1069_3RANKIN!,3PELAHTCHIE! | G_1ANO U1 ID 1 |  | VH
205231 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 3798 | P1_2-1071_3PELAHTCHIE!, 3FORINDT2!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1071_3PELAHTCHIE!,3FORINDT2! | G_1ANO U1 ID 1 |  | VH
205232 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 3953 | P1_2-1072_3MONUMENT!, 3E.JACKSON!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1072_3MONUMENT!,3E.JACKSON! | G_1ANO U1 ID 1 |  | VH
205233 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0507 | 1.0691 | 0.92 | 1.05 | 4674 | P1_2-1105_8ATTALA!, 8MCADAMS%+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1105_8ATTALA!,8MCADAMS% | G_1ANO U2 ID 1 |  | VH
205234 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0513 | 1.0691 | 0.92 | 1.05 | 5396 | P1_2-1128_6S.GRENADA!, 6TILLATOBA!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1128_6S.GRENADA!,6TILLATOBA! | G_1ANO U1 ID 1 |  | VH
205235 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0509 | 1.0691 | 0.92 | 1.05 | 5397 | P1_2-1128_6S.GRENADA!, 6TILLATOBA!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1128_6S.GRENADA!,6TILLATOBA! | G_1ANO U2 ID 1 |  | VH
205236 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0691 | 0.92 | 1.05 | 5830 | P1_2-1133_3TILLATOBA!, 6TILLATOBA!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1133_3TILLATOBA!,6TILLATOBA! | G_1ANO U1 ID 1 |  | VH
205237 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0501 | 1.0691 | 0.92 | 1.05 | 5987 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+110 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! | G_1ANO U1 ID 1 |  | VH
205238 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0567 | 1.0439 | 0.92 | 1.05 | 5990 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! | G_1ISES U2 ID 1 |  | VH
205239 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0567 | 1.0439 | 0.92 | 1.05 | 5990 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!,3CLARKSDALE! | G_1ISES U2 ID 1 |  | VH
205240 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 6145 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+110 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1ANO U1 ID 1 |  | VH
205241 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 6148 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1ISES U2 ID 1 |  | VH
205242 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 6148 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!,6CROSSROADS! | G_1ISES U2 ID 1 |  | VH
205243 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0574 | 1.0466 | 0.92 | 1.05 | 6292 | P1_2-1140_6CROSSROADS!+G_1WHT BLUF U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1140_6CROSSROADS! | G_1WHT BLUF U1 ID 1 |  | VH
205244 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0572 | 1.0466 | 0.92 | 1.05 | 6293 | P1_2-1140_6CROSSROADS!+G_1WHT BLUF U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1140_6CROSSROADS! | G_1WHT BLUF U2 ID 1 |  | VH
205245 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0574 | 1.0466 | 0.92 | 1.05 | 6434 | P1_2-1141_6CROSSROADS!+G_1WHT BLUF U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1141_6CROSSROADS! | G_1WHT BLUF U1 ID 1 |  | VH
205246 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0572 | 1.0466 | 0.92 | 1.05 | 6435 | P1_2-1141_6CROSSROADS!+G_1WHT BLUF U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1141_6CROSSROADS! | G_1WHT BLUF U2 ID 1 |  | VH
205247 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0514 | 1.0394 | 0.92 | 1.05 | 6585 | P1_2-1142_6CROSSROADS!, 6MOONLAKE%+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1142_6CROSSROADS!,6MOONLAKE% | G_1WHT BLUF U1 ID 1 |  | VH
205248 | 18L | Approved | P3 | 33 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0504 | 1.0401 | 0.92 | 1.05 | 6585 | P1_2-1142_6CROSSROADS!, 6MOONLAKE%+108 | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1142_6CROSSROADS!,6MOONLAKE% | G_1WHT BLUF U1 ID 1 |  | VH
205249 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0593 | 1.0466 | 0.92 | 1.05 | 6585 | P1_2-1142_6CROSSROADS!, 6MOONLAKE%+108 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1142_6CROSSROADS!,6MOONLAKE% | G_1WHT BLUF U1 ID 1 |  | VH
205250 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0503 | 1.0691 | 0.92 | 1.05 | 6587 | P1_2-1142_6CROSSROADS!, 6MOONLAKE%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1142_6CROSSROADS!,6MOONLAKE% | G_1ANO U1 ID 1 |  | VH
205251 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.05 | 1.0691 | 0.92 | 1.05 | 6588 | P1_2-1142_6CROSSROADS!, 6MOONLAKE%+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1142_6CROSSROADS!,6MOONLAKE% | G_1ANO U2 ID 1 |  | VH
205252 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0516 | 1.0394 | 0.92 | 1.05 | 6881 | P1_2-1144_6MOONLAKE%, 6RITCHIE-2!+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%,6RITCHIE-2! | G_1WHT BLUF U1 ID 1 |  | VH
205253 | 18L | Approved | P3 | 33 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0502 | 1.0401 | 0.92 | 1.05 | 6881 | P1_2-1144_6MOONLAKE%, 6RITCHIE-2!+108 | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%,6RITCHIE-2! | G_1WHT BLUF U1 ID 1 |  | VH
205254 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0593 | 1.0466 | 0.92 | 1.05 | 6881 | P1_2-1144_6MOONLAKE%, 6RITCHIE-2!+108 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%,6RITCHIE-2! | G_1WHT BLUF U1 ID 1 |  | VH
205255 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0502 | 1.0691 | 0.92 | 1.05 | 7032 | P1_2-1147_6BATESVILLE!, 5BATESVILLE+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1147_6BATESVILLE!,5BATESVILLE | G_1ANO U1 ID 1 |  | VH
205256 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0567 | 1.0439 | 0.92 | 1.05 | 7034 | P1_2-1147_6BATESVILLE!, 5BATESVILLE+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1147_6BATESVILLE!,5BATESVILLE | G_1ISES U2 ID 1 |  | VH
205257 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0567 | 1.0439 | 0.92 | 1.05 | 7034 | P1_2-1147_6BATESVILLE!, 5BATESVILLE+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1147_6BATESVILLE!,5BATESVILLE | G_1ISES U2 ID 1 |  | VH
205258 | 18L | Approved | P3 | 33 | 3HORN LAKE! | VH |  |  |  |  | 1.0561 | 1.045 | 0.92 | 1.05 | 7187 | P1_2-1152_3GETWELL!, 3HORN LAKE!+108 | 337150 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1152_3GETWELL!,3HORN LAKE! | G_1WHT BLUF U1 ID 1 |  | VH
205259 | 18L | Approved | P3 | 33 | 3DESOTO MS | VH |  |  |  |  | 1.0535 | 1.043 | 0.92 | 1.05 | 7187 | P1_2-1152_3GETWELL!, 3HORN LAKE!+108 | 337151 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1152_3GETWELL!,3HORN LAKE! | G_1WHT BLUF U1 ID 1 |  | VH
205260 | 18L | Approved | P3 | 33 | 3WALLS | VH |  |  |  |  | 1.0509 | 1.0407 | 0.92 | 1.05 | 7497 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+108 | 337152 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1WHT BLUF U1 ID 1 |  | VH
205261 | 18L | Approved | P3 | 33 | 6TUNICA! | VH |  |  |  |  | 1.0538 | 1.0354 | 0.92 | 1.05 | 7497 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+108 | 337160 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1WHT BLUF U1 ID 1 |  | VH
205262 | 18L | Approved | P3 | 33 | 6ROBINSONVL | VH |  |  |  |  | 1.0504 | 1.0375 | 0.92 | 1.05 | 7497 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+108 | 337161 |  |  |  | 230 | 230 | 326 | EES-EMI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1WHT BLUF U1 ID 1 |  | VH
205263 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0551 | 1.0439 | 0.92 | 1.05 | 7500 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
205264 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0551 | 1.0439 | 0.92 | 1.05 | 7500 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
205265 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0589 | 1.0691 | 0.92 | 1.05 | 7500 | P1_2-1160_6TUNICA!, 6RITCHIE-1!+G_1ISES U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1160_6TUNICA!,6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
205266 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205267 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8517 | 1.0234 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205268 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8901 | 1.0237 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205269 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9136 | 1.034 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205270 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9128 | 1.034 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205271 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9126 | 1.0339 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205272 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9108 | 1.0347 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205273 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9079 | 1.0333 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205274 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9059 | 1.0328 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205275 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9045 | 1.0324 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205276 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9011 | 1.0315 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205277 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9155 | 1.032 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205278 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9141 | 1.0307 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205279 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9647 | 1.0362 | 0.975 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205280 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205281 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8898 | 1.0233 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205282 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8971 | 1.0273 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205283 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8972 | 1.0276 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205284 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8994 | 1.034 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205285 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8611 | 1.0252 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205286 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8587 | 1.0247 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205287 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8427 | 1.0244 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205288 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205289 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8971 | 1.0276 | 0.92 | 1.05 | 7546 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+2 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U1% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205290 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205291 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8518 | 1.0234 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205292 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8902 | 1.0237 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205293 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9137 | 1.034 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205294 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9129 | 1.034 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205295 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9127 | 1.0339 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205296 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9109 | 1.0347 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205297 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.908 | 1.0333 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205298 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.906 | 1.0328 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205299 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9046 | 1.0324 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205300 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9012 | 1.0315 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205301 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9157 | 1.032 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205302 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9142 | 1.0307 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205303 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9647 | 1.0362 | 0.975 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205304 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205305 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.89 | 1.0233 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205306 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8972 | 1.0273 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205307 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205308 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8995 | 1.034 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205309 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8612 | 1.0252 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205310 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8588 | 1.0247 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205311 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8428 | 1.0244 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205312 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205313 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7548 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+4 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1BCAJUN2_U3% ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205314 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VH |  |  |  |  | 1.0928 | 0.9963 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205315 | 18L | Approved | P3 | 33 | 3GILBERT | VH |  |  |  |  | 1.229 | 1.0234 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205316 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VH |  |  |  |  | 1.1181 | 1.0237 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205317 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VH |  |  |  |  | 1.1269 | 1.034 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205318 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VH |  |  |  |  | 1.1266 | 1.034 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205319 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VH |  |  |  |  | 1.1265 | 1.0339 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205320 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VH |  |  |  |  | 1.1263 | 1.0347 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205321 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VH |  |  |  |  | 1.1244 | 1.0333 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205322 | 18L | Approved | P3 | 33 | 3INTL PAPER | VH |  |  |  |  | 1.1234 | 1.0328 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205323 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VH |  |  |  |  | 1.1226 | 1.0324 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205324 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VH |  |  |  |  | 1.1208 | 1.0315 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205325 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VH |  |  |  |  | 1.1203 | 1.032 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205326 | 18L | Approved | P3 | 33 | 3CROSBY+ | VH |  |  |  |  | 1.1033 | 1.0276 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336511 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205327 | 18L | Approved | P3 | 33 | 3GLOSTER | VH |  |  |  |  | 1.0984 | 1.0265 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336512 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205328 | 18L | Approved | P3 | 33 | 3LIBERTY P/L | VH |  |  |  |  | 1.0726 | 1.0357 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336513 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205329 | 18L | Approved | P3 | 33 | 3WOODVILLE | VH |  |  |  |  | 1.0788 | 1.0052 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205330 | 18L | Approved | P3 | 33 | 3LIBERTY! | VH |  |  |  |  | 1.0727 | 1.0357 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336515 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205331 | 18L | Approved | P3 | 33 | 3INTRSTE P/L | VH |  |  |  |  | 1.0727 | 1.0357 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336516 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205332 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VH |  |  |  |  | 1.1191 | 1.0307 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205333 | 18L | Approved | P3 | 33 | 3CENTREVILLE | VH |  |  |  |  | 1.0844 | 1.0113 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336520 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205334 | 18L | Approved | P3 | 33 | 3SMITHDALE+ | VH |  |  |  |  | 1.0545 | 1.0354 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336525 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205335 | 18L | Approved | P3 | 33 | 3WASHINGTON+ | VH |  |  |  |  | 1.1187 | 1.0329 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205336 | 18L | Approved | P3 | 33 | 3ROXIE | VH |  |  |  |  | 1.0929 | 1.0323 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336528 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205337 | 18L | Approved | P3 | 33 | 3MEADVILLE | VH |  |  |  |  | 1.0726 | 1.0338 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336529 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205338 | 18L | Approved | P3 | 33 | 3CRANFIELD+ | VH |  |  |  |  | 1.1096 | 1.0322 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336530 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205339 | 18L | Approved | P3 | 33 | 3FAYETTE | VH |  |  |  |  | 1.1168 | 1.0326 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336785 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205340 | 18L | Approved | P3 | 33 | 3LORMAN+ | VH |  |  |  |  | 1.097 | 1.0335 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336786 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205341 | 18L | Approved | P3 | 33 | 3LORMAN | VH |  |  |  |  | 1.0969 | 1.0334 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336787 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205342 | 18L | Approved | P3 | 33 | 3PORTGIBSON! | VH |  |  |  |  | 1.0837 | 1.0373 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336788 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205343 | 18L | Approved | P3 | 33 | 3GGNS | VH |  |  |  |  | 1.0827 | 1.0362 | 0.975 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205344 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VH |  |  |  |  | 1.0928 | 0.9963 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205345 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VH |  |  |  |  | 1.1172 | 1.0233 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205346 | 18L | Approved | P3 | 33 | 3PLANTATION! | VH |  |  |  |  | 1.1125 | 1.0273 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205347 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VH |  |  |  |  | 1.1144 | 1.0276 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205348 | 18L | Approved | P3 | 33 | 3RED_GUM! | VH |  |  |  |  | 1.1386 | 1.034 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205349 | 18L | Approved | P3 | 33 | 3METROPOLIS | VH |  |  |  |  | 1.2169 | 1.0252 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205350 | 18L | Approved | P3 | 33 | 3WISNER | VH |  |  |  |  | 1.2225 | 1.0247 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205351 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VH |  |  |  |  | 1.2444 | 1.0244 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205352 | 18L | Approved | P3 | 33 | JNESVIL3 | VH |  |  |  |  | 1.0928 | 0.9963 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205353 | 18L | Approved | P3 | 33 | VIDALIA3 | VH |  |  |  |  | 1.1144 | 1.0276 | 0.92 | 1.05 | 7604 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+60 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 |  | VH
205354 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8548 | 0.9963 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205355 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8472 | 1.0234 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205356 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8866 | 1.0237 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205357 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.91 | 1.034 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205358 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9092 | 1.034 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205359 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.909 | 1.0339 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205360 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9073 | 1.0347 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205361 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9044 | 1.0333 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205362 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9024 | 1.0328 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205363 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9011 | 1.0324 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205364 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.8977 | 1.0315 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205365 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9123 | 1.032 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205366 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9108 | 1.0307 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205367 | 18L | Approved | P3 | 33 | 3WASHINGTON+ | VL |  |  |  |  | 0.9171 | 1.0329 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205368 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9603 | 1.0362 | 0.975 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205369 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8548 | 0.9963 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205370 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8864 | 1.0233 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205371 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8937 | 1.0273 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205372 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8937 | 1.0276 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205373 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8957 | 1.034 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205374 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8568 | 1.0252 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205375 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8544 | 1.0247 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205376 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8379 | 1.0244 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205377 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8548 | 0.9963 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205378 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8937 | 1.0276 | 0.92 | 1.05 | 7607 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1WAT U3! ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205379 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205380 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8519 | 1.0234 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205381 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8903 | 1.0237 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205382 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9137 | 1.034 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205383 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9129 | 1.034 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205384 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9127 | 1.0339 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205385 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9109 | 1.0347 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205386 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.908 | 1.0333 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205387 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.906 | 1.0328 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205388 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9046 | 1.0324 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205389 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9012 | 1.0315 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205390 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9157 | 1.032 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205391 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9142 | 1.0307 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205392 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9648 | 1.0362 | 0.975 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205393 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205394 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.89 | 1.0233 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205395 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8972 | 1.0273 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205396 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205397 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8995 | 1.034 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205398 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8612 | 1.0252 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205399 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8588 | 1.0247 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205400 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8428 | 1.0244 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205401 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205402 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7611 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1SOXY U1! ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205403 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8583 | 0.9963 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205404 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8519 | 1.0234 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205405 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8903 | 1.0237 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205406 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9137 | 1.034 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205407 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9129 | 1.034 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205408 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9127 | 1.0339 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205409 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.911 | 1.0347 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205410 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.908 | 1.0333 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205411 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.906 | 1.0328 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205412 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9046 | 1.0324 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205413 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9012 | 1.0315 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205414 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9157 | 1.032 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205415 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9142 | 1.0307 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205416 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9649 | 1.0362 | 0.975 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205417 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8584 | 0.9963 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205418 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.89 | 1.0233 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205419 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8973 | 1.0273 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205420 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205421 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8995 | 1.034 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205422 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8612 | 1.0252 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205423 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8588 | 1.0247 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205424 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8428 | 1.0244 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205425 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8584 | 0.9963 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205426 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8973 | 1.0276 | 0.92 | 1.05 | 7622 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1NMIL U4! ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205427 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205428 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8517 | 1.0234 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205429 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8901 | 1.0237 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205430 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9136 | 1.034 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205431 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9128 | 1.034 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205432 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9126 | 1.0339 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205433 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9108 | 1.0347 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205434 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9079 | 1.0333 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205435 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9059 | 1.0328 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205436 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9045 | 1.0324 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205437 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9011 | 1.0315 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205438 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9155 | 1.032 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205439 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.9141 | 1.0307 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205440 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9648 | 1.0362 | 0.975 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205441 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205442 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8899 | 1.0233 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205443 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8971 | 1.0273 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205444 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8972 | 1.0276 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205445 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8994 | 1.034 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205446 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8611 | 1.0252 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205447 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8587 | 1.0247 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205448 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8427 | 1.0244 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205449 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8582 | 0.9963 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205450 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8972 | 1.0276 | 0.92 | 1.05 | 7626 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1MICH U3! ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205451 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8524 | 0.9963 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205452 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8447 | 1.0234 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205453 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8844 | 1.0237 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205454 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9084 | 1.034 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205455 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9075 | 1.034 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205456 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9073 | 1.0339 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205457 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9055 | 1.0347 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205458 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9026 | 1.0333 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205459 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9006 | 1.0328 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205460 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.8991 | 1.0324 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205461 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.8957 | 1.0315 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205462 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9104 | 1.032 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205463 | 18L | Approved | P3 | 33 | 3WOODVILLE | VL |  |  |  |  | 0.9188 | 1.0052 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336514 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205464 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.909 | 1.0307 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205465 | 18L | Approved | P3 | 33 | 3WASHINGTON+ | VL |  |  |  |  | 0.9157 | 1.0329 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336527 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205466 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.963 | 1.0362 | 0.975 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205467 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8524 | 0.9963 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205468 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8841 | 1.0233 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205469 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8915 | 1.0273 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205470 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8916 | 1.0276 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205471 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.8934 | 1.034 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205472 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8543 | 1.0252 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205473 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8519 | 1.0247 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205474 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8354 | 1.0244 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205475 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8524 | 0.9963 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205476 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8916 | 1.0276 | 0.92 | 1.05 | 7627 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1GGNS U1 ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205477 | 18L | Approved | P3 | 33 | 3GILBERT | VH |  |  |  |  | 1.128 | 1.0234 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205478 | 18L | Approved | P3 | 33 | 3RED_GUM! | VH |  |  |  |  | 1.0514 | 1.034 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205479 | 18L | Approved | P3 | 33 | 3METROPOLIS | VH |  |  |  |  | 1.1181 | 1.0252 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205480 | 18L | Approved | P3 | 33 | 3WISNER | VH |  |  |  |  | 1.1229 | 1.0247 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205481 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VH |  |  |  |  | 1.141 | 1.0244 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205482 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 7654 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1ANO U1 ID 1 |  | VH
205483 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8592 | 0.9963 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205484 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8528 | 1.0234 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205485 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8911 | 1.0237 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205486 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9145 | 1.034 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205487 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9137 | 1.034 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205488 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9135 | 1.0339 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205489 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9117 | 1.0347 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205490 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9087 | 1.0333 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205491 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9068 | 1.0328 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205492 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9054 | 1.0324 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205493 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.902 | 1.0315 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205494 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9164 | 1.032 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205495 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.915 | 1.0307 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205496 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9649 | 1.0362 | 0.975 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205497 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8593 | 0.9963 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205498 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8908 | 1.0233 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205499 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8981 | 1.0273 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205500 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8981 | 1.0276 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205501 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.9004 | 1.034 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205502 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8622 | 1.0252 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205503 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8598 | 1.0247 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205504 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8438 | 1.0244 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205505 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8593 | 0.9963 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205506 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8981 | 1.0276 | 0.92 | 1.05 | 7698 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_FLINTCR1 ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_FLINTCR1 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205507 | 18L | Approved | P3 | 33 | 3BLACK_RIV | VL |  |  |  |  | 0.8593 | 0.9963 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205508 | 18L | Approved | P3 | 33 | 3GILBERT | VL |  |  |  |  | 0.8528 | 1.0234 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205509 | 18L | Approved | P3 | 33 | 3PERSIM_MIL | VL |  |  |  |  | 0.8912 | 1.0237 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 303323 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205510 | 18L | Approved | P3 | 33 | 3NATCHEZSES% | VL |  |  |  |  | 0.9145 | 1.034 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336500 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205511 | 18L | Approved | P3 | 33 | 3PINE RIDGE+ | VL |  |  |  |  | 0.9137 | 1.034 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336502 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205512 | 18L | Approved | P3 | 33 | 3PINE RIDGE | VL |  |  |  |  | 0.9135 | 1.0339 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336503 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205513 | 18L | Approved | P3 | 33 | 3NATCHEZ! | VL |  |  |  |  | 0.9117 | 1.0347 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336504 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205514 | 18L | Approved | P3 | 33 | 3J.MANVILLE | VL |  |  |  |  | 0.9088 | 1.0333 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336505 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205515 | 18L | Approved | P3 | 33 | 3INTL PAPER | VL |  |  |  |  | 0.9068 | 1.0328 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336506 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205516 | 18L | Approved | P3 | 33 | 3S.NATCHEZ! | VL |  |  |  |  | 0.9054 | 1.0324 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336507 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205517 | 18L | Approved | P3 | 33 | 3NATCHEZ IND | VL |  |  |  |  | 0.9021 | 1.0315 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336508 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205518 | 18L | Approved | P3 | 33 | 3SE.NATCHEZ+ | VL |  |  |  |  | 0.9165 | 1.032 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336510 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205519 | 18L | Approved | P3 | 33 | 3KINGSTON MS | VL |  |  |  |  | 0.915 | 1.0307 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336519 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205520 | 18L | Approved | P3 | 33 | 3GGNS | VL |  |  |  |  | 0.9649 | 1.0362 | 0.975 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 336789 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205521 | 18L | Approved | P3 | 33 | 3BLACK_RIVER | VL |  |  |  |  | 0.8593 | 0.9963 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205522 | 18L | Approved | P3 | 33 | 3S_FERDAY_TP | VL |  |  |  |  | 0.8909 | 1.0233 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337319 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205523 | 18L | Approved | P3 | 33 | 3PLANTATION! | VL |  |  |  |  | 0.8981 | 1.0273 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337320 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205524 | 18L | Approved | P3 | 33 | 3VIDALIA_LA | VL |  |  |  |  | 0.8982 | 1.0276 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337321 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205525 | 18L | Approved | P3 | 33 | 3RED_GUM! | VL |  |  |  |  | 0.9004 | 1.034 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337327 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205526 | 18L | Approved | P3 | 33 | 3METROPOLIS | VL |  |  |  |  | 0.8622 | 1.0252 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205527 | 18L | Approved | P3 | 33 | 3WISNER | VL |  |  |  |  | 0.8598 | 1.0247 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205528 | 18L | Approved | P3 | 33 | 3WINNSBORO! | VL |  |  |  |  | 0.8438 | 1.0244 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205529 | 18L | Approved | P3 | 33 | JNESVIL3 | VL |  |  |  |  | 0.8593 | 0.9963 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205530 | 18L | Approved | P3 | 33 | VIDALIA3 | VL |  |  |  |  | 0.8981 | 1.0276 | 0.92 | 1.05 | 7701 | P1_2-1181_3WINNSBORO!, 3SWARTZ!+G_MUSKOG4G ID 1 | 503309 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_MUSKOG4G ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
205531 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 7812 | P1_2-1187_3DANVILE_LA!, 3HODGE_LA!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1187_3DANVILE_LA!,3HODGE_LA! | G_1ANO U1 ID 1 |  | VH
205532 | 18L | Approved | P3 | 33 | 3DELHI_LA! | VH |  |  |  |  | 1.0573 | 1.0187 | 0.92 | 1.05 | 8038 | P1_2-1257_3DELHI_LA!, 3DUNN!+G_1GGNS U1 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! | G_1GGNS U1 ID 1 |  | VH
205533 | 18L | Approved | P3 | 33 | 3DELHI_LA! | VH |  |  |  |  | 1.0545 | 1.0187 | 0.92 | 1.05 | 8063 | P1_2-1257_3DELHI_LA!, 3DUNN!+G_1WHT BLUF U1 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! | G_1WHT BLUF U1 ID 1 |  | VH
205534 | 18L | Approved | P3 | 33 | 3DELHI_LA! | VH |  |  |  |  | 1.0545 | 1.0187 | 0.92 | 1.05 | 8064 | P1_2-1257_3DELHI_LA!, 3DUNN!+G_1WHT BLUF U2 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! | G_1WHT BLUF U2 ID 1 |  | VH
205535 | 18L | Approved | P3 | 33 | 3DELHI_LA! | VH |  |  |  |  | 1.0544 | 1.0187 | 0.92 | 1.05 | 8070 | P1_2-1257_3DELHI_LA!, 3DUNN!+G_1LSPWRU1 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1257_3DELHI_LA!,3DUNN! | G_1LSPWRU1 ID 1 |  | VH
205536 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0566 | 1.0394 | 0.92 | 1.05 | 8221 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1WHT BLUF U1 ID 1 |  | VH
205537 | 18L | Approved | P3 | 33 | 3STUTGART IN | VH |  |  |  |  | 1.0515 | 1.0347 | 0.92 | 1.05 | 8221 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+108 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1WHT BLUF U1 ID 1 |  | VH
205538 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0626 | 1.0466 | 0.92 | 1.05 | 8221 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+108 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1WHT BLUF U1 ID 1 |  | VH
205539 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0502 | 1.0691 | 0.92 | 1.05 | 8224 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ANO U2 ID 1 |  | VH
205540 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0551 | 1.0394 | 0.92 | 1.05 | 8225 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U1 ID 1 |  | VH
205541 | 18L | Approved | P3 | 33 | 3STUTGART IN | VH |  |  |  |  | 1.05 | 1.0347 | 0.92 | 1.05 | 8225 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U1 ID 1 |  | VH
205542 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.061 | 1.0466 | 0.92 | 1.05 | 8225 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U1 ID 1 |  | VH
205543 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0548 | 1.0394 | 0.92 | 1.05 | 8226 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U2 ID 1 |  | VH
205544 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0571 | 1.0439 | 0.92 | 1.05 | 8226 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U2 ID 1 |  | VH
205545 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0571 | 1.0439 | 0.92 | 1.05 | 8226 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U2 ID 1 |  | VH
205546 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0607 | 1.0466 | 0.92 | 1.05 | 8226 | P1_2-1301_3WOODWARD-N!, 3RICUSKEY!+G_1ISES U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1301_3WOODWARD-N!,3RICUSKEY! | G_1ISES U2 ID 1 |  | VH
205547 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0505 | 1.0357 | 0.92 | 1.05 | 8379 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+108 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205548 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0535 | 1.0394 | 0.92 | 1.05 | 8379 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205549 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0554 | 1.0375 | 0.92 | 1.05 | 8379 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+108 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205550 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.06 | 1.0466 | 0.92 | 1.05 | 8379 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+108 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205551 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0513 | 1.0394 | 0.92 | 1.05 | 8381 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205552 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.051 | 1.0375 | 0.92 | 1.05 | 8381 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U1 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205553 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0579 | 1.0466 | 0.92 | 1.05 | 8381 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205554 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 8381 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205555 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0515 | 1.0394 | 0.92 | 1.05 | 8382 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205556 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0583 | 1.0439 | 0.92 | 1.05 | 8382 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205557 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0583 | 1.0439 | 0.92 | 1.05 | 8382 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205558 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0518 | 1.0375 | 0.92 | 1.05 | 8382 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U2 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205559 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0579 | 1.0466 | 0.92 | 1.05 | 8382 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+G_1ISES U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205560 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0512 | 1.0375 | 0.92 | 1.05 | 8386 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+117 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
205561 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0507 | 1.0256 | 0.92 | 1.05 | 8386 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+117 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
205562 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0502 | 1.0375 | 0.92 | 1.05 | 8399 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+130 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WRIGHTS S1 ID 1 |  | VH
205563 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0504 | 1.0375 | 0.92 | 1.05 | 8400 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+131 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WRIGHTS C7 ID 1 |  | VH
205564 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0502 | 1.0375 | 0.92 | 1.05 | 8401 | P1_2-1308_3PB IP SS%, 3PB ENERGY!+132 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%,3PB ENERGY! | G_1WRIGHTS S2 ID 1 |  | VH
205565 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0505 | 1.0357 | 0.92 | 1.05 | 8535 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205566 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0535 | 1.0394 | 0.92 | 1.05 | 8535 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205567 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0554 | 1.0375 | 0.92 | 1.05 | 8535 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U1 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205568 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.06 | 1.0466 | 0.92 | 1.05 | 8535 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
205569 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0503 | 1.0357 | 0.92 | 1.05 | 8536 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U2 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
205570 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0532 | 1.0394 | 0.92 | 1.05 | 8536 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
205571 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0551 | 1.0375 | 0.92 | 1.05 | 8536 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U2 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
205572 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0597 | 1.0466 | 0.92 | 1.05 | 8536 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WHT BLUF U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
205573 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0513 | 1.0394 | 0.92 | 1.05 | 8537 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205574 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.051 | 1.0375 | 0.92 | 1.05 | 8537 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U1 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205575 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0579 | 1.0466 | 0.92 | 1.05 | 8537 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205576 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 8537 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
205577 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0515 | 1.0394 | 0.92 | 1.05 | 8538 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205578 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0583 | 1.0439 | 0.92 | 1.05 | 8538 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205579 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0583 | 1.0439 | 0.92 | 1.05 | 8538 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205580 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0518 | 1.0375 | 0.92 | 1.05 | 8538 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U2 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205581 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0579 | 1.0466 | 0.92 | 1.05 | 8538 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1ISES U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
205582 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0512 | 1.0375 | 0.92 | 1.05 | 8542 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1MCCLELAN U1 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
205583 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0507 | 1.0256 | 0.92 | 1.05 | 8542 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
205584 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0502 | 1.0375 | 0.92 | 1.05 | 8555 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WRIGHTS S1 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WRIGHTS S1 ID 1 |  | VH
205585 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0504 | 1.0375 | 0.92 | 1.05 | 8556 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WRIGHTS C7 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WRIGHTS C7 ID 1 |  | VH
205586 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0502 | 1.0375 | 0.92 | 1.05 | 8557 | P1_2-1309_3PB IP!, 3PB ENERGY!+G_1WRIGHTS S2 ID 1 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!,3PB ENERGY! | G_1WRIGHTS S2 ID 1 |  | VH
205587 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0574 | 1.0691 | 0.92 | 1.05 | 8584 | P1_2-1319_8WHT BLUFF%+G_1NM G1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1NM G1 ID 1 |  | VH
205588 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0574 | 1.0691 | 0.92 | 1.05 | 8692 | P1_2-1319_8WHT BLUFF%+G_1WHT BLUF U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1WHT BLUF U2 ID 1 |  | VH
205589 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0595 | 1.0493 | 0.92 | 1.05 | 8692 | P1_2-1319_8WHT BLUFF%+G_1WHT BLUF U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1WHT BLUF U2 ID 1 |  | VH
205590 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0596 | 1.0439 | 0.92 | 1.05 | 8694 | P1_2-1319_8WHT BLUFF%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205591 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0597 | 1.0439 | 0.92 | 1.05 | 8694 | P1_2-1319_8WHT BLUFF%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205592 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0603 | 1.0493 | 0.92 | 1.05 | 8694 | P1_2-1319_8WHT BLUFF%+G_1ISES U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205593 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0525 | 1.0256 | 0.92 | 1.05 | 8697 | P1_2-1319_8WHT BLUFF%+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1MCCLELAN U1 ID 1 |  | VH
205594 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0574 | 1.0691 | 0.92 | 1.05 | 8846 | P1_2-1320_8WHT BLUFF%+G_1WHT BLUF U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1WHT BLUF U1 ID 1 |  | VH
205595 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0595 | 1.0493 | 0.92 | 1.05 | 8846 | P1_2-1320_8WHT BLUFF%+G_1WHT BLUF U1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1WHT BLUF U1 ID 1 |  | VH
205596 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 8849 | P1_2-1320_8WHT BLUFF%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205597 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 8849 | P1_2-1320_8WHT BLUFF%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205598 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0598 | 1.0493 | 0.92 | 1.05 | 8849 | P1_2-1320_8WHT BLUFF%+G_1ISES U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
205599 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0523 | 1.0256 | 0.92 | 1.05 | 8852 | P1_2-1320_8WHT BLUFF%+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1MCCLELAN U1 ID 1 |  | VH
205600 | 18L | Approved | P3 | 33 | 8MCNEIL% | VH |  |  |  |  | 1.0514 | 1.0379 | 0.92 | 1.05 | 9001 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337515 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
205601 | 18L | Approved | P3 | 33 | 8ETTA% | VH |  |  |  |  | 1.0638 | 1.0341 | 0.92 | 1.05 | 9001 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
205602 | 18L | Approved | P3 | 33 | 8DUKE HS-1! | VH |  |  |  |  | 1.0638 | 1.0341 | 0.92 | 1.05 | 9001 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
205603 | 18L | Approved | P3 | 33 | 8DUKE HS-2! | VH |  |  |  |  | 1.0638 | 1.0341 | 0.92 | 1.05 | 9001 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
205604 | 18L | Approved | P3 | 33 | 8MCNEIL% | VH |  |  |  |  | 1.0512 | 1.0379 | 0.92 | 1.05 | 9002 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337515 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
205605 | 18L | Approved | P3 | 33 | 8ETTA% | VH |  |  |  |  | 1.0636 | 1.0341 | 0.92 | 1.05 | 9002 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
205606 | 18L | Approved | P3 | 33 | 8DUKE HS-1! | VH |  |  |  |  | 1.0636 | 1.0341 | 0.92 | 1.05 | 9002 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
205607 | 18L | Approved | P3 | 33 | 8DUKE HS-2! | VH |  |  |  |  | 1.0636 | 1.0341 | 0.92 | 1.05 | 9002 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%,8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
205608 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0504 | 1.0365 | 0.92 | 1.05 | 9133 | P1_2-1396_8WRIGHTSVLE%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
205609 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0595 | 1.0439 | 0.92 | 1.05 | 9134 | P1_2-1396_8WRIGHTSVLE%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
205610 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0595 | 1.0439 | 0.92 | 1.05 | 9134 | P1_2-1396_8WRIGHTSVLE%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
205611 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0593 | 1.0493 | 0.92 | 1.05 | 9134 | P1_2-1396_8WRIGHTSVLE%+G_1ISES U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
205612 | 18L | Approved | P3 | 33 | 8HOLND BTM% | VH |  |  |  |  | 1.0515 | 1.0342 | 0.92 | 1.05 | 9170 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1NM G1 ID 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1NM G1 ID 1 |  | VH
205613 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0587 | 1.0691 | 0.92 | 1.05 | 9170 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1NM G1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1NM G1 ID 1 |  | VH
205614 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0606 | 1.0493 | 0.92 | 1.05 | 9170 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1NM G1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1NM G1 ID 1 |  | VH
205615 | 18L | Approved | P3 | 33 | 8HOLND BTM% | VH |  |  |  |  | 1.0516 | 1.0342 | 0.92 | 1.05 | 9277 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U1 ID 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U1 ID 1 |  | VH
205616 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0579 | 1.0691 | 0.92 | 1.05 | 9277 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U1 ID 1 |  | VH
205617 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0621 | 1.0493 | 0.92 | 1.05 | 9277 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U1 ID 1 |  | VH
205618 | 18L | Approved | P3 | 33 | 8HOLND BTM% | VH |  |  |  |  | 1.0514 | 1.0342 | 0.92 | 1.05 | 9278 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U2 ID 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U2 ID 1 |  | VH
205619 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0578 | 1.0691 | 0.92 | 1.05 | 9278 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U2 ID 1 |  | VH
205620 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0618 | 1.0493 | 0.92 | 1.05 | 9278 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1WHT BLUF U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1WHT BLUF U2 ID 1 |  | VH
205621 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0555 | 1.0691 | 0.92 | 1.05 | 9279 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ANO U1 ID 1 |  | VH
205622 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0545 | 1.0691 | 0.92 | 1.05 | 9280 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ANO U2 ID 1 |  | VH
205623 | 18L | Approved | P3 | 33 | 8HOLND BTM% | VH |  |  |  |  | 1.0548 | 1.0342 | 0.92 | 1.05 | 9281 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U1 ID 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
205624 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0584 | 1.0439 | 0.92 | 1.05 | 9281 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
205625 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0584 | 1.0439 | 0.92 | 1.05 | 9281 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
205626 | 18L | Approved | P3 | 33 | 5HOLND BTM! | VH |  |  |  |  | 1.0523 | 1.0335 | 0.92 | 1.05 | 9282 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U2 ID 1 | 338015 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
205627 | 18L | Approved | P3 | 33 | 8HOLND BTM% | VH |  |  |  |  | 1.0618 | 1.0342 | 0.92 | 1.05 | 9282 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U2 ID 1 | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
205628 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.067 | 1.0439 | 0.92 | 1.05 | 9282 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
205629 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0671 | 1.0439 | 0.92 | 1.05 | 9282 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
205630 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0601 | 1.0493 | 0.92 | 1.05 | 9282 | P1_2-1442_8KEO%, 8HOLND BTM%+G_1ISES U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%,8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
205631 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.057 | 1.0357 | 0.92 | 1.05 | 9590 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+108 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205632 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.056 | 1.0348 | 0.92 | 1.05 | 9590 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+108 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205633 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0612 | 1.0394 | 0.92 | 1.05 | 9590 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205634 | 18L | Approved | P3 | 33 | 3ALMYRA | VH |  |  |  |  | 1.0506 | 1.0297 | 0.92 | 1.05 | 9590 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+108 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205635 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0663 | 1.0466 | 0.92 | 1.05 | 9590 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+108 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205636 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0517 | 1.0394 | 0.92 | 1.05 | 9592 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ANO U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ANO U1 ID 1 |  | VH
205637 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0504 | 1.0691 | 0.92 | 1.05 | 9592 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ANO U1 ID 1 |  | VH
205638 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0568 | 1.0466 | 0.92 | 1.05 | 9592 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ANO U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ANO U1 ID 1 |  | VH
205639 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0513 | 1.0394 | 0.92 | 1.05 | 9593 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ANO U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ANO U2 ID 1 |  | VH
205640 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0502 | 1.0691 | 0.92 | 1.05 | 9593 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ANO U2 ID 1 |  | VH
205641 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0524 | 1.0357 | 0.92 | 1.05 | 9594 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205642 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0514 | 1.0348 | 0.92 | 1.05 | 9594 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205643 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0567 | 1.0394 | 0.92 | 1.05 | 9594 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205644 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0622 | 1.0466 | 0.92 | 1.05 | 9594 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U1 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205645 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0531 | 1.0357 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205646 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0521 | 1.0348 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205647 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0574 | 1.0394 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205648 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0575 | 1.0439 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205649 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0576 | 1.0439 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205650 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0627 | 1.0466 | 0.92 | 1.05 | 9595 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1ISES U2 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1ISES U2 ID 1 | Project Proposed | VH | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
205651 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0512 | 1.0357 | 0.92 | 1.05 | 9597 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1LSPWRU1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1LSPWRU1 ID 1 |  | VH
205652 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0502 | 1.0348 | 0.92 | 1.05 | 9597 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1LSPWRU1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1LSPWRU1 ID 1 |  | VH
205653 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0556 | 1.0394 | 0.92 | 1.05 | 9597 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1LSPWRU1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1LSPWRU1 ID 1 |  | VH
205654 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0607 | 1.0466 | 0.92 | 1.05 | 9597 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+G_1LSPWRU1 ID 1 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1LSPWRU1 ID 1 |  | VH
205655 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0515 | 1.0357 | 0.92 | 1.05 | 9599 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+117 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1MCCLELAN U1 ID 1 |  | VH
205656 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0505 | 1.0348 | 0.92 | 1.05 | 9599 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+117 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1MCCLELAN U1 ID 1 |  | VH
205657 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0558 | 1.0394 | 0.92 | 1.05 | 9599 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+117 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1MCCLELAN U1 ID 1 |  | VH
205658 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0607 | 1.0466 | 0.92 | 1.05 | 9599 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+117 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1MCCLELAN U1 ID 1 |  | VH
205659 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9606 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+124 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 1 |  | VH
205660 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9606 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+124 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 1 |  | VH
205661 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9606 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+124 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 1 |  | VH
205662 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9606 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+124 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 1 |  | VH
205663 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9607 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+125 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 2 |  | VH
205664 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9607 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+125 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 2 |  | VH
205665 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9607 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+125 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 2 |  | VH
205666 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9607 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+125 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C1 ID 2 |  | VH
205667 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9608 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+126 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 1 |  | VH
205668 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9608 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+126 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 1 |  | VH
205669 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9608 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+126 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 1 |  | VH
205670 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9608 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+126 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 1 |  | VH
205671 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9609 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+127 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 2 |  | VH
205672 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9609 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+127 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 2 |  | VH
205673 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9609 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+127 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 2 |  | VH
205674 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9609 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+127 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C3 ID 2 |  | VH
205675 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9610 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+128 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 1 |  | VH
205676 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9610 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+128 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 1 |  | VH
205677 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9610 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+128 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 1 |  | VH
205678 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9610 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+128 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 1 |  | VH
205679 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0511 | 1.0357 | 0.92 | 1.05 | 9611 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+129 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 2 |  | VH
205680 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0501 | 1.0348 | 0.92 | 1.05 | 9611 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+129 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 2 |  | VH
205681 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0554 | 1.0394 | 0.92 | 1.05 | 9611 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+129 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 2 |  | VH
205682 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0605 | 1.0466 | 0.92 | 1.05 | 9611 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+129 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C5 ID 2 |  | VH
205683 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0514 | 1.0357 | 0.92 | 1.05 | 9612 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+130 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S1 ID 1 |  | VH
205684 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0504 | 1.0348 | 0.92 | 1.05 | 9612 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+130 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S1 ID 1 |  | VH
205685 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0558 | 1.0394 | 0.92 | 1.05 | 9612 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+130 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S1 ID 1 |  | VH
205686 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0608 | 1.0466 | 0.92 | 1.05 | 9612 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+130 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S1 ID 1 |  | VH
205687 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0516 | 1.0357 | 0.92 | 1.05 | 9613 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+131 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C7 ID 1 |  | VH
205688 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0507 | 1.0348 | 0.92 | 1.05 | 9613 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+131 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C7 ID 1 |  | VH
205689 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.056 | 1.0394 | 0.92 | 1.05 | 9613 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+131 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C7 ID 1 |  | VH
205690 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.061 | 1.0466 | 0.92 | 1.05 | 9613 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+131 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS C7 ID 1 |  | VH
205691 | 18L | Approved | P3 | 33 | 3STUTGART.N+ | VH |  |  |  |  | 1.0514 | 1.0357 | 0.92 | 1.05 | 9614 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+132 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S2 ID 1 |  | VH
205692 | 18L | Approved | P3 | 33 | 3STUTGART.N | VH |  |  |  |  | 1.0504 | 1.0348 | 0.92 | 1.05 | 9614 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+132 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S2 ID 1 |  | VH
205693 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.0557 | 1.0394 | 0.92 | 1.05 | 9614 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+132 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S2 ID 1 |  | VH
205694 | 18L | Approved | P3 | 33 | 2DELUCE | VH |  |  |  |  | 1.0608 | 1.0466 | 0.92 | 1.05 | 9614 | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E!+132 | 338581 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!,3BRINKLEY.E! | G_1WRIGHTS S2 ID 1 |  | VH
205695 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0534 | 1.0365 | 0.92 | 1.05 | 9748 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+108 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1WHT BLUF U1 ID 1 |  | VH
205696 | 18L | Approved | P3 | 33 | 2WYNNE.E | VH |  |  |  |  | 1.0617 | 1.0451 | 0.92 | 1.05 | 9748 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+108 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1WHT BLUF U1 ID 1 |  | VH
205697 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0505 | 1.0691 | 0.92 | 1.05 | 9750 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ANO U1 ID 1 |  | VH
205698 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0503 | 1.0691 | 0.92 | 1.05 | 9751 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ANO U2 ID 1 |  | VH
205699 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0552 | 1.0365 | 0.92 | 1.05 | 9752 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U1 ID 1 |  | VH
205700 | 18L | Approved | P3 | 33 | 2WYNNE.E | VH |  |  |  |  | 1.0575 | 1.0451 | 0.92 | 1.05 | 9752 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U1 ID 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U1 ID 1 |  | VH
205701 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0577 | 1.0439 | 0.92 | 1.05 | 9753 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U2 ID 1 |  | VH
205702 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0578 | 1.0439 | 0.92 | 1.05 | 9753 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U2 ID 1 |  | VH
205703 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.054 | 1.0365 | 0.92 | 1.05 | 9753 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U2 ID 1 |  | VH
205704 | 18L | Approved | P3 | 33 | 2WYNNE.E | VH |  |  |  |  | 1.0609 | 1.0451 | 0.92 | 1.05 | 9753 | P1_2-1458_3BRINKLEY.E!, 5MOSES%+G_1ISES U2 ID 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!,5MOSES% | G_1ISES U2 ID 1 |  | VH
205705 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0569 | 1.0691 | 0.92 | 1.05 | 9908 | P1_2-1461_3SRCY PRICE!, 5SRCY PRICE!+113 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1461_3SRCY PRICE!,5SRCY PRICE! | G_1ISES U2 ID 1 |  | VH
205706 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0588 | 1.0439 | 0.92 | 1.05 | 10064 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!,5ISES-2! | G_1ISES U2 ID 1 |  | VH
205707 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0588 | 1.0439 | 0.92 | 1.05 | 10064 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!,5ISES-2! | G_1ISES U2 ID 1 |  | VH
205708 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 10064 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!,5ISES-2! | G_1ISES U2 ID 1 |  | VH
205709 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0551 | 1.0439 | 0.92 | 1.05 | 10172 | P1_2-1494_8ISES%+G_1WAT U3! ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WAT U3! ID 1 |  | VH
205710 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0551 | 1.0439 | 0.92 | 1.05 | 10172 | P1_2-1494_8ISES%+G_1WAT U3! ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WAT U3! ID 1 |  | VH
205711 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0588 | 1.0691 | 0.92 | 1.05 | 10172 | P1_2-1494_8ISES%+G_1WAT U3! ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WAT U3! ID 1 |  | VH
205712 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0596 | 1.0439 | 0.92 | 1.05 | 10217 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
205713 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0597 | 1.0439 | 0.92 | 1.05 | 10217 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
205714 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0603 | 1.0493 | 0.92 | 1.05 | 10217 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
205715 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 10218 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
205716 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 10218 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
205717 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0598 | 1.0493 | 0.92 | 1.05 | 10218 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
205718 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0588 | 1.0439 | 0.92 | 1.05 | 10219 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
205719 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0588 | 1.0439 | 0.92 | 1.05 | 10219 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
205720 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 10219 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
205721 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0561 | 1.0439 | 0.92 | 1.05 | 10255 | P1_2-1494_8ISES%+G_JBOGA&B1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_JBOGA&B1 ID 1 |  | VH
205722 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0561 | 1.0439 | 0.92 | 1.05 | 10255 | P1_2-1494_8ISES%+G_JBOGA&B1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_JBOGA&B1 ID 1 |  | VH
205723 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0587 | 1.0691 | 0.92 | 1.05 | 10255 | P1_2-1494_8ISES%+G_JBOGA&B1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_JBOGA&B1 ID 1 |  | VH
205724 | 18L | Approved | P3 | 33 | 8SANS SOUCI% | VH |  |  |  |  | 1.0719 | 1.0614 | 0.92 | 1.05 | 10373 | P1_2-1522_8DELL%, 8SANS SOUCI%+G_1WHT BLUF U1 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1WHT BLUF U1 ID 1 |  | VH
205725 | 18L | Approved | P3 | 33 | 8SANS SOUCI% | VH |  |  |  |  | 1.0718 | 1.0614 | 0.92 | 1.05 | 10374 | P1_2-1522_8DELL%, 8SANS SOUCI%+G_1WHT BLUF U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1WHT BLUF U2 ID 1 |  | VH
205726 | 18L | Approved | P3 | 33 | 8SANS SOUCI% | VH |  |  |  |  | 1.0715 | 1.0614 | 0.92 | 1.05 | 10378 | P1_2-1522_8DELL%, 8SANS SOUCI%+G_1ISES U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1522_8DELL%,8SANS SOUCI% | G_1ISES U2 ID 1 |  | VH
205727 | 18L | Approved | P3 | 33 | 3SEDGWICK | VH |  |  |  |  | 1.0631 | 1.0484 | 0.92 | 1.05 | 10423 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+G_1NM G1 ID 1 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1NM G1 ID 1 |  | VH
205728 | 18L | Approved | P3 | 33 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0544 | 1.0396 | 0.92 | 1.05 | 10423 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+G_1NM G1 ID 1 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1NM G1 ID 1 |  | VH
205729 | 18L | Approved | P3 | 33 | 3WALNUT RDG! | VH |  |  |  |  | 1.0633 | 1.0461 | 0.92 | 1.05 | 10423 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+G_1NM G1 ID 1 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1NM G1 ID 1 |  | VH
205730 | 18L | Approved | P3 | 33 | 3LIGHT# | VH |  |  |  |  | 1.0643 | 1.0517 | 0.92 | 1.05 | 10423 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+G_1NM G1 ID 1 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1NM G1 ID 1 |  | VH
205731 | 18L | Approved | P3 | 33 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0655 | 1.0549 | 0.92 | 1.05 | 10423 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+G_1NM G1 ID 1 | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1NM G1 ID 1 |  | VH
205732 | 18L | Approved | P3 | 33 | 3SEDGWICK | VH |  |  |  |  | 1.0627 | 1.0484 | 0.92 | 1.05 | 10530 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+108 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1WHT BLUF U1 ID 1 |  | VH
205733 | 18L | Approved | P3 | 33 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0541 | 1.0396 | 0.92 | 1.05 | 10530 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+108 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1WHT BLUF U1 ID 1 |  | VH
205734 | 18L | Approved | P3 | 33 | 3WALNUT RDG! | VH |  |  |  |  | 1.063 | 1.0461 | 0.92 | 1.05 | 10530 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+108 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1WHT BLUF U1 ID 1 |  | VH
205735 | 18L | Approved | P3 | 33 | 3LIGHT# | VH |  |  |  |  | 1.0639 | 1.0517 | 0.92 | 1.05 | 10530 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+108 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1WHT BLUF U1 ID 1 |  | VH
205736 | 18L | Approved | P3 | 33 | 3CROWLEYRDG# | VH |  |  |  |  | 1.0652 | 1.0549 | 0.92 | 1.05 | 10530 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+108 | 338710 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1WHT BLUF U1 ID 1 |  | VH
205737 | 18L | Approved | P3 | 33 | 3SEDGWICK | VH |  |  |  |  | 1.061 | 1.0484 | 0.92 | 1.05 | 10534 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+112 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U1 ID 1 |  | VH
205738 | 18L | Approved | P3 | 33 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0524 | 1.0396 | 0.92 | 1.05 | 10534 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+112 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U1 ID 1 |  | VH
205739 | 18L | Approved | P3 | 33 | 3WALNUT RDG! | VH |  |  |  |  | 1.0613 | 1.0461 | 0.92 | 1.05 | 10534 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+112 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U1 ID 1 |  | VH
205740 | 18L | Approved | P3 | 33 | 3LIGHT# | VH |  |  |  |  | 1.0622 | 1.0517 | 0.92 | 1.05 | 10534 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+112 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U1 ID 1 |  | VH
205741 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0566 | 1.0439 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205742 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0566 | 1.0439 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205743 | 18L | Approved | P3 | 33 | 3SEDGWICK | VH |  |  |  |  | 1.0611 | 1.0484 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338206 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205744 | 18L | Approved | P3 | 33 | 3T.E.P/S-7 | VH |  |  |  |  | 1.0524 | 1.0396 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338207 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205745 | 18L | Approved | P3 | 33 | 3WALNUT RDG! | VH |  |  |  |  | 1.0613 | 1.0461 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338208 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205746 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0552 | 1.0691 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205747 | 18L | Approved | P3 | 33 | 3LIGHT# | VH |  |  |  |  | 1.0623 | 1.0517 | 0.92 | 1.05 | 10535 | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG%+113 | 338704 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!,5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
205748 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 11311 | P1_2-1591_8FRENCHCAMP%, 8CHOCTAW MS%+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% | G_1ISES U2 ID 1 |  | VH
205749 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 11311 | P1_2-1591_8FRENCHCAMP%, 8CHOCTAW MS%+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% | G_1ISES U2 ID 1 |  | VH
205750 | 18L | Approved | P3 | 33 | 8CHOCTAW CC | VH |  |  |  |  | 1.0511 | 1.0348 | 0.92 | 1.05 | 11311 | P1_2-1591_8FRENCHCAMP%, 8CHOCTAW MS%+113 | 360627 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% | G_1ISES U2 ID 1 |  | VH
205751 | 18L | Approved | P3 | 33 | 8CHOCTAW MS | VH |  |  |  |  | 1.0511 | 1.0348 | 0.92 | 1.05 | 11311 | P1_2-1591_8FRENCHCAMP%, 8CHOCTAW MS%+113 | 360654 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1591_8FRENCHCAMP%,8CHOCTAW MS% | G_1ISES U2 ID 1 |  | VH
205752 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 11463 | P1_2-1603_3NEWTON!, 3HICKORY SO+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1603_3NEWTON!,3HICKORY SO | G_1ANO U1 ID 1 |  | VH
205753 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 11618 | P1_2-1605_3NEWTON!, 3SP W FOR,3FORINDT2!+110 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1605_3NEWTON!,3SP W FOR,3FORINDT2! | G_1ANO U1 ID 1 |  | VH
205754 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 11621 | P1_2-1605_3NEWTON!, 3SP W FOR,3FORINDT2!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1605_3NEWTON!,3SP W FOR,3FORINDT2! | G_1ISES U2 ID 1 |  | VH
205755 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 11621 | P1_2-1605_3NEWTON!, 3SP W FOR,3FORINDT2!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1605_3NEWTON!,3SP W FOR,3FORINDT2! | G_1ISES U2 ID 1 |  | VH
205756 | 18L | Approved | P3 | 33 | 8DANIEL | VH |  |  |  |  | 1.0833 | 1.0292 | 0.92 | 1.05 | 11749 | P1_2-1607_8DANIEL%, 6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
205757 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0508 | 1.0691 | 0.92 | 1.05 | 11777 | P1_2-1607_8DANIEL%, 6DANIEL!+G_1ANO U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1ANO U2 ID 1 |  | VH
205758 | 18L | Approved | P3 | 33 | 8DANIEL | VH |  |  |  |  | 1.0812 | 1.0292 | 0.92 | 1.05 | 11777 | P1_2-1607_8DANIEL%, 6DANIEL!+G_1ANO U2 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1ANO U2 ID 1 |  | VH
205759 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 11934 | P1_2-1639_CLARN 6!, MESSICK6!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1639_CLARN 6!,MESSICK6! | G_1ANO U1 ID 1 |  | VH
205760 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 12092 | P1_2-1640_CLARN 4!, NATCH 4!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_1ANO U1 ID 1 |  | VH
205761 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 12248 | P1_2-1655_COUGH 4!, MARKSVL4!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1655_COUGH 4!,MARKSVL4! | G_1ANO U1 ID 1 |  | VH
205762 | 18L | Approved | P3 | 33 | 4CANEY | VL |  |  |  |  | 0.9179 | 0.9974 | 0.92 | 1.05 | 12338 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
205763 | 18L | Approved | P3 | 33 | OAKDALE4 | VL |  |  |  |  | 0.9197 | 0.9969 | 0.92 | 1.05 | 12338 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
205764 | 18L | Approved | P3 | 33 | PNPRARIE 4 | VL |  |  |  |  | 0.9111 | 1.0028 | 0.92 | 1.05 | 12338 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
205765 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0514 | 1.0691 | 0.92 | 1.05 | 12406 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1 |  | VH
205766 | 18L | Approved | P3 | 33 | PNPRARIE 4 | VL |  |  |  |  | 0.9156 | 1.0028 | 0.92 | 1.05 | 12406 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1ANO U1 ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_1ANO U1 ID 1
205767 | 18L | Approved | P3 | 33 | 5HARRISBURG+ | VH |  |  |  |  | 1.0502 | 1.0314 | 0.92 | 1.05 | 12703 | P1_2-1772_HERGETT2!, JONESBO2!+G_1WHT BLUF U2 ID 1 | 338167 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1772_HERGETT2!,JONESBO2! | G_1WHT BLUF U2 ID 1 |  | VH
205768 | 18L | Approved | P3 | 33 | 5TRUMANN | VH |  |  |  |  | 1.0502 | 1.0301 | 0.92 | 1.05 | 12703 | P1_2-1772_HERGETT2!, JONESBO2!+G_1WHT BLUF U2 ID 1 | 338169 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1772_HERGETT2!,JONESBO2! | G_1WHT BLUF U2 ID 1 |  | VH
205769 | 18L | Approved | P3 | 33 | 2TRUMANN.W | VH |  |  |  |  | 1.0506 | 1.0265 | 0.92 | 1.05 | 12703 | P1_2-1772_HERGETT2!, JONESBO2!+G_1WHT BLUF U2 ID 1 | 338568 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1772_HERGETT2!,JONESBO2! | G_1WHT BLUF U2 ID 1 |  | VH
205770 | 18L | Approved | P3 | 33 | 2WYNNE.E | VH |  |  |  |  | 1.0557 | 1.0451 | 0.92 | 1.05 | 12703 | P1_2-1772_HERGETT2!, JONESBO2!+G_1WHT BLUF U2 ID 1 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1772_HERGETT2!,JONESBO2! | G_1WHT BLUF U2 ID 1 |  | VH
205771 | 18L | Approved | P3 | 33 | 5TRUMANN.W# | VH |  |  |  |  | 1.0506 | 1.0265 | 0.92 | 1.05 | 12703 | P1_2-1772_HERGETT2!, JONESBO2!+G_1WHT BLUF U2 ID 1 | 338707 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1772_HERGETT2!,JONESBO2! | G_1WHT BLUF U2 ID 1 |  | VH
205772 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0515 | 1.0691 | 0.92 | 1.05 | 12852 | P1_2-1866_LEBROCK7!, TENRUSK7!+G_1ANO U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U1 ID 1 |  | VH
205773 | 18L | Approved | P3 | 33 | TENRUSK7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 12852 | P1_2-1866_LEBROCK7!, TENRUSK7!+G_1ANO U1 ID 1 | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U1 ID 1 |  | VH
205774 | 18L | Approved | P3 | 33 | TENGEN 7 | VH |  |  |  |  | 1.0567 | 1.0205 | 0.92 | 1.05 | 12852 | P1_2-1866_LEBROCK7!, TENRUSK7!+G_1ANO U1 ID 1 | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1866_LEBROCK7!,TENRUSK7! | G_1ANO U1 ID 1 |  | VH
205775 | 18L | Approved | P3 | 33 | FTSMITH7 | VH |  |  |  |  | 1.0567 | 1.0373 | 0.92 | 1.05 | 13055 | P1_2-1892_FTSMITH7%, FTSMITH8%+G_MUSKOG4G ID 1 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | P1_2-1892_FTSMITH7%,FTSMITH8% | G_MUSKOG4G ID 1 |  | VH
205776 | 18L | Approved | P3 | 33 | 3CORNING.N# | VH |  |  |  |  | 1.0503 | 1.0391 | 0.92 | 1.05 | 13086 | G_1NM G1 ID 1+P1_2-1532_5JIM HILL%, 3JIM HILL! | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%,3JIM HILL! | G_1NM G1 ID 1 |  | VH
205777 | 18L | Approved | P3 | 33 | 3PARAGOULD! | VH |  |  |  |  | 1.0692 | 1.0589 | 0.92 | 1.05 | 13087 | G_1NM G1 ID 1+P1_2-1534_3PARAGOULD!, 3WALNUT RDG! | 338205 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!,3WALNUT RDG! | G_1NM G1 ID 1 |  | VH
205778 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0504 | 1.0242 | 0.92 | 1.05 | 13101 | G_1BCAJUN2_U1% ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1BCAJUN2_U1% ID 1 |  | VH
205779 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0526 | 1.0418 | 0.92 | 1.05 | 13169 | G_1G1LEWIS! ID 1+P1_2-234_2PANSY!, 2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1G1LEWIS! ID 1 |  | VH
205780 | 18L | Approved | P3 | 33 | 2HIMEX | VH |  |  |  |  | 1.0526 | 1.0418 | 0.92 | 1.05 | 13201 | G_1G2LEWIS! ID 1+P1_2-234_2PANSY!, 2SO.BMT.! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-234_2PANSY!,2SO.BMT.! | G_1G2LEWIS! ID 1 |  | VH
205781 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0546 | 1.0242 | 0.92 | 1.05 | 13221 | G_1PELCNRD U1! ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1PELCNRD U1! ID 1 |  | VH
205782 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0546 | 1.0242 | 0.92 | 1.05 | 13237 | G_1PELCNRD U2! ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1PELCNRD U2! ID 1 |  | VH
205783 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0505 | 1.0242 | 0.92 | 1.05 | 13320 | G_1NELSON_G6! ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1NELSON_G6! ID 1 |  | VH
205784 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0507 | 1.0242 | 0.92 | 1.05 | 13406 | G_1WAT U3! ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1WAT U3! ID 1 |  | VH
205785 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0506 | 1.0242 | 0.92 | 1.05 | 13486 | G_1GGNS U1 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1GGNS U1 ID 1 |  | VH
205786 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0945 | 1.0777 | 0.92 | 1.05 | 13507 | G_1GGNS U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1GGNS U1 ID 1 |  | VH
205787 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.1017 | 1.0715 | 0.92 | 1.05 | 13507 | G_1GGNS U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1GGNS U1 ID 1 |  | VH
205788 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0945 | 1.0802 | 0.92 | 1.05 | 13507 | G_1GGNS U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1GGNS U1 ID 1 |  | VH
205789 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.1017 | 1.0715 | 0.92 | 1.05 | 13507 | G_1GGNS U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1GGNS U1 ID 1 |  | VH
205790 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205791 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205792 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205793 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205794 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205795 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205796 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205797 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205798 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0535 | 1.0211 | 0.92 | 1.05 | 13728 | G_1ATTALA S1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ATTALA S1 ID 1 |  | VH
205799 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 13729 | G_1ATTALA S1 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1ATTALA S1 ID 1 |  | VH
205800 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205801 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205802 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205803 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205804 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205805 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205806 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205807 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205808 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205809 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 14278 | G_1ATTALA S1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ATTALA S1 ID 1 |  | VH
205810 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9044 | 1.0071 | 0.92 | 1.05 | 15153 | G_1ATTALA S1 ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ATTALA S1 ID 1 |  | Facility: Radial
205811 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205812 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205813 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205814 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0591 | 1.0209 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205815 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205816 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205817 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205818 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205819 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0535 | 1.0211 | 0.92 | 1.05 | 15373 | G_1SLSBAU3 ID 5+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1SLSBAU3 ID 5 |  | VH
205820 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 15374 | G_1SLSBAU3 ID 5+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1SLSBAU3 ID 5 |  | VH
205821 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205822 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205823 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205824 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205825 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205826 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205827 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205828 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205829 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205830 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 15939 | G_1SLSBAU3 ID 5+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1SLSBAU3 ID 5 |  | VH
205831 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0524 | 1.0667 | 0.92 | 1.05 | 16284 | G_1SLSBAU3 ID 5+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1SLSBAU3 ID 5 |  | VH
205832 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0583 | 1.0691 | 0.92 | 1.05 | 16592 | G_1SLSBAU3 ID 5+P1_2-1495_8ISES%, 8DELL% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1495_8ISES%,8DELL% | G_1SLSBAU3 ID 5 |  | VH
205833 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0563 | 1.0715 | 0.92 | 1.05 | 16655 | G_1SLSBAU3 ID 5+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205834 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0563 | 1.0715 | 0.92 | 1.05 | 16655 | G_1SLSBAU3 ID 5+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205835 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0921 | 1.0777 | 0.92 | 1.05 | 16658 | G_1SLSBAU3 ID 5+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205836 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 16658 | G_1SLSBAU3 ID 5+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205837 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0922 | 1.0802 | 0.92 | 1.05 | 16658 | G_1SLSBAU3 ID 5+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205838 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 16658 | G_1SLSBAU3 ID 5+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1SLSBAU3 ID 5 |  | VH
205839 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9044 | 1.0071 | 0.92 | 1.05 | 16983 | G_1SLSBAU3 ID 5+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1SLSBAU3 ID 5 |  | Facility: Radial
205840 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0574 | 1.0691 | 0.92 | 1.05 | 17032 | G_1WHT BLUF U1 ID 1+P1_2-28_5NEWMAD! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-28_5NEWMAD! | G_1WHT BLUF U1 ID 1 |  | VH
205841 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0689 | 1.0242 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205842 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205843 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205844 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205845 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205846 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205847 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205848 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0522 | 1.0213 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205849 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0536 | 1.0211 | 0.92 | 1.05 | 17190 | G_1WHT BLUF U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1WHT BLUF U1 ID 1 |  | VH
205850 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 17191 | G_1WHT BLUF U1 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1WHT BLUF U1 ID 1 |  | VH
205851 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205852 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205853 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205854 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205855 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205856 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205857 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205858 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205859 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205860 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 17756 | G_1WHT BLUF U1 ID 1+923 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1WHT BLUF U1 ID 1 |  | VH
205861 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0551 | 1.0667 | 0.92 | 1.05 | 18117 | G_1WHT BLUF U1 ID 1+1320 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1WHT BLUF U1 ID 1 |  | VH
205862 | 18L | Approved | P3 | 33 | 2GLENDALE-1 | VH |  |  |  |  | 1.0513 | 1.0375 | 0.92 | 1.05 | 18230 | G_1WHT BLUF U1 ID 1+1437 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1279_3EL DORADO!,3MONTCELO.E! | G_1WHT BLUF U1 ID 1 |  | VH
205863 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0593 | 1.0493 | 0.92 | 1.05 | 18324 | G_1WHT BLUF U1 ID 1+1537 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1379_8MABELVALE%,8MAYFLOWER% | G_1WHT BLUF U1 ID 1 |  | VH
205864 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0594 | 1.0493 | 0.92 | 1.05 | 18328 | G_1WHT BLUF U1 ID 1+P1_2-1383_3LR.S!, 3NLR DIXIE! | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1383_3LR.S!,3NLR DIXIE! | G_1WHT BLUF U1 ID 1 |  | VH
205865 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0594 | 1.0493 | 0.92 | 1.05 | 18343 | G_1WHT BLUF U1 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%,8KEO% | G_1WHT BLUF U1 ID 1 |  | VH
205866 | 18L | Approved | P3 | 33 | 2HEBER.N | VH |  |  |  |  | 1.0543 | 1.044 | 0.92 | 1.05 | 18359 | G_1WHT BLUF U1 ID 1+P1_2-1417_5QUITMAN!, 5HAMLET% | 338585 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1417_5QUITMAN!,5HAMLET% | G_1WHT BLUF U1 ID 1 |  | VH
205867 | 18L | Approved | P3 | 33 | 2HEBER.N | VH |  |  |  |  | 1.0544 | 1.044 | 0.92 | 1.05 | 18360 | G_1WHT BLUF U1 ID 1+P1_2-1418_5QUITMAN!, 5HILLTOP% | 338585 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1418_5QUITMAN!,5HILLTOP% | G_1WHT BLUF U1 ID 1 |  | VH
205868 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0596 | 1.0493 | 0.92 | 1.05 | 18370 | G_1WHT BLUF U1 ID 1+1586 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1428_3MURRAY HYD!,3SYLVAN HLS!,3NLR LEVY! | G_1WHT BLUF U1 ID 1 |  | VH
205869 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0594 | 1.0493 | 0.92 | 1.05 | 18381 | G_1WHT BLUF U1 ID 1+1597 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1439_3JAXNVLE.N!,3HOLND BTM! | G_1WHT BLUF U1 ID 1 |  | VH
205870 | 18L | Approved | P3 | 33 | 3RICUSKEY! | VH |  |  |  |  | 1.052 | 1.0394 | 0.92 | 1.05 | 18384 | G_1WHT BLUF U1 ID 1+1603 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!,3GILLETT! | G_1WHT BLUF U1 ID 1 |  | VH
205871 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0611 | 1.0493 | 0.92 | 1.05 | 18408 | G_1WHT BLUF U1 ID 1+1630 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!,5SOUTHSIDE! | G_1WHT BLUF U1 ID 1 |  | VH
205872 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0545 | 1.0439 | 0.92 | 1.05 | 18421 | G_1WHT BLUF U1 ID 1+1644 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | G_1WHT BLUF U1 ID 1 |  | VH
205873 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0525 | 1.0256 | 0.92 | 1.05 | 18476 | G_1WHT BLUF U1 ID 1+P1_2-1551_3MCCLELLAN#! | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1WHT BLUF U1 ID 1 |  | VH
205874 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0591 | 1.0715 | 0.92 | 1.05 | 18485 | G_1WHT BLUF U1 ID 1+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205875 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0591 | 1.0715 | 0.92 | 1.05 | 18485 | G_1WHT BLUF U1 ID 1+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205876 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0929 | 1.0777 | 0.92 | 1.05 | 18488 | G_1WHT BLUF U1 ID 1+1720 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205877 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.1001 | 1.0715 | 0.92 | 1.05 | 18488 | G_1WHT BLUF U1 ID 1+1720 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205878 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0929 | 1.0802 | 0.92 | 1.05 | 18488 | G_1WHT BLUF U1 ID 1+1720 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205879 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.1001 | 1.0715 | 0.92 | 1.05 | 18488 | G_1WHT BLUF U1 ID 1+1720 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1WHT BLUF U1 ID 1 |  | VH
205880 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0559 | 1.0667 | 0.92 | 1.05 | 18490 | G_1WHT BLUF U1 ID 1+1722 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1WHT BLUF U1 ID 1 |  | VH
205881 | 18L | Approved | P3 | 33 | 8HAYWOOD TN | VH |  |  |  |  | 1.0752 | 1.0647 | 0.92 | 1.05 | 18492 | G_1WHT BLUF U1 ID 1+1726 | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1571_8CORDOVA TN!,8HAYWOOD TN | G_1WHT BLUF U1 ID 1 |  | VH
205882 | 18L | Approved | P3 | 33 | 5JONESBORO! | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 18671 | G_1WHT BLUF U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5,JONESBO5% | G_1WHT BLUF U1 ID 1 |  | VH
205883 | 18L | Approved | P3 | 33 | 2JONSBORO.W | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 18671 | G_1WHT BLUF U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5,JONESBO5% | G_1WHT BLUF U1 ID 1 |  | VH
205884 | 18L | Approved | P3 | 33 | 5JONSBORO.W# | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 18671 | G_1WHT BLUF U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5,JONESBO5% | G_1WHT BLUF U1 ID 1 |  | VH
205885 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9046 | 1.0071 | 0.92 | 1.05 | 18815 | G_1WHT BLUF U1 ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WHT BLUF U1 ID 1 |  | Facility: Radial
205886 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205887 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205888 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205889 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205890 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205891 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205892 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205893 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205894 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0536 | 1.0211 | 0.92 | 1.05 | 18998 | G_1PERRYV_C1! ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1PERRYV_C1! ID 1 |  | VH
205895 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 18999 | G_1PERRYV_C1! ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1PERRYV_C1! ID 1 |  | VH
205896 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205897 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205898 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205899 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205900 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205901 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205902 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205903 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205904 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205905 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 19564 | G_1PERRYV_C1! ID 1+923 | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1PERRYV_C1! ID 1 |  | VH
205906 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0517 | 1.0667 | 0.92 | 1.05 | 19925 | G_1PERRYV_C1! ID 1+1320 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1PERRYV_C1! ID 1 |  | VH
205907 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 20292 | G_1PERRYV_C1! ID 1+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205908 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0562 | 1.0715 | 0.92 | 1.05 | 20292 | G_1PERRYV_C1! ID 1+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205909 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0921 | 1.0777 | 0.92 | 1.05 | 20295 | G_1PERRYV_C1! ID 1+1720 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205910 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 20295 | G_1PERRYV_C1! ID 1+1720 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205911 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0922 | 1.0802 | 0.92 | 1.05 | 20295 | G_1PERRYV_C1! ID 1+1720 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205912 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0993 | 1.0715 | 0.92 | 1.05 | 20295 | G_1PERRYV_C1! ID 1+1720 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1PERRYV_C1! ID 1 |  | VH
205913 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0519 | 1.0667 | 0.92 | 1.05 | 20297 | G_1PERRYV_C1! ID 1+1722 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1PERRYV_C1! ID 1 |  | VH
205914 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9045 | 1.0071 | 0.92 | 1.05 | 20622 | G_1PERRYV_C1! ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1PERRYV_C1! ID 1 |  | Facility: Radial
205915 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0691 | 0.92 | 1.05 | 20623 | G_1ANO U1 ID 1+1249 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1091_3ROLING FRK!,3GREENVILLE! | G_1ANO U1 ID 1 | Project Proposed | VH | 11-EMI-007-CP | 2019-06-01 | Install breakers at Hollandale and Belzoni Tap 115 kV; close normally-open point
205916 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0513 | 1.0691 | 0.92 | 1.05 | 20624 | G_1ANO U1 ID 1+P1_2-1100_6MCADAMS%, 3ATTALA! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1100_6MCADAMS%,3ATTALA! | G_1ANO U1 ID 1 |  | VH
205917 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0512 | 1.0691 | 0.92 | 1.05 | 20625 | G_1ANO U1 ID 1+P1_2-1115_6ANDRUS%, 3BAGBY! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1115_6ANDRUS%,3BAGBY! | G_1ANO U1 ID 1 |  | VH
205918 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0511 | 1.0691 | 0.92 | 1.05 | 20626 | G_1ANO U1 ID 1+P1_2-1127_6S.GRENADA!, 3S.GRENADA! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1127_6S.GRENADA!,3S.GRENADA! | G_1ANO U1 ID 1 |  | VH
205919 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0918 | 1.0777 | 0.92 | 1.05 | 20630 | G_1ANO U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U1 ID 1 |  | VH
205920 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.099 | 1.0715 | 0.92 | 1.05 | 20630 | G_1ANO U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U1 ID 1 |  | VH
205921 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0919 | 1.0802 | 0.92 | 1.05 | 20630 | G_1ANO U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U1 ID 1 |  | VH
205922 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.099 | 1.0715 | 0.92 | 1.05 | 20630 | G_1ANO U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U1 ID 1 |  | VH
205923 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0946 | 1.0777 | 0.92 | 1.05 | 20637 | G_1ANO U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U2 ID 1 |  | VH
205924 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.1018 | 1.0715 | 0.92 | 1.05 | 20637 | G_1ANO U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U2 ID 1 |  | VH
205925 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0946 | 1.0802 | 0.92 | 1.05 | 20637 | G_1ANO U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U2 ID 1 |  | VH
205926 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.1018 | 1.0715 | 0.92 | 1.05 | 20637 | G_1ANO U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ANO U2 ID 1 |  | VH
205927 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0556 | 1.0691 | 0.92 | 1.05 | 20680 | G_1ISES U1 ID 1+P1_2-47_5GOBKNOB!, 5COXCRK% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-47_5GOBKNOB!,5COXCRK% | G_1ISES U1 ID 1 |  | VH
205928 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0573 | 1.0691 | 0.92 | 1.05 | 20696 | G_1ISES U1 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%,5THAYER.S! | G_1ISES U1 ID 1 |  | VH
205929 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205930 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205931 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205932 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205933 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205934 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205935 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205936 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205937 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0536 | 1.0211 | 0.92 | 1.05 | 20820 | G_1ISES U1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U1 ID 1 |  | VH
205938 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 20821 | G_1ISES U1 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1ISES U1 ID 1 |  | VH
205939 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205940 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205941 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205942 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205943 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205944 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205945 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205946 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205947 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205948 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 21386 | G_1ISES U1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U1 ID 1 |  | VH
205949 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0529 | 1.0667 | 0.92 | 1.05 | 21747 | G_1ISES U1 ID 1+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1ISES U1 ID 1 |  | VH
205950 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0543 | 1.0439 | 0.92 | 1.05 | 21897 | G_1ISES U1 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U1 ID 1 |  | VH
205951 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0543 | 1.0439 | 0.92 | 1.05 | 21897 | G_1ISES U1 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U1 ID 1 |  | VH
205952 | 18L | Approved | P3 | 33 | 2WARD | VH |  |  |  |  | 1.0594 | 1.0493 | 0.92 | 1.05 | 21897 | G_1ISES U1 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U1 ID 1 |  | VH
205953 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0515 | 1.0365 | 0.92 | 1.05 | 21897 | G_1ISES U1 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U1 ID 1 |  | VH
205954 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0365 | 0.92 | 1.05 | 21971 | G_1ISES U1 ID 1+P1_2-1397_8WRIGHTSVLE% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
205955 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0503 | 1.0365 | 0.92 | 1.05 | 21972 | G_1ISES U1 ID 1+P1_2-1398_8WRIGHTSVLE% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
205956 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.051 | 1.0365 | 0.92 | 1.05 | 21973 | G_1ISES U1 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%,8KEO% | G_1ISES U1 ID 1 |  | VH
205957 | 18L | Approved | P3 | 33 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0505 | 1.0401 | 0.92 | 1.05 | 22025 | G_1ISES U1 ID 1+P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1456_3BRINKLEY.E!,3CARLISLE! | G_1ISES U1 ID 1 |  | VH
205958 | 18L | Approved | P3 | 33 | 2BAILEY | VH |  |  |  |  | 1.0546 | 1.0365 | 0.92 | 1.05 | 22032 | G_1ISES U1 ID 1+P1_2-1468_5MOSES%, 5BAILEY#! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1468_5MOSES%,5BAILEY#! | G_1ISES U1 ID 1 |  | VH
205959 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0579 | 1.0691 | 0.92 | 1.05 | 22072 | G_1ISES U1 ID 1+P1_2-1512_5JONESBORO!, JONESBO5% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1512_5JONESBORO!,JONESBO5% | G_1ISES U1 ID 1 |  | VH
205960 | 18L | Approved | P3 | 33 | 5JONESBORO! | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 22073 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!,HERGETT5! | G_1ISES U1 ID 1 |  | VH
205961 | 18L | Approved | P3 | 33 | 2JONSBORO.W | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 22073 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!,HERGETT5! | G_1ISES U1 ID 1 |  | VH
205962 | 18L | Approved | P3 | 33 | 5JONSBORO.W# | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 22073 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!,HERGETT5! | G_1ISES U1 ID 1 |  | VH
205963 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0567 | 1.0691 | 0.92 | 1.05 | 22092 | G_1ISES U1 ID 1+P1_2-1533_5PARAGOULD%, 3PARAGOULD! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1533_5PARAGOULD%,3PARAGOULD! | G_1ISES U1 ID 1 |  | VH
205964 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0583 | 1.0715 | 0.92 | 1.05 | 22118 | G_1ISES U1 ID 1+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205965 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0583 | 1.0715 | 0.92 | 1.05 | 22118 | G_1ISES U1 ID 1+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205966 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.0925 | 1.0777 | 0.92 | 1.05 | 22121 | G_1ISES U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205967 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0997 | 1.0715 | 0.92 | 1.05 | 22121 | G_1ISES U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205968 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0925 | 1.0802 | 0.92 | 1.05 | 22121 | G_1ISES U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205969 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0997 | 1.0715 | 0.92 | 1.05 | 22121 | G_1ISES U1 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U1 ID 1 |  | VH
205970 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0537 | 1.0667 | 0.92 | 1.05 | 22123 | G_1ISES U1 ID 1+1722 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1ISES U1 ID 1 |  | VH
205971 | 18L | Approved | P3 | 33 | 8HAYWOOD TN | VH |  |  |  |  | 1.0749 | 1.0647 | 0.92 | 1.05 | 22125 | G_1ISES U1 ID 1+1726 | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1571_8CORDOVA TN!,8HAYWOOD TN | G_1ISES U1 ID 1 |  | VH
205972 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9045 | 1.0071 | 0.92 | 1.05 | 22448 | G_1ISES U1 ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ISES U1 ID 1 |  | Facility: Radial
205973 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0564 | 1.0439 | 0.92 | 1.05 | 22453 | G_1ISES U2 ID 1+P1_2-6_7FLETCH, 7GOBKNOB% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-6_7FLETCH,7GOBKNOB% | G_1ISES U2 ID 1 |  | VH
205974 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0564 | 1.0439 | 0.92 | 1.05 | 22453 | G_1ISES U2 ID 1+P1_2-6_7FLETCH, 7GOBKNOB% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-6_7FLETCH,7GOBKNOB% | G_1ISES U2 ID 1 |  | VH
205975 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0581 | 1.0691 | 0.92 | 1.05 | 22453 | G_1ISES U2 ID 1+P1_2-6_7FLETCH, 7GOBKNOB% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-6_7FLETCH,7GOBKNOB% | G_1ISES U2 ID 1 |  | VH
205976 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0565 | 1.0439 | 0.92 | 1.05 | 22459 | G_1ISES U2 ID 1+P1_2-14_7GOBKNOB%, 5GOBKNOB! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-14_7GOBKNOB%,5GOBKNOB! | G_1ISES U2 ID 1 |  | VH
205977 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0566 | 1.0439 | 0.92 | 1.05 | 22459 | G_1ISES U2 ID 1+P1_2-14_7GOBKNOB%, 5GOBKNOB! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-14_7GOBKNOB%,5GOBKNOB! | G_1ISES U2 ID 1 |  | VH
205978 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0563 | 1.0691 | 0.92 | 1.05 | 22459 | G_1ISES U2 ID 1+P1_2-14_7GOBKNOB%, 5GOBKNOB! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-14_7GOBKNOB%,5GOBKNOB! | G_1ISES U2 ID 1 |  | VH
205979 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0565 | 1.0439 | 0.92 | 1.05 | 22507 | G_1ISES U2 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%,5THAYER.S! | G_1ISES U2 ID 1 |  | VH
205980 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0565 | 1.0439 | 0.92 | 1.05 | 22507 | G_1ISES U2 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%,5THAYER.S! | G_1ISES U2 ID 1 |  | VH
205981 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0522 | 1.0691 | 0.92 | 1.05 | 22507 | G_1ISES U2 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%,5THAYER.S! | G_1ISES U2 ID 1 |  | VH
205982 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205983 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205984 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205985 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0592 | 1.0209 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205986 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205987 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205988 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0516 | 1.0207 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205989 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205990 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0536 | 1.0211 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205991 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205992 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 22631 | G_1ISES U2 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1ISES U2 ID 1 |  | VH
205993 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 22632 | G_1ISES U2 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1ISES U2 ID 1 |  | VH
205994 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 22632 | G_1ISES U2 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1ISES U2 ID 1 |  | VH
205995 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 22632 | G_1ISES U2 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1ISES U2 ID 1 |  | VH
205996 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
205997 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
205998 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
205999 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206000 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206001 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206002 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206003 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206004 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206005 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206006 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206007 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 23197 | G_1ISES U2 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1ISES U2 ID 1 |  | VH
206008 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0552 | 1.0439 | 0.92 | 1.05 | 23309 | G_1ISES U2 ID 1+P1_2-879_6WATFRD% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-879_6WATFRD% | G_1ISES U2 ID 1 |  | VH
206009 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0552 | 1.0439 | 0.92 | 1.05 | 23309 | G_1ISES U2 ID 1+P1_2-879_6WATFRD% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-879_6WATFRD% | G_1ISES U2 ID 1 |  | VH
206010 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0589 | 1.0691 | 0.92 | 1.05 | 23309 | G_1ISES U2 ID 1+P1_2-879_6WATFRD% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-879_6WATFRD% | G_1ISES U2 ID 1 |  | VH
206011 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0538 | 1.0667 | 0.92 | 1.05 | 23558 | G_1ISES U2 ID 1+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1ISES U2 ID 1 |  | VH
206012 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 23558 | G_1ISES U2 ID 1+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1ISES U2 ID 1 |  | VH
206013 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 23558 | G_1ISES U2 ID 1+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1ISES U2 ID 1 |  | VH
206014 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0585 | 1.0691 | 0.92 | 1.05 | 23658 | G_1ISES U2 ID 1+P1_2-1266_8MCNEIL%, 8ETTA% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1266_8MCNEIL%,8ETTA% | G_1ISES U2 ID 1 |  | VH
206015 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0545 | 1.0439 | 0.92 | 1.05 | 23702 | G_1ISES U2 ID 1+P1_2-1313_8SHERIDAN%, 8WHT BLUFF% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
206016 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0546 | 1.0439 | 0.92 | 1.05 | 23702 | G_1ISES U2 ID 1+P1_2-1313_8SHERIDAN%, 8WHT BLUFF% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
206017 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0589 | 1.0691 | 0.92 | 1.05 | 23702 | G_1ISES U2 ID 1+P1_2-1313_8SHERIDAN%, 8WHT BLUFF% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1313_8SHERIDAN%,8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
206018 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0592 | 1.0439 | 0.92 | 1.05 | 23708 | G_1ISES U2 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U2 ID 1 |  | VH
206019 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 23708 | G_1ISES U2 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%,8KEO% | G_1ISES U2 ID 1 |  | VH
206020 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0546 | 1.0439 | 0.92 | 1.05 | 23737 | G_1ISES U2 ID 1+P1_2-1351_8HS EHV%, 8MAGNETCOVE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1ISES U2 ID 1 |  | VH
206021 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0546 | 1.0439 | 0.92 | 1.05 | 23737 | G_1ISES U2 ID 1+P1_2-1351_8HS EHV%, 8MAGNETCOVE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1ISES U2 ID 1 |  | VH
206022 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0589 | 1.0691 | 0.92 | 1.05 | 23737 | G_1ISES U2 ID 1+P1_2-1351_8HS EHV%, 8MAGNETCOVE% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1351_8HS EHV%,8MAGNETCOVE% | G_1ISES U2 ID 1 |  | VH
206023 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0592 | 1.0439 | 0.92 | 1.05 | 23782 | G_1ISES U2 ID 1+P1_2-1397_8WRIGHTSVLE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
206024 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 23782 | G_1ISES U2 ID 1+P1_2-1397_8WRIGHTSVLE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
206025 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0593 | 1.0439 | 0.92 | 1.05 | 23783 | G_1ISES U2 ID 1+P1_2-1398_8WRIGHTSVLE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
206026 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0594 | 1.0439 | 0.92 | 1.05 | 23783 | G_1ISES U2 ID 1+P1_2-1398_8WRIGHTSVLE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
206027 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0547 | 1.0439 | 0.92 | 1.05 | 23792 | G_1ISES U2 ID 1+P1_2-1409_8ANO%, FTSMITH8% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1409_8ANO%,FTSMITH8% | G_1ISES U2 ID 1 |  | VH
206028 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0548 | 1.0439 | 0.92 | 1.05 | 23792 | G_1ISES U2 ID 1+P1_2-1409_8ANO%, FTSMITH8% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1409_8ANO%,FTSMITH8% | G_1ISES U2 ID 1 |  | VH
206029 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0586 | 1.0691 | 0.92 | 1.05 | 23792 | G_1ISES U2 ID 1+P1_2-1409_8ANO%, FTSMITH8% | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1409_8ANO%,FTSMITH8% | G_1ISES U2 ID 1 |  | VH
206030 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0551 | 1.0439 | 0.92 | 1.05 | 23837 | G_1ISES U2 ID 1+1617 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1460_3SRCY PRICE!,3HOLND BTM! | G_1ISES U2 ID 1 |  | VH
206031 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0552 | 1.0439 | 0.92 | 1.05 | 23837 | G_1ISES U2 ID 1+1617 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1460_3SRCY PRICE!,3HOLND BTM! | G_1ISES U2 ID 1 |  | VH
206032 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0578 | 1.0691 | 0.92 | 1.05 | 23837 | G_1ISES U2 ID 1+1617 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1460_3SRCY PRICE!,3HOLND BTM! | G_1ISES U2 ID 1 |  | VH
206033 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0559 | 1.0439 | 0.92 | 1.05 | 23844 | G_1ISES U2 ID 1+P1_2-1470_5PARKIN!, 5NEWPORT! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1470_5PARKIN!,5NEWPORT! | G_1ISES U2 ID 1 |  | VH
206034 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0559 | 1.0439 | 0.92 | 1.05 | 23844 | G_1ISES U2 ID 1+P1_2-1470_5PARKIN!, 5NEWPORT! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1470_5PARKIN!,5NEWPORT! | G_1ISES U2 ID 1 |  | VH
206035 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0583 | 1.0691 | 0.92 | 1.05 | 23844 | G_1ISES U2 ID 1+P1_2-1470_5PARKIN!, 5NEWPORT! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1470_5PARKIN!,5NEWPORT! | G_1ISES U2 ID 1 |  | VH
206036 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0542 | 1.0439 | 0.92 | 1.05 | 23849 | G_1ISES U2 ID 1+1630 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!,5SOUTHSIDE! | G_1ISES U2 ID 1 |  | VH
206037 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0542 | 1.0439 | 0.92 | 1.05 | 23849 | G_1ISES U2 ID 1+1630 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!,5SOUTHSIDE! | G_1ISES U2 ID 1 |  | VH
206038 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0576 | 1.0691 | 0.92 | 1.05 | 23849 | G_1ISES U2 ID 1+1630 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!,5SOUTHSIDE! | G_1ISES U2 ID 1 |  | VH
206039 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0644 | 1.0439 | 0.92 | 1.05 | 23862 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%, 8ISES% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%,8ISES% | G_1ISES U2 ID 1 |  | VH
206040 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0645 | 1.0439 | 0.92 | 1.05 | 23862 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%, 8ISES% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%,8ISES% | G_1ISES U2 ID 1 |  | VH
206041 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0631 | 1.0439 | 0.92 | 1.05 | 23863 | G_1ISES U2 ID 1+1644 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1489_5ISES-1!,8ISES%,5ISES-2! | G_1ISES U2 ID 1 |  | VH
206042 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0557 | 1.0439 | 0.92 | 1.05 | 23864 | G_1ISES U2 ID 1+P1_2-1490_5ISES-1!, 5RUTHERFORD! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1490_5ISES-1!,5RUTHERFORD! | G_1ISES U2 ID 1 |  | VH
206043 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0557 | 1.0439 | 0.92 | 1.05 | 23864 | G_1ISES U2 ID 1+P1_2-1490_5ISES-1!, 5RUTHERFORD! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1490_5ISES-1!,5RUTHERFORD! | G_1ISES U2 ID 1 |  | VH
206044 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.059 | 1.0691 | 0.92 | 1.05 | 23864 | G_1ISES U2 ID 1+P1_2-1490_5ISES-1!, 5RUTHERFORD! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1490_5ISES-1!,5RUTHERFORD! | G_1ISES U2 ID 1 |  | VH
206045 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.056 | 1.0439 | 0.92 | 1.05 | 23870 | G_1ISES U2 ID 1+P1_2-1499_5NEWPORT!, 5JONESBORO! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1499_5NEWPORT!,5JONESBORO! | G_1ISES U2 ID 1 |  | VH
206046 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0561 | 1.0439 | 0.92 | 1.05 | 23870 | G_1ISES U2 ID 1+P1_2-1499_5NEWPORT!, 5JONESBORO! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1499_5NEWPORT!,5JONESBORO! | G_1ISES U2 ID 1 |  | VH
206047 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0584 | 1.0691 | 0.92 | 1.05 | 23870 | G_1ISES U2 ID 1+P1_2-1499_5NEWPORT!, 5JONESBORO! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1499_5NEWPORT!,5JONESBORO! | G_1ISES U2 ID 1 |  | VH
206048 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0562 | 1.0439 | 0.92 | 1.05 | 23872 | G_1ISES U2 ID 1+P1_2-1501_5NEWPORT!, 5BAILEY#! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1501_5NEWPORT!,5BAILEY#! | G_1ISES U2 ID 1 |  | VH
206049 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0562 | 1.0439 | 0.92 | 1.05 | 23872 | G_1ISES U2 ID 1+P1_2-1501_5NEWPORT!, 5BAILEY#! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1501_5NEWPORT!,5BAILEY#! | G_1ISES U2 ID 1 |  | VH
206050 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0591 | 1.0691 | 0.92 | 1.05 | 23872 | G_1ISES U2 ID 1+P1_2-1501_5NEWPORT!, 5BAILEY#! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1501_5NEWPORT!,5BAILEY#! | G_1ISES U2 ID 1 |  | VH
206051 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0567 | 1.0439 | 0.92 | 1.05 | 23904 | G_1ISES U2 ID 1+1689 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!,3WALNUT RDG! | G_1ISES U2 ID 1 |  | VH
206052 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 23904 | G_1ISES U2 ID 1+1689 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!,3WALNUT RDG! | G_1ISES U2 ID 1 |  | VH
206053 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0553 | 1.0691 | 0.92 | 1.05 | 23904 | G_1ISES U2 ID 1+1689 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!,3WALNUT RDG! | G_1ISES U2 ID 1 |  | VH
206054 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0554 | 1.0439 | 0.92 | 1.05 | 23929 | G_1ISES U2 ID 1+1715 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206055 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0554 | 1.0439 | 0.92 | 1.05 | 23929 | G_1ISES U2 ID 1+1715 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206056 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0596 | 1.0715 | 0.92 | 1.05 | 23929 | G_1ISES U2 ID 1+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206057 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0596 | 1.0715 | 0.92 | 1.05 | 23929 | G_1ISES U2 ID 1+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206058 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0559 | 1.0439 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206059 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0559 | 1.0439 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206060 | 18L | Approved | P3 | 33 | 8WEAKLEY TN | VH |  |  |  |  | 1.093 | 1.0777 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206061 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.1002 | 1.0715 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206062 | 18L | Approved | P3 | 33 | 8GLEASON CT | VH |  |  |  |  | 1.0931 | 1.0802 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206063 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.1002 | 1.0715 | 0.92 | 1.05 | 23932 | G_1ISES U2 ID 1+P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!,8LAG CRK CT% | G_1ISES U2 ID 1 |  | VH
206064 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0552 | 1.0439 | 0.92 | 1.05 | 23936 | G_1ISES U2 ID 1+1726 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1571_8CORDOVA TN!,8HAYWOOD TN | G_1ISES U2 ID 1 |  | VH
206065 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0552 | 1.0439 | 0.92 | 1.05 | 23936 | G_1ISES U2 ID 1+1726 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1571_8CORDOVA TN!,8HAYWOOD TN | G_1ISES U2 ID 1 |  | VH
206066 | 18L | Approved | P3 | 33 | 8HAYWOOD TN | VH |  |  |  |  | 1.0752 | 1.0647 | 0.92 | 1.05 | 23936 | G_1ISES U2 ID 1+1726 | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1571_8CORDOVA TN!,8HAYWOOD TN | G_1ISES U2 ID 1 |  | VH
206067 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.056 | 1.0439 | 0.92 | 1.05 | 24118 | G_1ISES U2 ID 1+P1_2-1762_JONESBO5%, JONESBO2! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1762_JONESBO5%,JONESBO2! | G_1ISES U2 ID 1 |  | VH
206068 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0561 | 1.0439 | 0.92 | 1.05 | 24118 | G_1ISES U2 ID 1+P1_2-1762_JONESBO5%, JONESBO2! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1762_JONESBO5%,JONESBO2! | G_1ISES U2 ID 1 |  | VH
206069 | 18L | Approved | P3 | 33 | 2BLACK ROCK | VH |  |  |  |  | 1.0587 | 1.0691 | 0.92 | 1.05 | 24118 | G_1ISES U2 ID 1+P1_2-1762_JONESBO5%, JONESBO2! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1762_JONESBO5%,JONESBO2! | G_1ISES U2 ID 1 |  | VH
206070 | 18L | Approved | P3 | 33 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0439 | 0.92 | 1.05 | 24259 | G_1ISES U2 ID 1+2061 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | VH
206071 | 18L | Approved | P3 | 33 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0439 | 0.92 | 1.05 | 24259 | G_1ISES U2 ID 1+2061 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | VH
206072 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9045 | 1.0071 | 0.92 | 1.05 | 24259 | G_1ISES U2 ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1ISES U2 ID 1 |  | Facility: Radial
206073 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0688 | 1.0242 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206074 | 18L | Approved | P3 | 33 | 4SHECORR | VH |  |  |  |  | 1.0682 | 1.0237 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334130 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206075 | 18L | Approved | P3 | 33 | 4CAMDEN | VH |  |  |  |  | 1.0653 | 1.0221 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334131 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206076 | 18L | Approved | P3 | 33 | 4DEER 1 | VH |  |  |  |  | 1.0591 | 1.0209 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334132 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206077 | 18L | Approved | P3 | 33 | 4TURKEYCRK | VH |  |  |  |  | 1.0565 | 1.0207 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334279 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206078 | 18L | Approved | P3 | 33 | 4DOUCETT! | VH |  |  |  |  | 1.0569 | 1.0207 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334280 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206079 | 18L | Approved | P3 | 33 | 4FORK CK | VH |  |  |  |  | 1.0515 | 1.0207 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334281 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206080 | 18L | Approved | P3 | 33 | 4URLAND! | VH |  |  |  |  | 1.0521 | 1.0213 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334314 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206081 | 18L | Approved | P3 | 33 | 4WOODVILLE | VH |  |  |  |  | 1.0535 | 1.0211 | 0.92 | 1.05 | 24447 | G_1LSPWRU1 ID 1+P1_2-189_4STALEY!, 4CORIGAN! | 334315 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-189_4STALEY!,4CORIGAN! | G_1LSPWRU1 ID 1 |  | VH
206082 | 18L | Approved | P3 | 33 | 4CORIGAN! | VH |  |  |  |  | 1.0502 | 1.0242 | 0.92 | 1.05 | 24448 | G_1LSPWRU1 ID 1+P1_2-190_4CORIGAN!, 4DOUCETT! | 334129 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-190_4CORIGAN!,4DOUCETT! | G_1LSPWRU1 ID 1 |  | VH
206083 | 18L | Approved | P3 | 33 | 2JACKSON! | VH |  |  |  |  | 1.0588 | 1.0213 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335785 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206084 | 18L | Approved | P3 | 33 | 2FELICIANA | VH |  |  |  |  | 1.0627 | 1.0143 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206085 | 18L | Approved | P3 | 33 | 2MCMANUS | VH |  |  |  |  | 1.0653 | 1.0101 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206086 | 18L | Approved | P3 | 33 | 2BRADY_HGHTS | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206087 | 18L | Approved | P3 | 33 | 2CLINTON | VH |  |  |  |  | 1.0609 | 1.0054 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206088 | 18L | Approved | P3 | 33 | 2CLINTON_REA | VH |  |  |  |  | 1.0613 | 1.0058 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206089 | 18L | Approved | P3 | 33 | 2TEJAC | VH |  |  |  |  | 1.0638 | 1.027 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335791 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206090 | 18L | Approved | P3 | 33 | 2MARYDALE | VH |  |  |  |  | 1.0692 | 1.0329 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335792 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206091 | 18L | Approved | P3 | 33 | 2FRANCIS! | VH |  |  |  |  | 1.0652 | 1.032 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335793 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206092 | 18L | Approved | P3 | 33 | 2ANGOLA | VH |  |  |  |  | 1.0507 | 1.017 | 0.92 | 1.05 | 25013 | G_1LSPWRU1 ID 1+P1_2-765_2FRANCIS!, 2PORT_HUD_B! | 335794 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-765_2FRANCIS!,2PORT_HUD_B! | G_1LSPWRU1 ID 1 |  | VH
206093 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0528 | 1.0667 | 0.92 | 1.05 | 25357 | G_1LSPWRU1 ID 1+P1_2-1162_6FREEPORT%, 6HORN LAKE% | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1162_6FREEPORT%,6HORN LAKE% | G_1LSPWRU1 ID 1 |  | VH
206094 | 18L | Approved | P3 | 33 | 8LAG CRK CT | VH |  |  |  |  | 1.0565 | 1.0715 | 0.92 | 1.05 | 25727 | G_1LSPWRU1 ID 1+1715 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1LSPWRU1 ID 1 |  | VH
206095 | 18L | Approved | P3 | 33 | 8LAG CRK CC | VH |  |  |  |  | 1.0565 | 1.0715 | 0.92 | 1.05 | 25727 | G_1LSPWRU1 ID 1+1715 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1560_8WEAKLEY TN,8LAG CRK CT% | G_1LSPWRU1 ID 1 |  | VH
206096 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0527 | 1.0667 | 0.92 | 1.05 | 25731 | G_1LSPWRU1 ID 1+1722 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1LSPWRU1 ID 1 |  | VH
206097 | 18L | Approved | P3 | 33 | ELKS 6 | VL |  |  |  |  | 0.9044 | 1.0071 | 0.92 | 1.05 | 26052 | G_1LSPWRU1 ID 1+2061 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1LSPWRU1 ID 1 |  | Facility: Radial
206098 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0576 | 1.0256 | 0.92 | 1.05 | 26056 | G_1MCCLELAN U1 ID 1+1432 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1274_3CAMDEN.N!,3FORDYCE! | G_1MCCLELAN U1 ID 1 |  | VH
206099 | 18L | Approved | P3 | 33 | 2MCCLELLAN | VH |  |  |  |  | 1.0518 | 1.0256 | 0.92 | 1.05 | 26057 | G_1MCCLELAN U1 ID 1+1449 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1291_3FORDYCE!,3WOODWARD-S! | G_1MCCLELAN U1 ID 1 |  | VH
206100 | 18L | Approved | P3 | 33 | 5HORN LAKE% | VH |  |  |  |  | 1.0509 | 1.0667 | 0.92 | 1.05 | 26160 | G_1CUMBRL F1HL ID 1+1722 | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | P1_2-1567_8FREEPORTTN%,8CORDOVA TN! | G_1CUMBRL F1HL ID 1 |  | VH
206101 | 18L | Approved | P3 | 33 | VALIANT7 | VH |  |  |  |  | 1.0505 | 1.0382 | 0.92 | 1.05 | 26241 | G_TURKCOAL ID 1+P1_2-1853_LYDIA 7, WELSH 7! | 510911 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1853_LYDIA 7,WELSH 7! | G_TURKCOAL ID 1 |  | VH
206102 | 18S | Approved | P2 | 34 | 3BEEBE | VL |  |  |  |  | 0.8644 | 0.9845 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338007 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206103 | 18S | Approved | P2 | 34 | 3GARNER+ | VL |  |  |  |  | 0.8377 | 0.9892 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338008 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206104 | 18S | Approved | P2 | 34 | 3T.E.P/S-MC | VL |  |  |  |  | 0.8375 | 0.9891 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338009 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206105 | 18S | Approved | P2 | 34 | 3SRCY PRICE! | VL |  |  |  |  | 0.8112 | 0.9956 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338010 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206106 | 18S | Approved | P2 | 34 | 3GRIFFITHVLE | VL |  |  |  |  | 0.8314 | 0.9933 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338011 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206107 | 18S | Approved | P2 | 34 | 3DES ARC | VL |  |  |  |  | 0.8648 | 0.9925 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338012 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206108 | 18S | Approved | P2 | 34 | 3COTTON PLNT | VL |  |  |  |  | 0.918 | 0.9968 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338013 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206109 | 18S | Approved | P2 | 34 | 5SRCY PRICE! | VL |  |  |  |  | 0.7906 | 0.988 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338045 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206110 | 18S | Approved | P2 | 34 | 5SEARCY.S | VL |  |  |  |  | 0.7834 | 0.9874 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338046 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206111 | 18S | Approved | P2 | 34 | 5PANGBURN | VL |  |  |  |  | 0.7597 | 1.0036 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338047 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206112 | 18S | Approved | P2 | 34 | 5BALD KNOB | VL |  |  |  |  | 0.7873 | 0.9872 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338048 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206113 | 18S | Approved | P2 | 34 | 5T.E.P/S-6 | VL |  |  |  |  | 0.7872 | 0.9876 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338049 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206114 | 18S | Approved | P2 | 34 | 3T.E.P/S-6 | VL |  |  |  |  | 0.7657 | 0.9632 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338050 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206115 | 18S | Approved | P2 | 34 | 5NEWARK AR | VL |  |  |  |  | 0.7286 | 0.9995 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338147 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206116 | 18S | Approved | P2 | 34 | 5RUTHERFORD! | VL |  |  |  |  | 0.7289 | 0.9988 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338148 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206117 | 18S | Approved | P2 | 34 | 5SOUTHSIDE! | VL |  |  |  |  | 0.7327 | 0.9971 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338149 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206118 | 18S | Approved | P2 | 34 | 5CEDARGROVE | VL |  |  |  |  | 0.7447 | 0.9996 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338150 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206119 | 18S | Approved | P2 | 34 | 5COPPERSPRG# | VL |  |  |  |  | 0.7725 | 0.9924 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338751 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206120 | 18S | Approved | P2 | 34 | 3WARD# | VL |  |  |  |  | 0.9122 | 0.9838 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338756 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206121 | 18S | Approved | P2 | 34 | 5COFFEEVLE# | VL |  |  |  |  | 0.7874 | 0.9924 | 0.92 | 1.05 | 8 | ISES 161kV bus #1 | 338759 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ISES 161kV bus #1 |  | Project Proposed |  | 11-EAI-016-CP | 2018-06-01 | Reconfigure ISES 161 kV Bus
206124 | 18L | Approved | P1 | 36 | 2RAYWOOD! | VL |  |  |  |  | 0.9112 | 0.9886 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334230 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206125 | 18L | Approved | P1 | 36 | 2DAISY | VL |  |  |  |  | 0.9147 | 0.9841 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334249 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206126 | 18L | Approved | P1 | 36 | 2DAISETA! | VL |  |  |  |  | 0.9135 | 0.9862 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334250 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206127 | 18L | Approved | P1 | 36 | 2HULL | VL |  |  |  |  | 0.9167 | 0.9822 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334251 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206128 | 18L | Approved | P1 | 36 | 26L594TAP | VL |  |  |  |  | 0.9197 | 0.9809 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334252 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206129 | 18L | Approved | P1 | 36 | 2HARDIN | VL |  |  |  |  | 0.9176 | 0.9789 | 0.92 | 1.05 | 27 | 4RAYWOOD! 138/69.0 1 + Batson - Quality Mills clos | 334253 |  |  |  | 69 | 69 | 351 | EES |  |  | 4RAYWOOD! 138/69.0 1, Batson-QMills closed |  | Project Proposed |  | 14-ETI-001-01-CP | 2018-06-01 | Install Raywood 2nd 138-69 kV Auto
206130 | 15S | Approved | P0 | 37 | 5HORN LAKE% | VH |  |  |  |  | 1.0574 | 1.0574 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
206131 | 15S | Approved | P0 | 37 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
206132 | 15S | Approved | P0 | 37 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
206169 | 15S | Approved | P3 | 37 | 4MILLCR! | VL |  |  |  |  | 0.9129 | 0.9955 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206170 | 15S | Approved | P3 | 37 | 4PINELND | VL |  |  |  |  | 0.9074 | 0.9798 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206171 | 15S | Approved | P3 | 37 | 4BROADUS | VL |  |  |  |  | 0.9034 | 0.9764 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206172 | 15S | Approved | P3 | 37 | 4ETOIL | VL |  |  |  |  | 0.9019 | 0.9751 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206173 | 15S | Approved | P3 | 37 | 4HRTNHIL | VL |  |  |  |  | 0.9091 | 0.9867 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206174 | 15S | Approved | P3 | 37 | 2WEIRGAT | VL |  |  |  |  | 0.911 | 0.9778 | 0.92 | 1.05 | 7 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206175 | 15S | Approved | P3 | 37 | 4MILLCR! | VL |  |  |  |  | 0.913 | 0.9955 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206176 | 15S | Approved | P3 | 37 | 4PINELND | VL |  |  |  |  | 0.9075 | 0.9798 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206177 | 15S | Approved | P3 | 37 | 4BROADUS | VL |  |  |  |  | 0.9036 | 0.9764 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206178 | 15S | Approved | P3 | 37 | 4ETOIL | VL |  |  |  |  | 0.9021 | 0.9751 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206179 | 15S | Approved | P3 | 37 | 4HRTNHIL | VL |  |  |  |  | 0.9092 | 0.9867 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206180 | 15S | Approved | P3 | 37 | 2WEIRGAT | VL |  |  |  |  | 0.9112 | 0.9778 | 0.92 | 1.05 | 8 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206199 | 15S | Approved | P3 | 37 | 4MILLCR! | VL |  |  |  |  | 0.9023 | 0.9955 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206200 | 15S | Approved | P3 | 37 | 4PINELND | VL |  |  |  |  | 0.8962 | 0.9798 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206201 | 15S | Approved | P3 | 37 | 4BROADUS | VL |  |  |  |  | 0.8921 | 0.9764 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206202 | 15S | Approved | P3 | 37 | 4ETOIL | VL |  |  |  |  | 0.8906 | 0.9751 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206203 | 15S | Approved | P3 | 37 | 4HRTNHIL | VL |  |  |  |  | 0.8982 | 0.9867 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206204 | 15S | Approved | P3 | 37 | 2PINELND | VL |  |  |  |  | 0.9116 | 0.9887 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206205 | 15S | Approved | P3 | 37 | 2TEMPL1* | VL |  |  |  |  | 0.9098 | 0.9871 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206206 | 15S | Approved | P3 | 37 | 2TEMPLE1 | VL |  |  |  |  | 0.9095 | 0.9868 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206207 | 15S | Approved | P3 | 37 | 2TEMPL2* | VL |  |  |  |  | 0.9096 | 0.9869 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206208 | 15S | Approved | P3 | 37 | 2TEMPLE2 | VL |  |  |  |  | 0.9094 | 0.9867 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206209 | 15S | Approved | P3 | 37 | 2TMPLSWC | VL |  |  |  |  | 0.9095 | 0.9868 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206210 | 15S | Approved | P3 | 37 | 2WEIRGAT | VL |  |  |  |  | 0.8991 | 0.9778 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206211 | 15S | Approved | P3 | 37 | 4PEACH! | VL |  |  |  |  | 0.9107 | 0.9944 | 0.92 | 1.05 | 12 | P1_2-231_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206230 | 15S | Approved | P3 | 37 | 4MILLCR! | VL |  |  |  |  | 0.9092 | 0.9955 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206231 | 15S | Approved | P3 | 37 | 4PINELND | VL |  |  |  |  | 0.9037 | 0.9798 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206232 | 15S | Approved | P3 | 37 | 4BROADUS | VL |  |  |  |  | 0.8998 | 0.9764 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206233 | 15S | Approved | P3 | 37 | 4ETOIL | VL |  |  |  |  | 0.8983 | 0.9751 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206234 | 15S | Approved | P3 | 37 | 4HRTNHIL | VL |  |  |  |  | 0.9054 | 0.9867 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206235 | 15S | Approved | P3 | 37 | 2PINELND | VL |  |  |  |  | 0.9195 | 0.9887 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206236 | 15S | Approved | P3 | 37 | 2TEMPL1* | VL |  |  |  |  | 0.9177 | 0.9871 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206237 | 15S | Approved | P3 | 37 | 2TEMPLE1 | VL |  |  |  |  | 0.9174 | 0.9868 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206238 | 15S | Approved | P3 | 37 | 2TEMPL2* | VL |  |  |  |  | 0.9175 | 0.9869 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206239 | 15S | Approved | P3 | 37 | 2TEMPLE2 | VL |  |  |  |  | 0.9173 | 0.9867 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206240 | 15S | Approved | P3 | 37 | 2TMPLSWC | VL |  |  |  |  | 0.9174 | 0.9868 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206241 | 15S | Approved | P3 | 37 | 2WEIRGAT | VL |  |  |  |  | 0.9075 | 0.9778 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206242 | 15S | Approved | P3 | 37 | 4PEACH! | VL |  |  |  |  | 0.9173 | 0.9944 | 0.92 | 1.05 | 16 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206243 | 15S | Approved | P3 | 37 | 4MILLCR! | VL |  |  |  |  | 0.9131 | 0.9955 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206244 | 15S | Approved | P3 | 37 | 4PINELND | VL |  |  |  |  | 0.9074 | 0.9798 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206245 | 15S | Approved | P3 | 37 | 4BROADUS | VL |  |  |  |  | 0.9035 | 0.9764 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206246 | 15S | Approved | P3 | 37 | 4ETOIL | VL |  |  |  |  | 0.902 | 0.9751 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206247 | 15S | Approved | P3 | 37 | 4HRTNHIL | VL |  |  |  |  | 0.9092 | 0.9867 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206248 | 15S | Approved | P3 | 37 | 2WEIRGAT | VL |  |  |  |  | 0.911 | 0.9778 | 0.92 | 1.05 | 17 | P1_2-231_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-231_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206591 | 15S | Approved | P3 | 37 | 2ST_MARTIN | VL |  |  |  |  | 0.9193 | 0.9608 | 0.92 | 1.05 | 99 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_1WAT U3! ID 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-573_2MORIL!,2NEW_IBERIA! | G_1WAT U3! ID 1 | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
206592 | 15S | Approved | P3 | 37 | LONGFL 2 | VL |  |  |  |  | 0.9193 | 0.9608 | 0.92 | 1.05 | 99 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_1WAT U3! ID 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-573_2MORIL!,2NEW_IBERIA! | G_1WAT U3! ID 1 | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
206593 | 15S | Approved | P3 | 37 | 2ST_MARTIN | VL |  |  |  |  | 0.9198 | 0.9608 | 0.92 | 1.05 | 101 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_LABBE2 ID 1 | 335429 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-573_2MORIL!,2NEW_IBERIA! | G_LABBE2 ID 1 | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
206594 | 15S | Approved | P3 | 37 | LONGFL 2 | VL |  |  |  |  | 0.9199 | 0.9608 | 0.92 | 1.05 | 101 | P1_2-573_2MORIL!,2NEW_IBERIA!+G_LABBE2 ID 1 | 500490 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-573_2MORIL!,2NEW_IBERIA! | G_LABBE2 ID 1 | Project Proposed |  | 12-EGL-010-CP | 2015-06-01 | Construct New Iberia 138 kV; install 138-69 kV transformer
206679 | 15S | Approved | P3 | 37 | 3DELHI_LA! | VL |  |  |  |  | 0.8929 | 0.979 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206680 | 15S | Approved | P3 | 37 | 3OAK_RIDGE | VL |  |  |  |  | 0.8721 | 0.9779 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206681 | 15S | Approved | P3 | 37 | 3CARSON | VL |  |  |  |  | 0.8698 | 0.9729 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206682 | 15S | Approved | P3 | 37 | 3SACKSONIA | VL |  |  |  |  | 0.8667 | 0.9702 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206683 | 15S | Approved | P3 | 37 | 3DUNN! | VL |  |  |  |  | 0.8694 | 0.9733 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206684 | 15S | Approved | P3 | 37 | 3DELHI_RX | VL |  |  |  |  | 0.8821 | 0.9765 | 0.92 | 1.05 | 142 | P1_2-1210_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1210_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
206813 | 15S | Approved | P3 | 37 | 3GILLETT! | VL |  |  |  |  | 0.9187 | 0.9696 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206814 | 15S | Approved | P3 | 37 | 3ELAINE | VL |  |  |  |  | 0.8927 | 0.9695 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206815 | 15S | Approved | P3 | 37 | 3MARVELL | VL |  |  |  |  | 0.8849 | 0.9713 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206816 | 15S | Approved | P3 | 37 | 3BARTON | VL |  |  |  |  | 0.8821 | 0.9718 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206817 | 15S | Approved | P3 | 37 | 3HELENA.W+ | VL |  |  |  |  | 0.8777 | 0.9728 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206818 | 15S | Approved | P3 | 37 | 3HELENA.C | VL |  |  |  |  | 0.876 | 0.9732 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206819 | 15S | Approved | P3 | 37 | 3HELENA IN#! | VL |  |  |  |  | 0.8757 | 0.9754 | 0.92 | 1.05 | 195 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206820 | 15S | Approved | P3 | 37 | 3GILLETT! | VL |  |  |  |  | 0.9173 | 0.9696 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206821 | 15S | Approved | P3 | 37 | 3ELAINE | VL |  |  |  |  | 0.8905 | 0.9695 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206822 | 15S | Approved | P3 | 37 | 3MARVELL | VL |  |  |  |  | 0.8825 | 0.9713 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206823 | 15S | Approved | P3 | 37 | 3BARTON | VL |  |  |  |  | 0.8797 | 0.9718 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206824 | 15S | Approved | P3 | 37 | 3HELENA.W+ | VL |  |  |  |  | 0.8752 | 0.9728 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206825 | 15S | Approved | P3 | 37 | 3HELENA.C | VL |  |  |  |  | 0.8734 | 0.9732 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206826 | 15S | Approved | P3 | 37 | 3HELENA IN#! | VL |  |  |  |  | 0.8732 | 0.9754 | 0.92 | 1.05 | 196 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206827 | 15S | Approved | P3 | 37 | 3GILLETT! | VL |  |  |  |  | 0.9178 | 0.9696 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206828 | 15S | Approved | P3 | 37 | 3ELAINE | VL |  |  |  |  | 0.8907 | 0.9695 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206829 | 15S | Approved | P3 | 37 | 3MARVELL | VL |  |  |  |  | 0.8825 | 0.9713 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206830 | 15S | Approved | P3 | 37 | 3BARTON | VL |  |  |  |  | 0.8797 | 0.9718 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206831 | 15S | Approved | P3 | 37 | 3HELENA.W+ | VL |  |  |  |  | 0.8751 | 0.9728 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206832 | 15S | Approved | P3 | 37 | 3HELENA.C | VL |  |  |  |  | 0.8734 | 0.9732 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206833 | 15S | Approved | P3 | 37 | 3HELENA IN#! | VL |  |  |  |  | 0.8731 | 0.9754 | 0.92 | 1.05 | 197 | P1_2-1443_3RITCHIE!,3HELENA IN#!+140 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206834 | 15S | Approved | P3 | 37 | 3GILLETT! | VL |  |  |  |  | 0.9177 | 0.9696 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206835 | 15S | Approved | P3 | 37 | 3ELAINE | VL |  |  |  |  | 0.8909 | 0.9695 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206836 | 15S | Approved | P3 | 37 | 3MARVELL | VL |  |  |  |  | 0.8829 | 0.9713 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206837 | 15S | Approved | P3 | 37 | 3BARTON | VL |  |  |  |  | 0.8801 | 0.9718 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206838 | 15S | Approved | P3 | 37 | 3HELENA.W+ | VL |  |  |  |  | 0.8756 | 0.9728 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206839 | 15S | Approved | P3 | 37 | 3HELENA.C | VL |  |  |  |  | 0.8738 | 0.9732 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206840 | 15S | Approved | P3 | 37 | 3HELENA IN#! | VL |  |  |  |  | 0.8736 | 0.9754 | 0.92 | 1.05 | 198 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
206841 | 15S | Approved | P3 | 37 | 8DANIEL | VH |  |  |  |  | 1.0756 | 1.0446 | 0.92 | 1.05 | 206 | P1_2-1599_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1599_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
206842 | 15S | Approved | P3 | 37 | 4CANEY | VL |  |  |  |  | 0.8727 | 0.9953 | 0.92 | 1.05 | 358 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
206843 | 15S | Approved | P3 | 37 | OAKDALE4 | VL |  |  |  |  | 0.8746 | 0.9936 | 0.92 | 1.05 | 358 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
206844 | 15S | Approved | P3 | 37 | PNPRARIE 4 | VL |  |  |  |  | 0.8655 | 1.0068 | 0.92 | 1.05 | 358 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
206845 | 15S | Approved | P3 | 37 | WSTBAY 4 | VL |  |  |  |  | 0.8864 | 0.9929 | 0.92 | 1.05 | 358 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
206846 | 15S | Approved | P3 | 37 | 4CANEY | VL |  |  |  |  | 0.8756 | 0.9953 | 0.92 | 1.05 | 359 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G4! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G4! ID 1
206847 | 15S | Approved | P3 | 37 | OAKDALE4 | VL |  |  |  |  | 0.8775 | 0.9936 | 0.92 | 1.05 | 359 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G4! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G4! ID 1
206848 | 15S | Approved | P3 | 37 | PNPRARIE 4 | VL |  |  |  |  | 0.8685 | 1.0068 | 0.92 | 1.05 | 359 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G4! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G4! ID 1
206849 | 15S | Approved | P3 | 37 | WSTBAY 4 | VL |  |  |  |  | 0.8892 | 0.9929 | 0.92 | 1.05 | 359 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G4! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G4! ID 1
206850 | 15S | Approved | P3 | 37 | 4CANEY | VL |  |  |  |  | 0.8715 | 0.9953 | 0.92 | 1.05 | 360 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
206851 | 15S | Approved | P3 | 37 | CENTNL 4 | VL |  |  |  |  | 0.919 | 0.995 | 0.92 | 1.05 | 360 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
206852 | 15S | Approved | P3 | 37 | OAKDALE4 | VL |  |  |  |  | 0.8735 | 0.9936 | 0.92 | 1.05 | 360 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
206853 | 15S | Approved | P3 | 37 | PNPRARIE 4 | VL |  |  |  |  | 0.8643 | 1.0068 | 0.92 | 1.05 | 360 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
206854 | 15S | Approved | P3 | 37 | WSTBAY 4 | VL |  |  |  |  | 0.8853 | 0.9929 | 0.92 | 1.05 | 360 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
206855 | 15S | Approved | P3 | 37 | 4CANEY | VL |  |  |  |  | 0.8754 | 0.9953 | 0.92 | 1.05 | 361 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
206856 | 15S | Approved | P3 | 37 | OAKDALE4 | VL |  |  |  |  | 0.8773 | 0.9936 | 0.92 | 1.05 | 361 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
206857 | 15S | Approved | P3 | 37 | PNPRARIE 4 | VL |  |  |  |  | 0.8682 | 1.0068 | 0.92 | 1.05 | 361 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
206858 | 15S | Approved | P3 | 37 | WSTBAY 4 | VL |  |  |  |  | 0.8891 | 0.9929 | 0.92 | 1.05 | 361 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
206859 | 15S | Approved | P3 | 37 | 4VEAZIE | VL |  |  |  |  | 0.8928 | 0.9773 | 0.92 | 1.05 | 362 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206860 | 15S | Approved | P3 | 37 | GUIDRY 4 | VL |  |  |  |  | 0.8915 | 0.9761 | 0.92 | 1.05 | 362 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206861 | 15S | Approved | P3 | 37 | PLAISAN4 | VL |  |  |  |  | 0.9065 | 0.9897 | 0.92 | 1.05 | 362 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206862 | 15S | Approved | P3 | 37 | 4VEAZIE | VL |  |  |  |  | 0.8921 | 0.9773 | 0.92 | 1.05 | 363 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206863 | 15S | Approved | P3 | 37 | GUIDRY 4 | VL |  |  |  |  | 0.8907 | 0.9761 | 0.92 | 1.05 | 363 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206864 | 15S | Approved | P3 | 37 | PLAISAN4 | VL |  |  |  |  | 0.9058 | 0.9897 | 0.92 | 1.05 | 363 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206874 | 15S | Approved | P3 | 37 | 4VEAZIE | VL |  |  |  |  | 0.8916 | 0.9773 | 0.92 | 1.05 | 367 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206875 | 15S | Approved | P3 | 37 | GUIDRY 4 | VL |  |  |  |  | 0.8903 | 0.9761 | 0.92 | 1.05 | 367 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206876 | 15S | Approved | P3 | 37 | PLAISAN4 | VL |  |  |  |  | 0.9053 | 0.9897 | 0.92 | 1.05 | 367 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
206877 | 15S | Approved | P3 | 37 | IPAPER 4 | VL |  |  |  |  | 0.9104 | 0.9802 | 0.92 | 1.05 | 376 | P1_2-1656_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 500430 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project External |  | Messick 500/230
206878 | 15S | Approved | P3 | 37 | IPAPER 4 | VL |  |  |  |  | 0.9142 | 0.9802 | 0.92 | 1.05 | 377 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 500430 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project External |  | Messick 500/230
206879 | 15S | Approved | P3 | 37 | IPAPER 4 | VL |  |  |  |  | 0.9142 | 0.9802 | 0.92 | 1.05 | 378 | P1_2-1656_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 500430 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project External |  | Messick 500/230
206880 | 15S | Approved | P3 | 37 | IPAPER 4 | VL |  |  |  |  | 0.9138 | 0.9802 | 0.92 | 1.05 | 379 | P1_2-1656_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 500430 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project External |  | Messick 500/230
206881 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9193 | 0.9878 | 0.92 | 1.05 | 444 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 | turn on switch shunt at BEADLE 230kV sub
206882 | 15S | Approved | P3 | 37 | BEADLE 6 | VL |  |  |  |  | 0.9199 | 0.9889 | 0.92 | 1.05 | 444 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1
206883 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9198 | 0.9878 | 0.92 | 1.05 | 445 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
206884 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9198 | 0.9878 | 0.92 | 1.05 | 446 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
206885 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9033 | 0.9878 | 0.92 | 1.05 | 447 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+69 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
206886 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9034 | 0.9878 | 0.92 | 1.05 | 448 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+173 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | Facility: Radial
206887 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9032 | 0.9878 | 0.92 | 1.05 | 449 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
206888 | 15S | Approved | P3 | 37 | ELKS 6 | VL |  |  |  |  | 0.9032 | 0.9878 | 0.92 | 1.05 | 450 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
206889 | 15S | Approved | P3 | 37 | 4STALEY! | VL |  |  |  |  | 0.9101 | 0.9904 | 0.92 | 1.05 | 459 | G_4RAYBURN% ID 1+P1_2-147_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-147_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
206890 | 15S | Approved | P3 | 37 | 4MAGROVE | VL |  |  |  |  | 0.9196 | 0.9904 | 0.92 | 1.05 | 459 | G_4RAYBURN% ID 1+P1_2-147_4RIVTRIN%,4STALEY! | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-147_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
206891 | 15S | Approved | P3 | 37 | 4KIRBY | VL |  |  |  |  | 0.9129 | 0.9942 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206892 | 15S | Approved | P3 | 37 | 4CALL! | VL |  |  |  |  | 0.909 | 0.9951 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206893 | 15S | Approved | P3 | 37 | 4NBUNA | VL |  |  |  |  | 0.9033 | 0.9989 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334304 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206894 | 15S | Approved | P3 | 37 | 4BUNASW | VL |  |  |  |  | 0.9033 | 0.9989 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334305 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206895 | 15S | Approved | P3 | 37 | 4TEMPLE | VL |  |  |  |  | 0.9033 | 0.9989 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334306 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206896 | 15S | Approved | P3 | 37 | 4BUNA! | VL |  |  |  |  | 0.9026 | 1.0006 | 0.92 | 1.05 | 460 | G_4RAYBURN% ID 1+P1_2-241_4BUNA!,4EVADALE! | 334307 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-241_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
206897 | 15S | Approved | P3 | 37 | 2DEWEYVL! | VL |  |  |  |  | 0.9179 | 0.9814 | 0.92 | 1.05 | 461 | G_4RAYBURN% ID 1+P1_2-408_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-408_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
206898 | 15S | Approved | P3 | 37 | 2SKBVREG | VL |  |  |  |  | 0.9196 | 0.9831 | 0.92 | 1.05 | 461 | G_4RAYBURN% ID 1+P1_2-408_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-408_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
206899 | 15S | Approved | P3 | 37 | 2NECHESO | VL |  |  |  |  | 0.9137 | 0.9433 | 0.92 | 1.05 | 464 | G_1EXXONGT1! ID 1+P1_2-287_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-287_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
206900 | 15S | Approved | P3 | 37 | 2NECHESO | VL |  |  |  |  | 0.9133 | 0.9433 | 0.92 | 1.05 | 465 | G_1EXXONGT1! ID 1+P1_2-288_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-288_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
206901 | 15S | Approved | P3 | 37 | 2NECHESO | VL |  |  |  |  | 0.9153 | 0.9433 | 0.92 | 1.05 | 466 | G_1EXXONGT1! ID 1+P1_2-293_4UNION!,4STONGAT! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-293_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 |  | Facility: Radial
206902 | 15S | Approved | P3 | 37 | 2NECHESO | VL |  |  |  |  | 0.913 | 0.9433 | 0.92 | 1.05 | 467 | G_1EXXONGT1! ID 1+P1_2-294_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
206903 | 15S | Approved | P3 | 37 | 2HIMEX | VH |  |  |  |  | 1.0509 | 1.0241 | 0.92 | 1.05 | 470 | G_1G3SABIN! ID 1+P1_2-223_2STOWELL!,2WINSHIR! | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-223_2STOWELL!,2WINSHIR! | G_1G3SABIN! ID 1 |  | VH
206904 | 15S | Approved | P3 | 37 | 3SMACKOVER | VL |  |  |  |  | 0.9194 | 1.0153 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337536 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206905 | 15S | Approved | P3 | 37 | 3SMACKOVER+ | VL |  |  |  |  | 0.9194 | 1.0175 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337537 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206906 | 15S | Approved | P3 | 37 | 3HAYS CITY | VL |  |  |  |  | 0.9168 | 1.0152 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337538 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206907 | 15S | Approved | P3 | 37 | 3EL DORADO! | VL |  |  |  |  | 0.9199 | 1.0281 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337539 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206908 | 15S | Approved | P3 | 37 | 3ELD DONAN | VL |  |  |  |  | 0.9181 | 1.0234 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337540 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206909 | 15S | Approved | P3 | 37 | 3T.E.P/S-ELD | VL |  |  |  |  | 0.9177 | 1.0231 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337541 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206910 | 15S | Approved | P3 | 37 | 3ELD MONSNTO | VL |  |  |  |  | 0.9194 | 1.021 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337542 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206911 | 15S | Approved | P3 | 37 | 3ELD LION | VL |  |  |  |  | 0.9182 | 1.0155 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337551 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206912 | 15S | Approved | P3 | 37 | 3ELD JACKSON | VL |  |  |  |  | 0.9177 | 1.0161 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337552 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206913 | 15S | Approved | P3 | 37 | 3ELDORADO.E! | VL |  |  |  |  | 0.9193 | 1.02 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337553 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206914 | 15S | Approved | P3 | 37 | 3T.E.P/S-F | VL |  |  |  |  | 0.9162 | 1.013 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337555 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206915 | 15S | Approved | P3 | 37 | 3ELD QUINN | VL |  |  |  |  | 0.92 | 1.0281 | 0.92 | 1.05 | 504 | G_1MCCLELAN U1 ID 1+1502 | 337560 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1270_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
206916 | 15S | Approved | P3 | 37 | MAURICE2 | VL |  |  |  |  | 0.9137 | 0.9898 | 0.92 | 1.05 | 509 | G_G1WKRAFT! ID 3+P1_2-1166_6MONTGOMERY!,CLARN 6! | 500565 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1WKRAFT! ID 3 | Project External |  | Messick 500/230
206917 | 15S | Approved | P3 | 37 | 4LEBLANC! | VL |  |  |  |  | 0.9185 | 0.9703 | 0.92 | 1.05 | 515 | G_G3TECHE! ID 1+P1_2-113_4LEBLANC!,4MORIL! | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Proposed |  | 14-EGL-006-CP | 2017-06-01 | Install 25.1 Mvar capacitor bank #1 at LeBlanc 138 kV
206918 | 23S | Approved | P0 | 38 | 5HORN LAKE% | VH |  |  |  |  | 1.0564 | 1.0564 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
206919 | 23S | Approved | P3 | 38 | 4LEBLANC! | VL |  |  |  |  | 0.8918 | 0.9588 | 0.92 | 1.05 | 1 | P1_2-113_4LEBLANC!,4MORIL!+G_1WAT U3! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
206920 | 23S | Approved | P3 | 38 | 4LEBLANC! | VL |  |  |  |  | 0.8818 | 0.9588 | 0.92 | 1.05 | 2 | P1_2-113_4LEBLANC!,4MORIL!+G_G3TECHE! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
206921 | 23S | Approved | P3 | 38 | 4ABBEVILLE | VL |  |  |  |  | 0.9132 | 0.9638 | 0.92 | 1.05 | 2 | P1_2-113_4LEBLANC!,4MORIL!+G_G3TECHE! ID 1 | 335386 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
206922 | 23S | Approved | P3 | 38 | ABBEVL 4 | VL |  |  |  |  | 0.9132 | 0.9638 | 0.92 | 1.05 | 2 | P1_2-113_4LEBLANC!,4MORIL!+G_G3TECHE! ID 1 | 500010 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
206923 | 23S | Approved | P3 | 38 | 4LEBLANC! | VL |  |  |  |  | 0.8901 | 0.9588 | 0.92 | 1.05 | 3 | P1_2-113_4LEBLANC!,4MORIL!+G_G1 ACAD! ID 1 | 303150 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-113_4LEBLANC!,4MORIL! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-012-HZ | 2022-06-01 | Install 25.1 Mvar capacitor bank #2 at LeBlanc 138 kV
206935 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.8556 | 0.9642 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206936 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.8693 | 0.964 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206937 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.8857 | 0.9666 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206938 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.8838 | 0.9649 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206939 | 23S | Approved | P3 | 38 | 46L533TP8 | VL |  |  |  |  | 0.907 | 0.9719 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206940 | 23S | Approved | P3 | 38 | 4KLMP-EX | VL |  |  |  |  | 0.907 | 0.9719 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206941 | 23S | Approved | P3 | 38 | 4ROLKERD | VL |  |  |  |  | 0.9107 | 0.9728 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206942 | 23S | Approved | P3 | 38 | 4ADAYTON! | VL |  |  |  |  | 0.9106 | 0.9727 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206943 | 23S | Approved | P3 | 38 | 4BDAYTON! | VL |  |  |  |  | 0.9106 | 0.9727 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206944 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9117 | 0.9661 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206945 | 23S | Approved | P3 | 38 | 4GORDON | VL |  |  |  |  | 0.9105 | 0.9727 | 0.92 | 1.05 | 6 | P1_2-182_4PORTER%,4NEWCANY!+G_1G1LEWIS! ID 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206946 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.8563 | 0.9642 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206947 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.87 | 0.964 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206948 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.8863 | 0.9666 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206949 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.8844 | 0.9649 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206950 | 23S | Approved | P3 | 38 | 46L533TP8 | VL |  |  |  |  | 0.9075 | 0.9719 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206951 | 23S | Approved | P3 | 38 | 4KLMP-EX | VL |  |  |  |  | 0.9075 | 0.9719 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206952 | 23S | Approved | P3 | 38 | 4ROLKERD | VL |  |  |  |  | 0.9112 | 0.9728 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206953 | 23S | Approved | P3 | 38 | 4ADAYTON! | VL |  |  |  |  | 0.9111 | 0.9727 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206954 | 23S | Approved | P3 | 38 | 4BDAYTON! | VL |  |  |  |  | 0.9111 | 0.9727 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206955 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9123 | 0.9661 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
206956 | 23S | Approved | P3 | 38 | 4GORDON | VL |  |  |  |  | 0.911 | 0.9727 | 0.92 | 1.05 | 7 | P1_2-182_4PORTER%,4NEWCANY!+G_1G2LEWIS! ID 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207012 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.8562 | 0.9642 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207013 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.8698 | 0.964 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207014 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.8861 | 0.9666 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207015 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.8843 | 0.9649 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207016 | 23S | Approved | P3 | 38 | 46L533TP8 | VL |  |  |  |  | 0.9074 | 0.9719 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207017 | 23S | Approved | P3 | 38 | 4KLMP-EX | VL |  |  |  |  | 0.9074 | 0.9719 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207018 | 23S | Approved | P3 | 38 | 4ROLKERD | VL |  |  |  |  | 0.911 | 0.9728 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207019 | 23S | Approved | P3 | 38 | 4ADAYTON! | VL |  |  |  |  | 0.9109 | 0.9727 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207020 | 23S | Approved | P3 | 38 | 4BDAYTON! | VL |  |  |  |  | 0.911 | 0.9727 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207021 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9129 | 0.9661 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207022 | 23S | Approved | P3 | 38 | 4GORDON | VL |  |  |  |  | 0.9108 | 0.9727 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207023 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9156 | 0.9396 | 0.92 | 1.05 | 13 | P1_2-182_4PORTER%,4NEWCANY!+G_1EXXONGT1! ID 1 | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1EXXONGT1! ID 1 |  | Facility: Radial
207024 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.8588 | 0.9642 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207025 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.8723 | 0.964 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207026 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.8885 | 0.9666 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207027 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.8867 | 0.9649 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207028 | 23S | Approved | P3 | 38 | 46L533TP8 | VL |  |  |  |  | 0.9097 | 0.9719 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334115 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207029 | 23S | Approved | P3 | 38 | 4KLMP-EX | VL |  |  |  |  | 0.9097 | 0.9719 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334116 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207030 | 23S | Approved | P3 | 38 | 4ROLKERD | VL |  |  |  |  | 0.9133 | 0.9728 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334209 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207031 | 23S | Approved | P3 | 38 | 4ADAYTON! | VL |  |  |  |  | 0.9132 | 0.9727 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334210 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207032 | 23S | Approved | P3 | 38 | 4BDAYTON! | VL |  |  |  |  | 0.9133 | 0.9727 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334211 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207033 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9148 | 0.9661 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207034 | 23S | Approved | P3 | 38 | 4GORDON | VL |  |  |  |  | 0.9131 | 0.9727 | 0.92 | 1.05 | 14 | P1_2-182_4PORTER%,4NEWCANY!+G_1G4SABIN! ID 1 | 334216 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-182_4PORTER%,4NEWCANY! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207123 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9159 | 0.9858 | 0.92 | 1.05 | 23 | P1_2-204_6CHINA%,4CHINA%+G_1FRNTR 1! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1FRNTR 1! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207124 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.9145 | 1.001 | 0.92 | 1.05 | 23 | P1_2-204_6CHINA%,4CHINA%+G_1FRNTR 1! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1FRNTR 1! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207125 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9159 | 0.9858 | 0.92 | 1.05 | 24 | P1_2-204_6CHINA%,4CHINA%+G_1FRNTR 2! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1FRNTR 2! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207126 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.9145 | 1.001 | 0.92 | 1.05 | 24 | P1_2-204_6CHINA%,4CHINA%+G_1FRNTR 2! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1FRNTR 2! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207127 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9197 | 0.9649 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207128 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9073 | 0.9661 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207129 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.905 | 0.9752 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207130 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9005 | 0.9858 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207131 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.8991 | 1.001 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207132 | 23S | Approved | P3 | 38 | 4MAG AMS | VL |  |  |  |  | 0.9062 | 0.9744 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334217 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207133 | 23S | Approved | P3 | 38 | 45L541T43 | VL |  |  |  |  | 0.9075 | 0.9757 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334218 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207134 | 23S | Approved | P3 | 38 | 4SHILOH! | VL |  |  |  |  | 0.9135 | 0.978 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334219 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207135 | 23S | Approved | P3 | 38 | 4BRKSCRK | VL |  |  |  |  | 0.9171 | 0.9797 | 0.92 | 1.05 | 25 | P1_2-204_6CHINA%,4CHINA%+G_1G1LEWIS! ID 1 | 334220 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207136 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9199 | 0.9649 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207137 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9075 | 0.9661 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207138 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.9052 | 0.9752 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207139 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9007 | 0.9858 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207140 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.8993 | 1.001 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207141 | 23S | Approved | P3 | 38 | 4MAG AMS | VL |  |  |  |  | 0.9064 | 0.9744 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334217 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207142 | 23S | Approved | P3 | 38 | 45L541T43 | VL |  |  |  |  | 0.9077 | 0.9757 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334218 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207143 | 23S | Approved | P3 | 38 | 4SHILOH! | VL |  |  |  |  | 0.9137 | 0.978 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334219 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207144 | 23S | Approved | P3 | 38 | 4BRKSCRK | VL |  |  |  |  | 0.9173 | 0.9797 | 0.92 | 1.05 | 26 | P1_2-204_6CHINA%,4CHINA%+G_1G2LEWIS! ID 1 | 334220 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207149 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.9182 | 0.9752 | 0.92 | 1.05 | 29 | P1_2-204_6CHINA%,4CHINA%+G_1EXXONGT1! ID 1 | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1EXXONGT1! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207150 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9138 | 0.9858 | 0.92 | 1.05 | 29 | P1_2-204_6CHINA%,4CHINA%+G_1EXXONGT1! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207151 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.9124 | 1.001 | 0.92 | 1.05 | 29 | P1_2-204_6CHINA%,4CHINA%+G_1EXXONGT1! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207152 | 23S | Approved | P3 | 38 | 4MAG AMS | VL |  |  |  |  | 0.919 | 0.9744 | 0.92 | 1.05 | 29 | P1_2-204_6CHINA%,4CHINA%+G_1EXXONGT1! ID 1 | 334217 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1EXXONGT1! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207153 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9182 | 0.9396 | 0.92 | 1.05 | 29 | P1_2-204_6CHINA%,4CHINA%+G_1EXXONGT1! ID 1 | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1EXXONGT1! ID 1 |  | Facility: Radial
207154 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.9178 | 0.9752 | 0.92 | 1.05 | 30 | P1_2-204_6CHINA%,4CHINA%+G_1G4SABIN! ID 1 | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G4SABIN! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207155 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9134 | 0.9858 | 0.92 | 1.05 | 30 | P1_2-204_6CHINA%,4CHINA%+G_1G4SABIN! ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207156 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.912 | 1.001 | 0.92 | 1.05 | 30 | P1_2-204_6CHINA%,4CHINA%+G_1G4SABIN! ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207157 | 23S | Approved | P3 | 38 | 4MAG AMS | VL |  |  |  |  | 0.9183 | 0.9744 | 0.92 | 1.05 | 30 | P1_2-204_6CHINA%,4CHINA%+G_1G4SABIN! ID 1 | 334217 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G4SABIN! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207158 | 23S | Approved | P3 | 38 | 45L541T43 | VL |  |  |  |  | 0.9196 | 0.9757 | 0.92 | 1.05 | 30 | P1_2-204_6CHINA%,4CHINA%+G_1G4SABIN! ID 1 | 334218 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_1G4SABIN! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
207161 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9168 | 0.9858 | 0.92 | 1.05 | 32 | P1_2-204_6CHINA%,4CHINA%+G_PIRKEY 1 ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_PIRKEY 1 ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207162 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.9154 | 1.001 | 0.92 | 1.05 | 32 | P1_2-204_6CHINA%,4CHINA%+G_PIRKEY 1 ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_PIRKEY 1 ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207163 | 23S | Approved | P3 | 38 | 4DEVERS | VL |  |  |  |  | 0.9182 | 0.9858 | 0.92 | 1.05 | 33 | P1_2-204_6CHINA%,4CHINA%+G_WELSH2-1 ID 1 | 334214 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_WELSH2-1 ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207164 | 23S | Approved | P3 | 38 | 4CHINA% | VL |  |  |  |  | 0.9168 | 1.001 | 0.92 | 1.05 | 33 | P1_2-204_6CHINA%,4CHINA%+G_WELSH2-1 ID 1 | 334215 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-204_6CHINA%,4CHINA% | G_WELSH2-1 ID 1 | Project Proposed |  | 11-ETI-037-CP | 2018-06-01 | Construct China-Stowell 138 kV
207199 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8725 | 0.9941 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207200 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8617 | 0.9758 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207201 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8566 | 0.9717 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207202 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8545 | 0.97 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207203 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8657 | 0.9838 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207204 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8752 | 0.9839 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207205 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8732 | 0.9822 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207206 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8728 | 0.9819 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207207 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8729 | 0.982 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207208 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8727 | 0.9818 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207209 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8728 | 0.9819 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207210 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8606 | 0.9719 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207211 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8838 | 0.9925 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207212 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9 | 0.9914 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207213 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9135 | 0.9913 | 0.92 | 1.05 | 40 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G1LEWIS! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207214 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8728 | 0.9941 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207215 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.862 | 0.9758 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207216 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.857 | 0.9717 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207217 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8549 | 0.97 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207218 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.866 | 0.9838 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207219 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8756 | 0.9839 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207220 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8736 | 0.9822 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207221 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8732 | 0.9819 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207222 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8733 | 0.982 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207223 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8731 | 0.9818 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207224 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8732 | 0.9819 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207225 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.861 | 0.9719 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207226 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8841 | 0.9925 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207227 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9003 | 0.9914 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207228 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9138 | 0.9913 | 0.92 | 1.05 | 41 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G2LEWIS! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207229 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8792 | 0.9941 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207230 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8688 | 0.9758 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207231 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8638 | 0.9717 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207232 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8617 | 0.97 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207233 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8726 | 0.9838 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207234 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8826 | 0.9839 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207235 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8806 | 0.9822 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207236 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8802 | 0.9819 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207237 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8803 | 0.982 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207238 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8801 | 0.9818 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207239 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8802 | 0.9819 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207240 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8682 | 0.9719 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207241 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8903 | 0.9925 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207242 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9062 | 0.9914 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207243 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9195 | 0.9913 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U1! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207244 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8792 | 0.9941 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207245 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8688 | 0.9758 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207246 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8638 | 0.9717 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207247 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8617 | 0.97 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207248 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8726 | 0.9838 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207249 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8826 | 0.9839 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207250 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8806 | 0.9822 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207251 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8802 | 0.9819 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207252 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8803 | 0.982 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207253 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8801 | 0.9818 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207254 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8802 | 0.9819 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207255 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8682 | 0.9719 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207256 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8903 | 0.9925 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207257 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9062 | 0.9914 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207258 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9195 | 0.9913 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CYPR U2! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CYPR U2! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207259 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8671 | 0.9941 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207260 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8563 | 0.9758 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207261 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8513 | 0.9717 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207262 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8492 | 0.97 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207263 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8603 | 0.9838 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207264 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8697 | 0.9839 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207265 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8677 | 0.9822 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207266 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8673 | 0.9819 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207267 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8674 | 0.982 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207268 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8672 | 0.9818 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207269 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8673 | 0.9819 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207270 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8554 | 0.9719 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207271 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8786 | 0.9925 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207272 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.8949 | 0.9914 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207273 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9085 | 0.9913 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207274 | 23S | Approved | P3 | 38 | 4CALL! | VL |  |  |  |  | 0.9188 | 0.9921 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207275 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.919 | 0.9396 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 |  | Facility: Radial
207276 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8794 | 0.9941 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207277 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8691 | 0.9758 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207278 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8641 | 0.9717 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207279 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.862 | 0.97 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207280 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8728 | 0.9838 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207281 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8828 | 0.9839 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207282 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8809 | 0.9822 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207283 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8805 | 0.9819 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207284 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8806 | 0.982 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207285 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8804 | 0.9818 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207286 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8805 | 0.9819 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207287 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8684 | 0.9719 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207288 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8905 | 0.9925 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207289 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9064 | 0.9914 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207290 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9197 | 0.9913 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G3SABIN! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G3SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207291 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8724 | 0.9941 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207292 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8619 | 0.9758 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207293 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.857 | 0.9717 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207294 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8549 | 0.97 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207295 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8658 | 0.9838 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207296 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8755 | 0.9839 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207297 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8735 | 0.9822 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207298 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8732 | 0.9819 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207299 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8732 | 0.982 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207300 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8731 | 0.9818 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207301 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8732 | 0.9819 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207302 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8614 | 0.9719 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207303 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8837 | 0.9925 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207304 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.8998 | 0.9914 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207305 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9132 | 0.9913 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G4SABIN! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G4SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207306 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8788 | 0.9941 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207307 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.8686 | 0.9758 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207308 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8637 | 0.9717 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207309 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.8617 | 0.97 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207310 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8723 | 0.9838 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207311 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8824 | 0.9839 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207312 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8805 | 0.9822 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207313 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8801 | 0.9819 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207314 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8802 | 0.982 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207315 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.88 | 0.9818 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207316 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8801 | 0.9819 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207317 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8684 | 0.9719 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207318 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8899 | 0.9925 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207319 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9058 | 0.9914 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207320 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.919 | 0.9913 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%,4MILLCR!+G_1G5SABIN! ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1G5SABIN! ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207321 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.8786 | 0.9941 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207322 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.868 | 0.9758 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207323 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.8631 | 0.9717 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207324 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.861 | 0.97 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207325 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.8719 | 0.9838 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207326 | 23S | Approved | P3 | 38 | 2PINELND | VL |  |  |  |  | 0.8817 | 0.9839 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207327 | 23S | Approved | P3 | 38 | 2TEMPL1* | VL |  |  |  |  | 0.8797 | 0.9822 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207328 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.8793 | 0.9819 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207329 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.8794 | 0.982 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207330 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.8792 | 0.9818 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207331 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.8793 | 0.9819 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207332 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.8673 | 0.9719 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207333 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.8898 | 0.9925 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207334 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.9058 | 0.9914 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207335 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.9191 | 0.9913 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
207338 | 23S | Approved | P3 | 38 | 3ASHLAND | VL |  |  |  |  | 0.8954 | 1.0143 | 0.92 | 1.05 | 75 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 303205 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
207339 | 23S | Approved | P3 | 38 | 3HOUMA! | VL |  |  |  |  | 0.8973 | 1.0141 | 0.92 | 1.05 | 75 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 336035 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
207340 | 23S | Approved | P3 | 38 | 3CHAVIN! | VL |  |  |  |  | 0.9195 | 1.0255 | 0.92 | 1.05 | 75 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 336036 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
207341 | 23S | Approved | P3 | 38 | HOUMA 3 | VL |  |  |  |  | 0.8973 | 1.0141 | 0.92 | 1.05 | 75 | P1_2-802_3COTEAU!,3HOUMA!+G_HOUMA 3 ID 1 | 503305 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-802_3COTEAU!,3HOUMA! | G_HOUMA 3 ID 1 |  | Solution: Adjust caps
207342 | 23S | Approved | P3 | 38 | 3CLAYTN! | VL |  |  |  |  | 0.9122 | 0.9847 | 0.92 | 1.05 | 76 | P1_2-924_3GYPSY%,3CLAYTN!+G_1GYP U3! ID 1 | 336230 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1GYP U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
207343 | 23S | Approved | P3 | 38 | 3NORCO% | VL |  |  |  |  | 0.913 | 0.9819 | 0.92 | 1.05 | 76 | P1_2-924_3GYPSY%,3CLAYTN!+G_1GYP U3! ID 1 | 336231 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1GYP U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
207344 | 23S | Approved | P3 | 38 | 3CLAYTN! | VL |  |  |  |  | 0.9152 | 0.9847 | 0.92 | 1.05 | 77 | P1_2-924_3GYPSY%,3CLAYTN!+G_1MICH U3! ID 1 | 336230 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1MICH U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
207345 | 23S | Approved | P3 | 38 | 3NORCO% | VL |  |  |  |  | 0.916 | 0.9819 | 0.92 | 1.05 | 77 | P1_2-924_3GYPSY%,3CLAYTN!+G_1MICH U3! ID 1 | 336231 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-924_3GYPSY%,3CLAYTN! | G_1MICH U3! ID 1 | Project Proposed |  | 14-ELL-001-CP | 2017-06-01 | Install 30.5 Mvar capacitor bank at Norco 115 kV
207346 | 23S | Approved | P3 | 38 | 3BASKIN | VL |  |  |  |  | 0.903 | 0.9452 | 0.92 | 1.05 | 78 | P1_2-1176_3RED_GUM!,3WINNSBORO!+G_1ANDRUS U1 ID 1 | 303325 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1176_3RED_GUM!,3WINNSBORO! | G_1ANDRUS U1 ID 1 | turn switch shunt at Winnsbord 115kV sub
207347 | 23S | Approved | P3 | 38 | 3WINNSBORO! | VL |  |  |  |  | 0.892 | 0.9426 | 0.92 | 1.05 | 78 | P1_2-1176_3RED_GUM!,3WINNSBORO!+G_1ANDRUS U1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1176_3RED_GUM!,3WINNSBORO! | G_1ANDRUS U1 ID 1 | turn switch shunt at Winnsbord 115kV sub
207348 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9136 | 0.9823 | 0.92 | 1.05 | 79 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1WKRAFT! ID 3 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1WKRAFT! ID 3
207349 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9166 | 0.9911 | 0.92 | 1.05 | 79 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1WKRAFT! ID 3 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1WKRAFT! ID 3 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207350 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9152 | 0.9898 | 0.92 | 1.05 | 79 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1WKRAFT! ID 3 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1WKRAFT! ID 3 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207351 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9064 | 0.9823 | 0.92 | 1.05 | 80 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1DOLHIL! ID 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1
207352 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9096 | 0.9911 | 0.92 | 1.05 | 80 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1DOLHIL! ID 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207353 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9081 | 0.9898 | 0.92 | 1.05 | 80 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_G1DOLHIL! ID 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_G1DOLHIL! ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207354 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9139 | 0.9823 | 0.92 | 1.05 | 81 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_PIRKEY 1 ID 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_PIRKEY 1 ID 1
207355 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9173 | 0.9911 | 0.92 | 1.05 | 81 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_PIRKEY 1 ID 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207356 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9158 | 0.9898 | 0.92 | 1.05 | 81 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_PIRKEY 1 ID 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_PIRKEY 1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207357 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9151 | 0.9823 | 0.92 | 1.05 | 82 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH2-1 ID 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH2-1 ID 1
207358 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9184 | 0.9911 | 0.92 | 1.05 | 82 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH2-1 ID 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH2-1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207359 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9169 | 0.9898 | 0.92 | 1.05 | 82 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH2-1 ID 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH2-1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207360 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9151 | 0.9823 | 0.92 | 1.05 | 83 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH3-1 ID 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH3-1 ID 1
207361 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9184 | 0.9911 | 0.92 | 1.05 | 83 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH3-1 ID 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH3-1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207362 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9169 | 0.9898 | 0.92 | 1.05 | 83 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_WELSH3-1 ID 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_WELSH3-1 ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207363 | 23S | Approved | P3 | 38 | 3MINDEN_LG | VL |  |  |  |  | 0.9153 | 0.9823 | 0.92 | 1.05 | 84 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_TURKCOAL ID 1 | 303302 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_TURKCOAL ID 1
207364 | 23S | Approved | P3 | 38 | 3MINDEN_LA! | VL |  |  |  |  | 0.9186 | 0.9911 | 0.92 | 1.05 | 84 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_TURKCOAL ID 1 | 337361 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_TURKCOAL ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207365 | 23S | Approved | P3 | 38 | 3LA_ORD_PLNT | VL |  |  |  |  | 0.9172 | 0.9898 | 0.92 | 1.05 | 84 | P1_2-1192_3MINDEN_LA!,3SAREPTA!+G_TURKCOAL ID 1 | 337362 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1192_3MINDEN_LA!,3SAREPTA! | G_TURKCOAL ID 1 | Project Proposed |  | 13-ELL-004-CP | 2015-06-01 | Install capacitor bank at Minden REA 115 kV
207462 | 23S | Approved | P3 | 38 | 3DELHI_LA! | VL |  |  |  |  | 0.8635 | 0.9792 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207463 | 23S | Approved | P3 | 38 | 3OAK_RIDGE | VL |  |  |  |  | 0.8366 | 0.9757 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207464 | 23S | Approved | P3 | 38 | 3CARSON | VL |  |  |  |  | 0.8359 | 0.9714 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207465 | 23S | Approved | P3 | 38 | 3SACKSONIA | VL |  |  |  |  | 0.8327 | 0.9687 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207466 | 23S | Approved | P3 | 38 | 3DUNN! | VL |  |  |  |  | 0.8353 | 0.9717 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207467 | 23S | Approved | P3 | 38 | 3DELHI_RX | VL |  |  |  |  | 0.8499 | 0.9746 | 0.92 | 1.05 | 122 | P1_2-1215_3SWARTZ!,3DUNN!+G_1B.WLSN U2 ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1B.WLSN U2 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207480 | 23S | Approved | P3 | 38 | 3DELHI_LA! | VL |  |  |  |  | 0.8797 | 0.9792 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207481 | 23S | Approved | P3 | 38 | 3OAK_RIDGE | VL |  |  |  |  | 0.8551 | 0.9757 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207482 | 23S | Approved | P3 | 38 | 3CARSON | VL |  |  |  |  | 0.8538 | 0.9714 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207483 | 23S | Approved | P3 | 38 | 3SACKSONIA | VL |  |  |  |  | 0.8508 | 0.9687 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207484 | 23S | Approved | P3 | 38 | 3DUNN! | VL |  |  |  |  | 0.8533 | 0.9717 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207485 | 23S | Approved | P3 | 38 | 3DELHI_RX | VL |  |  |  |  | 0.8673 | 0.9746 | 0.92 | 1.05 | 125 | P1_2-1215_3SWARTZ!,3DUNN!+G_1HINDS S1 ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1HINDS S1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207486 | 23S | Approved | P3 | 38 | 3DELHI_LA! | VL |  |  |  |  | 0.8791 | 0.9792 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207487 | 23S | Approved | P3 | 38 | 3OAK_RIDGE | VL |  |  |  |  | 0.8543 | 0.9757 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207488 | 23S | Approved | P3 | 38 | 3CARSON | VL |  |  |  |  | 0.8531 | 0.9714 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207489 | 23S | Approved | P3 | 38 | 3SACKSONIA | VL |  |  |  |  | 0.85 | 0.9687 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207490 | 23S | Approved | P3 | 38 | 3DUNN! | VL |  |  |  |  | 0.8526 | 0.9717 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207491 | 23S | Approved | P3 | 38 | 3DELHI_RX | VL |  |  |  |  | 0.8665 | 0.9746 | 0.92 | 1.05 | 126 | P1_2-1215_3SWARTZ!,3DUNN!+G_3YAZOO MUNI ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3YAZOO MUNI ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207510 | 23S | Approved | P3 | 38 | 3DELHI_LA! | VL |  |  |  |  | 0.8707 | 0.9792 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207511 | 23S | Approved | P3 | 38 | 3OAK_RIDGE | VL |  |  |  |  | 0.8453 | 0.9757 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207512 | 23S | Approved | P3 | 38 | 3CARSON | VL |  |  |  |  | 0.8442 | 0.9714 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207513 | 23S | Approved | P3 | 38 | 3SACKSONIA | VL |  |  |  |  | 0.8411 | 0.9687 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207514 | 23S | Approved | P3 | 38 | 3DUNN! | VL |  |  |  |  | 0.8437 | 0.9717 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207515 | 23S | Approved | P3 | 38 | 3DELHI_RX | VL |  |  |  |  | 0.8578 | 0.9746 | 0.92 | 1.05 | 130 | P1_2-1215_3SWARTZ!,3DUNN!+G_1ANDRUS U1 ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_1ANDRUS U1 ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207516 | 23S | Approved | P3 | 38 | 3DELHI_LA! | VL |  |  |  |  | 0.8793 | 0.9792 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337448 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207517 | 23S | Approved | P3 | 38 | 3OAK_RIDGE | VL |  |  |  |  | 0.8546 | 0.9757 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337449 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207518 | 23S | Approved | P3 | 38 | 3CARSON | VL |  |  |  |  | 0.8534 | 0.9714 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337450 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207519 | 23S | Approved | P3 | 38 | 3SACKSONIA | VL |  |  |  |  | 0.8503 | 0.9687 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337451 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207520 | 23S | Approved | P3 | 38 | 3DUNN! | VL |  |  |  |  | 0.8529 | 0.9717 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337452 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207521 | 23S | Approved | P3 | 38 | 3DELHI_RX | VL |  |  |  |  | 0.8668 | 0.9746 | 0.92 | 1.05 | 131 | P1_2-1215_3SWARTZ!,3DUNN!+G_3GREENWOOD! ID 1 | 337453 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1215_3SWARTZ!,3DUNN! | G_3GREENWOOD! ID 1 |  | Model: Sterlington-Oak Ridge 115 kV should be closed after Approved project 11-ELL-003-02-CP
207569 | 23S | Approved | P3 | 38 | 3PINEBLUF.E% | VL |  |  |  |  | 0.9192 | 0.9495 | 0.92 | 1.05 | 140 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1LYNCH U3 ID 1 | 337624 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_3WHT BLUFF!,8WHT BLUFF% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
207570 | 23S | Approved | P3 | 38 | 3PB IP SS% | VL |  |  |  |  | 0.913 | 0.9435 | 0.92 | 1.05 | 140 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1LYNCH U3 ID 1 | 337627 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_3WHT BLUFF!,8WHT BLUFF% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
207571 | 23S | Approved | P3 | 38 | 3PB IP! | VL |  |  |  |  | 0.9124 | 0.9429 | 0.92 | 1.05 | 140 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1LYNCH U3 ID 1 | 337628 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_3WHT BLUFF!,8WHT BLUFF% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
207572 | 23S | Approved | P3 | 38 | 3PB PORT | VL |  |  |  |  | 0.9125 | 0.943 | 0.92 | 1.05 | 140 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1LYNCH U3 ID 1 | 337629 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_3WHT BLUFF!,8WHT BLUFF% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
207573 | 23S | Approved | P3 | 38 | 3PB ENERGY! | VL |  |  |  |  | 0.9124 | 0.9429 | 0.92 | 1.05 | 140 | P1_2-1313_3WHT BLUFF!,8WHT BLUFF%+G_1LYNCH U3 ID 1 | 337630 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1313_3WHT BLUFF!,8WHT BLUFF% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-008-CP | 2015-06-01 | Construct Woodward 230 kV ring bus; construct White Bluff-Woodward 230 kV line (Pine Bluff Voltage S
207588 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9188 | 0.9714 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207589 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9042 | 0.9877 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207590 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.902 | 0.9858 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207591 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9043 | 0.9927 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207592 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9038 | 0.9876 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207593 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9114 | 0.9867 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207594 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9014 | 0.9755 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207595 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9029 | 0.966 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207596 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9138 | 0.9642 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207597 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9095 | 0.9783 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207598 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9082 | 0.9628 | 0.92 | 1.05 | 306 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ANDRUS U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207599 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9194 | 0.9714 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207600 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9049 | 0.9877 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207601 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9027 | 0.9858 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207602 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.905 | 0.9927 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207603 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9045 | 0.9876 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207604 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9122 | 0.9867 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207605 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9022 | 0.9755 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207606 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9036 | 0.966 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207607 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9146 | 0.9642 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207608 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.91 | 0.9783 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207609 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.909 | 0.9628 | 0.92 | 1.05 | 307 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+108 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207610 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9194 | 0.9714 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207611 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9049 | 0.9877 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207612 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9027 | 0.9858 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207613 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.905 | 0.9927 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207614 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9045 | 0.9876 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207615 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9122 | 0.9867 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207616 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9022 | 0.9755 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207617 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9036 | 0.966 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207618 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9146 | 0.9642 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207619 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.91 | 0.9783 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207620 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.909 | 0.9628 | 0.92 | 1.05 | 308 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+109 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G2 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207621 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9194 | 0.9714 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207622 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9049 | 0.9877 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207623 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9027 | 0.9858 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207624 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.905 | 0.9927 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207625 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9045 | 0.9876 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207626 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9122 | 0.9867 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207627 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9022 | 0.9755 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207628 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9036 | 0.966 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207629 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9146 | 0.9642 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207630 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.91 | 0.9783 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207631 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.909 | 0.9628 | 0.92 | 1.05 | 309 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+110 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207632 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9194 | 0.9714 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207633 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9049 | 0.9877 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207634 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9027 | 0.9858 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207635 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.905 | 0.9927 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207636 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9045 | 0.9876 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207637 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9122 | 0.9867 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207638 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9022 | 0.9755 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207639 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9036 | 0.966 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207640 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9146 | 0.9642 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207641 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.91 | 0.9783 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207642 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.909 | 0.9628 | 0.92 | 1.05 | 310 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+111 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CROSSRDS G4 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207643 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9193 | 0.9714 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207644 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9047 | 0.9877 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207645 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9025 | 0.9858 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207646 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9048 | 0.9927 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207647 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9043 | 0.9876 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207648 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9119 | 0.9867 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207649 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9019 | 0.9755 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207650 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9033 | 0.966 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207651 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9142 | 0.9642 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207652 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9099 | 0.9783 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207653 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9087 | 0.9628 | 0.92 | 1.05 | 311 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1SLSBAU3 ID 5 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207654 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9184 | 0.9714 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207655 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9037 | 0.9877 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207656 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9015 | 0.9858 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207657 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9038 | 0.9927 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207658 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9033 | 0.9876 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207659 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.911 | 0.9867 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207660 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9009 | 0.9755 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207661 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9023 | 0.966 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207662 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9132 | 0.9642 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207663 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9089 | 0.9783 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207664 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9076 | 0.9628 | 0.92 | 1.05 | 312 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1CLSBAU3 ID 6 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207665 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9193 | 0.9714 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207666 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9047 | 0.9877 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207667 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9026 | 0.9858 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207668 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9048 | 0.9927 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207669 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9043 | 0.9876 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207670 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9119 | 0.9867 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207671 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.902 | 0.9755 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207672 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9034 | 0.966 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207673 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9144 | 0.9642 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207674 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9099 | 0.9783 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207675 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9088 | 0.9628 | 0.92 | 1.05 | 313 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1LYNCH U3 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207676 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9199 | 0.9714 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207677 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9059 | 0.9877 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207678 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9037 | 0.9858 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207679 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9061 | 0.9927 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207680 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9057 | 0.9876 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207681 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9134 | 0.9867 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207682 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9035 | 0.9755 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207683 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.905 | 0.966 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207684 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.916 | 0.9642 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207685 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9107 | 0.9783 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207686 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9104 | 0.9628 | 0.92 | 1.05 | 314 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207687 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9197 | 0.9714 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207688 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9051 | 0.9877 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207689 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9029 | 0.9858 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207690 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9053 | 0.9927 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207691 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9048 | 0.9876 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207692 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9124 | 0.9867 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207693 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9024 | 0.9755 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207694 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9039 | 0.966 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207695 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9148 | 0.9642 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207696 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9103 | 0.9783 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207697 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9092 | 0.9628 | 0.92 | 1.05 | 315 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1PLUM PT U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207698 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.918 | 0.9714 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207699 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9029 | 0.9877 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207700 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9007 | 0.9858 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207701 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9029 | 0.9927 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207702 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9024 | 0.9876 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207703 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9099 | 0.9867 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207704 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9 | 0.9755 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207705 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.9015 | 0.966 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207706 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9125 | 0.9642 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207707 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9083 | 0.9783 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207708 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9069 | 0.9628 | 0.92 | 1.05 | 316 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+G_1BAILEY U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207709 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9199 | 0.9714 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207710 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9053 | 0.9877 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207711 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9031 | 0.9858 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207712 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9055 | 0.9927 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207713 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9049 | 0.9876 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207714 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9126 | 0.9867 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207715 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9026 | 0.9755 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207716 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.904 | 0.966 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207717 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9149 | 0.9642 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207718 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9105 | 0.9783 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207719 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9094 | 0.9628 | 0.92 | 1.05 | 317 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+176 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207720 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9199 | 0.9714 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207721 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9053 | 0.9877 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207722 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9031 | 0.9858 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207723 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9055 | 0.9927 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207724 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9049 | 0.9876 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207725 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9126 | 0.9867 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207726 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9026 | 0.9755 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207727 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.904 | 0.966 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207728 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9149 | 0.9642 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207729 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9105 | 0.9783 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207730 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9094 | 0.9628 | 0.92 | 1.05 | 318 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+177 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F1HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207731 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9199 | 0.9714 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207732 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9053 | 0.9877 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207733 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9031 | 0.9858 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207734 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9054 | 0.9927 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207735 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9049 | 0.9876 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207736 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9126 | 0.9867 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207737 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9026 | 0.9755 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207738 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.904 | 0.966 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207739 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9149 | 0.9642 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207740 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9105 | 0.9783 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207741 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9094 | 0.9628 | 0.92 | 1.05 | 319 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+178 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207742 | 23S | Approved | P3 | 38 | 3WABBASEKA | VL |  |  |  |  | 0.9199 | 0.9714 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337964 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207743 | 23S | Approved | P3 | 38 | 3STUTGART.N+ | VL |  |  |  |  | 0.9053 | 0.9877 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207744 | 23S | Approved | P3 | 38 | 3STUTGART.N | VL |  |  |  |  | 0.9031 | 0.9858 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207745 | 23S | Approved | P3 | 38 | 3RICUSKEY! | VL |  |  |  |  | 0.9055 | 0.9927 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207746 | 23S | Approved | P3 | 38 | 3STUTGART IN | VL |  |  |  |  | 0.9049 | 0.9876 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207747 | 23S | Approved | P3 | 38 | 3ULM | VL |  |  |  |  | 0.9126 | 0.9867 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337970 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207748 | 23S | Approved | P3 | 38 | 3ALMYRA | VL |  |  |  |  | 0.9026 | 0.9755 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207749 | 23S | Approved | P3 | 38 | 3DEWITT | VL |  |  |  |  | 0.904 | 0.966 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207750 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9149 | 0.9642 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207751 | 23S | Approved | P3 | 38 | 3HUMPHREY# | VL |  |  |  |  | 0.9105 | 0.9783 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 338741 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207752 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9094 | 0.9628 | 0.92 | 1.05 | 320 | P1_2-1441_3RICUSKEY!,6RICUSKEY%+179 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1441_3RICUSKEY!,6RICUSKEY% | G_1CUMBRL F2HL ID 2 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207753 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9059 | 0.9642 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207754 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8777 | 0.9653 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207755 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8691 | 0.9676 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207756 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8661 | 0.9683 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207757 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.8615 | 0.9697 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207758 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8597 | 0.9701 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207759 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.911 | 0.9628 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207760 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.8593 | 0.9725 | 0.92 | 1.05 | 321 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207761 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9053 | 0.9642 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207762 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8765 | 0.9653 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207763 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8677 | 0.9676 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207764 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8648 | 0.9683 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207765 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.8601 | 0.9697 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207766 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8582 | 0.9701 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207767 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9105 | 0.9628 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207768 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.8579 | 0.9725 | 0.92 | 1.05 | 322 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1SLSBAU3 ID 5 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1SLSBAU3 ID 5 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207769 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9044 | 0.9642 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207770 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8755 | 0.9653 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207771 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8667 | 0.9676 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207772 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8637 | 0.9683 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207773 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.859 | 0.9697 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207774 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8572 | 0.9701 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207775 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9096 | 0.9628 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207776 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.8569 | 0.9725 | 0.92 | 1.05 | 323 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1CLSBAU3 ID 6 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1CLSBAU3 ID 6 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207777 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9054 | 0.9642 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207778 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8765 | 0.9653 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207779 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8678 | 0.9676 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207780 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8648 | 0.9683 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207781 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.8601 | 0.9697 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207782 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8583 | 0.9701 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207783 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9106 | 0.9628 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207784 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.858 | 0.9725 | 0.92 | 1.05 | 324 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1LYNCH U3 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1LYNCH U3 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207785 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.9052 | 0.9642 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207786 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8758 | 0.9653 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207787 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8669 | 0.9676 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207788 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8639 | 0.9683 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207789 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.8591 | 0.9697 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207790 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8573 | 0.9701 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207791 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9104 | 0.9628 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207792 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.8569 | 0.9725 | 0.92 | 1.05 | 325 | P1_2-1448_3RITCHIE!,3HELENA IN#!+155 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1PLUM PT U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207793 | 23S | Approved | P3 | 38 | 3GILLETT! | VL |  |  |  |  | 0.905 | 0.9642 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207794 | 23S | Approved | P3 | 38 | 3ELAINE | VL |  |  |  |  | 0.8761 | 0.9653 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207795 | 23S | Approved | P3 | 38 | 3MARVELL | VL |  |  |  |  | 0.8674 | 0.9676 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207796 | 23S | Approved | P3 | 38 | 3BARTON | VL |  |  |  |  | 0.8644 | 0.9683 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207797 | 23S | Approved | P3 | 38 | 3HELENA.W+ | VL |  |  |  |  | 0.8597 | 0.9697 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207798 | 23S | Approved | P3 | 38 | 3HELENA.C | VL |  |  |  |  | 0.8579 | 0.9701 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207799 | 23S | Approved | P3 | 38 | 3DELUCE# | VL |  |  |  |  | 0.9102 | 0.9628 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207800 | 23S | Approved | P3 | 38 | 3HELENA IN#! | VL |  |  |  |  | 0.8575 | 0.9725 | 0.92 | 1.05 | 326 | P1_2-1448_3RITCHIE!,3HELENA IN#!+G_1BAILEY U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1448_3RITCHIE!,3HELENA IN#! | G_1BAILEY U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
207846 | 23S | Approved | P3 | 38 | 4CANEY | VL |  |  |  |  | 0.8584 | 0.992 | 0.92 | 1.05 | 460 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
207847 | 23S | Approved | P3 | 38 | CENTNL 4 | VL |  |  |  |  | 0.9074 | 0.9892 | 0.92 | 1.05 | 460 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
207848 | 23S | Approved | P3 | 38 | OAKDALE4 | VL |  |  |  |  | 0.8604 | 0.99 | 0.92 | 1.05 | 460 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
207849 | 23S | Approved | P3 | 38 | PNPRARIE 4 | VL |  |  |  |  | 0.8511 | 1.005 | 0.92 | 1.05 | 460 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
207850 | 23S | Approved | P3 | 38 | WSTBAY 4 | VL |  |  |  |  | 0.8724 | 0.9885 | 0.92 | 1.05 | 460 | P1_2-1653_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1653_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
207881 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8765 | 0.9717 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207882 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.91 | 0.9569 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207883 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9096 | 0.964 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207884 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9108 | 0.968 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207885 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9101 | 0.9569 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207886 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.91 | 0.9568 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207887 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8751 | 0.9705 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207888 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8912 | 0.9849 | 0.92 | 1.05 | 467 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G2! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207889 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.88 | 0.9717 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207890 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.915 | 0.9569 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207891 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9133 | 0.964 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207892 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.914 | 0.968 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207893 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9151 | 0.9569 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207894 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9151 | 0.9568 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207895 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8786 | 0.9705 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207896 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8946 | 0.9849 | 0.92 | 1.05 | 468 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WILL_GL_G4! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WILL_GL_G4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207897 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8793 | 0.9717 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207898 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9149 | 0.9569 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207899 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9127 | 0.964 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207900 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9133 | 0.968 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207901 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.915 | 0.9569 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207902 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.915 | 0.9568 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207903 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8779 | 0.9705 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207904 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8939 | 0.9849 | 0.92 | 1.05 | 469 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207905 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8788 | 0.9717 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207906 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9143 | 0.9569 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207907 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9122 | 0.964 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207908 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9128 | 0.968 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207909 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9144 | 0.9569 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207910 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9144 | 0.9568 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207911 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8774 | 0.9705 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207912 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8934 | 0.9849 | 0.92 | 1.05 | 470 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207913 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.88 | 0.9717 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207914 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9153 | 0.9569 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207915 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9134 | 0.964 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207916 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.914 | 0.968 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207917 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9154 | 0.9569 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207918 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9154 | 0.9568 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207919 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8787 | 0.9705 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207920 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8947 | 0.9849 | 0.92 | 1.05 | 471 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U4! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U4! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207921 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.88 | 0.9717 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207922 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9153 | 0.9569 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207923 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9133 | 0.964 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207924 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.914 | 0.968 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207925 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9154 | 0.9569 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207926 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9153 | 0.9568 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207927 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8787 | 0.9705 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207928 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8946 | 0.9849 | 0.92 | 1.05 | 472 | P1_2-1654_COUGH 4!,PLAISAN4!+G_1NMIL U5! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_1NMIL U5! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207929 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8743 | 0.9717 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207930 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.911 | 0.9569 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207931 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9084 | 0.964 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207932 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9088 | 0.968 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207933 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9111 | 0.9569 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207934 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.911 | 0.9568 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207935 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8729 | 0.9705 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207936 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8891 | 0.9849 | 0.92 | 1.05 | 473 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207937 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8802 | 0.9717 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207938 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9155 | 0.9569 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207939 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9136 | 0.964 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207940 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9142 | 0.968 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207941 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9156 | 0.9569 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207942 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9155 | 0.9568 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207943 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8788 | 0.9705 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207944 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8948 | 0.9849 | 0.92 | 1.05 | 474 | P1_2-1654_COUGH 4!,PLAISAN4!+G_G1 ACAD! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_G1 ACAD! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207945 | 23S | Approved | P3 | 38 | 4VEAZIE | VL |  |  |  |  | 0.8798 | 0.9717 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207946 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.9144 | 0.9569 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207947 | 23S | Approved | P3 | 38 | 4BOBCAT | VL |  |  |  |  | 0.9131 | 0.964 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 335453 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207948 | 23S | Approved | P3 | 38 | 4CHAMPAGNE! | VL |  |  |  |  | 0.9139 | 0.968 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 335455 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207949 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9145 | 0.9569 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207950 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.9144 | 0.9568 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207951 | 23S | Approved | P3 | 38 | GUIDRY 4 | VL |  |  |  |  | 0.8785 | 0.9705 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207952 | 23S | Approved | P3 | 38 | PLAISAN4 | VL |  |  |  |  | 0.8945 | 0.9849 | 0.92 | 1.05 | 475 | P1_2-1654_COUGH 4!,PLAISAN4!+G_PLAQUEM6 ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1654_COUGH 4!,PLAISAN4! | G_PLAQUEM6 ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
207953 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9006 | 0.9802 | 0.92 | 1.05 | 543 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+74 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_1WAT U3! ID 1 |  | Facility: Radial
207954 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9007 | 0.9802 | 0.92 | 1.05 | 544 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+190 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G1 ACAD! ID 1 |  | Facility: Radial
207955 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9006 | 0.9802 | 0.92 | 1.05 | 545 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+196 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE1 ID 1 |  | Facility: Radial
207956 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9006 | 0.9802 | 0.92 | 1.05 | 546 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+197 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_LABBE2 ID 1 |  | Facility: Radial
207957 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.8913 | 0.9802 | 0.92 | 1.05 | 547 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+198 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
207958 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.8913 | 0.9802 | 0.92 | 1.05 | 548 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+199 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
207959 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.8994 | 0.9802 | 0.92 | 1.05 | 549 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+200 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 |  | Facility: Radial
207964 | 23S | Approved | P3 | 38 | 5WM DOVER RD | VL |  |  |  |  | 0.9194 | 1.0014 | 0.92 | 1.05 | 559 | G_1STFRG1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338410 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1STFRG1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
207965 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9169 | 0.9991 | 0.92 | 1.05 | 559 | G_1STFRG1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1STFRG1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
207966 | 23S | Approved | P3 | 38 | 5WM POLK AVE | VL |  |  |  |  | 0.9199 | 1.007 | 0.92 | 1.05 | 559 | G_1STFRG1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338414 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1STFRG1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
207967 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.915 | 1.0153 | 0.92 | 1.05 | 560 | G_1STFRG1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1STFRG1 ID 1 | Turn on switch shunt at Couch 69 kV sub
207968 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9165 | 1.0155 | 0.92 | 1.05 | 560 | G_1STFRG1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1STFRG1 ID 1 | Turn on switch shunt at Couch 69 kV sub
207983 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9175 | 0.9684 | 0.92 | 1.05 | 576 | G_1FRNTR 1! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 1! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207986 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9175 | 0.9684 | 0.92 | 1.05 | 583 | G_1FRNTR 2! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1FRNTR 2! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207989 | 23S | Approved | P3 | 38 | 4DOBBIN | VL |  |  |  |  | 0.9165 | 0.9788 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334044 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207990 | 23S | Approved | P3 | 38 | 4SPRINGBRNCH | VL |  |  |  |  | 0.9177 | 0.9786 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334046 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207991 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9169 | 0.9684 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207992 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9176 | 0.9674 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207993 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9169 | 0.965 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207994 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9176 | 0.9674 | 0.92 | 1.05 | 590 | G_1G1LEWIS! ID 1+391 | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207995 | 23S | Approved | P3 | 38 | 4STALEY! | VL |  |  |  |  | 0.9182 | 0.9838 | 0.92 | 1.05 | 591 | G_1G1LEWIS! ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_1G1LEWIS! ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
207996 | 23S | Approved | P3 | 38 | 4SHEAWIL | VL |  |  |  |  | 0.9199 | 0.9937 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334078 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207997 | 23S | Approved | P3 | 38 | 4FWPIPE | VL |  |  |  |  | 0.9188 | 0.9835 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334079 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207998 | 23S | Approved | P3 | 38 | 45L555T50 | VL |  |  |  |  | 0.9188 | 0.9825 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334080 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
207999 | 23S | Approved | P3 | 38 | 4CRYSTAL | VL |  |  |  |  | 0.9188 | 0.982 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334081 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208000 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9069 | 0.9684 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208001 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9101 | 0.9674 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208002 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9103 | 0.965 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208003 | 23S | Approved | P3 | 38 | 4OAKRIDG! | VL |  |  |  |  | 0.918 | 0.9674 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334093 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208004 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9102 | 0.9674 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208005 | 23S | Approved | P3 | 38 | 4CONAIR | VL |  |  |  |  | 0.9187 | 0.9815 | 0.92 | 1.05 | 592 | G_1G1LEWIS! ID 1+P1_2-156_1G2LEWIS!,4LEWIS% | 334106 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-156_1G2LEWIS!,4LEWIS% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208006 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9111 | 0.9684 | 0.92 | 1.05 | 593 | G_1G1LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208007 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9183 | 0.9674 | 0.92 | 1.05 | 593 | G_1G1LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208008 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9183 | 0.965 | 0.92 | 1.05 | 593 | G_1G1LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208009 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9183 | 0.9674 | 0.92 | 1.05 | 593 | G_1G1LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208010 | 23S | Approved | P3 | 38 | 4FWPIPE | VL |  |  |  |  | 0.919 | 0.9835 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334079 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208011 | 23S | Approved | P3 | 38 | 45L555T50 | VL |  |  |  |  | 0.9161 | 0.9825 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334080 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208012 | 23S | Approved | P3 | 38 | 4CRYSTAL | VL |  |  |  |  | 0.9146 | 0.982 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334081 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208013 | 23S | Approved | P3 | 38 | 4SECURTY! | VL |  |  |  |  | 0.9094 | 0.9837 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334082 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208014 | 23S | Approved | P3 | 38 | 4JAYHAWK! | VL |  |  |  |  | 0.9041 | 0.9877 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334083 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208015 | 23S | Approved | P3 | 38 | 4CLVELND! | VL |  |  |  |  | 0.901 | 0.9909 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334084 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208016 | 23S | Approved | P3 | 38 | 4TARKING! | VL |  |  |  |  | 0.9096 | 0.9775 | 0.92 | 1.05 | 594 | G_1G1LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334119 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G1LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208017 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.8985 | 0.9684 | 0.92 | 1.05 | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208018 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.8952 | 0.9674 | 0.92 | 1.05 | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208019 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.8892 | 0.965 | 0.92 | 1.05 | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208020 | 23S | Approved | P3 | 38 | 4OAKRIDG! | VL |  |  |  |  | 0.8876 | 0.9674 | 0.92 | 1.05 | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334093 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208021 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.8953 | 0.9674 | 0.92 | 1.05 | 598 | G_1G1LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208022 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9179 | 0.9684 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208023 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9195 | 0.9674 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208024 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9189 | 0.965 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208025 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9195 | 0.9674 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208026 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.9173 | 0.964 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208027 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9195 | 0.9649 | 0.92 | 1.05 | 599 | G_1G1LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208028 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9162 | 0.9684 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208029 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9179 | 0.9674 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208030 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9175 | 0.965 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208031 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9179 | 0.9674 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208032 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.9191 | 0.9642 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208033 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.9156 | 0.964 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208034 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.9193 | 0.9666 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208035 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9175 | 0.9649 | 0.92 | 1.05 | 600 | G_1G1LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208036 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9183 | 0.9661 | 0.92 | 1.05 | 601 | G_1G1LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-216_4RAYWOOD!,4CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208037 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.9193 | 0.9752 | 0.92 | 1.05 | 601 | G_1G1LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-216_4RAYWOOD!,4CHINA% | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208038 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9131 | 0.9814 | 0.92 | 1.05 | 606 | G_1G1LEWIS! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208039 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9147 | 0.9832 | 0.92 | 1.05 | 606 | G_1G1LEWIS! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G1LEWIS! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208040 | 23S | Approved | P3 | 38 | 4DOBBIN | VL |  |  |  |  | 0.9171 | 0.9788 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334044 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208041 | 23S | Approved | P3 | 38 | 4SPRINGBRNCH | VL |  |  |  |  | 0.9183 | 0.9786 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334046 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208042 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9173 | 0.9684 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208043 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9179 | 0.9674 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208044 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9172 | 0.965 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208045 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9179 | 0.9674 | 0.92 | 1.05 | 611 | G_1G2LEWIS! ID 1+391 | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-143_7GRIMES%,1FRNTR 1!,1FRNTR 2!,1FRNTR 3!,1F | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208046 | 23S | Approved | P3 | 38 | 4STALEY! | VL |  |  |  |  | 0.9184 | 0.9838 | 0.92 | 1.05 | 612 | G_1G2LEWIS! ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_1G2LEWIS! ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208047 | 23S | Approved | P3 | 38 | 4SHEAWIL | VL |  |  |  |  | 0.9199 | 0.9937 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334078 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208048 | 23S | Approved | P3 | 38 | 4FWPIPE | VL |  |  |  |  | 0.9188 | 0.9835 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334079 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208049 | 23S | Approved | P3 | 38 | 45L555T50 | VL |  |  |  |  | 0.9188 | 0.9825 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334080 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208050 | 23S | Approved | P3 | 38 | 4CRYSTAL | VL |  |  |  |  | 0.9188 | 0.982 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334081 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208051 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9069 | 0.9684 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208052 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9101 | 0.9674 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208053 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9103 | 0.965 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208054 | 23S | Approved | P3 | 38 | 4OAKRIDG! | VL |  |  |  |  | 0.918 | 0.9674 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334093 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208055 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9102 | 0.9674 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208056 | 23S | Approved | P3 | 38 | 4CONAIR | VL |  |  |  |  | 0.9187 | 0.9815 | 0.92 | 1.05 | 613 | G_1G2LEWIS! ID 1+P1_2-155_1G1LEWIS!,4LEWIS% | 334106 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-155_1G1LEWIS!,4LEWIS% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208057 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9112 | 0.9684 | 0.92 | 1.05 | 614 | G_1G2LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208058 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9185 | 0.9674 | 0.92 | 1.05 | 614 | G_1G2LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208059 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9184 | 0.965 | 0.92 | 1.05 | 614 | G_1G2LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208060 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9185 | 0.9674 | 0.92 | 1.05 | 614 | G_1G2LEWIS! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208061 | 23S | Approved | P3 | 38 | 4FWPIPE | VL |  |  |  |  | 0.9191 | 0.9835 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334079 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208062 | 23S | Approved | P3 | 38 | 45L555T50 | VL |  |  |  |  | 0.9162 | 0.9825 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334080 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208063 | 23S | Approved | P3 | 38 | 4CRYSTAL | VL |  |  |  |  | 0.9146 | 0.982 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334081 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208064 | 23S | Approved | P3 | 38 | 4SECURTY! | VL |  |  |  |  | 0.9095 | 0.9837 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334082 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208065 | 23S | Approved | P3 | 38 | 4JAYHAWK! | VL |  |  |  |  | 0.9042 | 0.9877 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334083 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208066 | 23S | Approved | P3 | 38 | 4CLVELND! | VL |  |  |  |  | 0.901 | 0.9909 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334084 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208067 | 23S | Approved | P3 | 38 | 4TARKING! | VL |  |  |  |  | 0.9097 | 0.9775 | 0.92 | 1.05 | 615 | G_1G2LEWIS! ID 1+P1_2-165_4CLVELND!,4JACINTO% | 334119 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-165_4CLVELND!,4JACINTO% | G_1G2LEWIS! ID 1 | Project Horizon |  | 13-ETI-015-HZ | 2021-06-01 | Eastgate 138 kV Substation: Add 37.7 Mvar capacitor bank
208068 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.899 | 0.9684 | 0.92 | 1.05 | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208069 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.8957 | 0.9674 | 0.92 | 1.05 | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208070 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.8897 | 0.965 | 0.92 | 1.05 | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208071 | 23S | Approved | P3 | 38 | 4OAKRIDG! | VL |  |  |  |  | 0.8881 | 0.9674 | 0.92 | 1.05 | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334093 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208072 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.8958 | 0.9674 | 0.92 | 1.05 | 619 | G_1G2LEWIS! ID 1+P1_2-175_4OAKRIDG!,4PORTER% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-175_4OAKRIDG!,4PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 12-ETI-007-CP | 2015-06-01 | Install capacitor bank at Alden 138 kV
208073 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9183 | 0.9684 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208074 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9199 | 0.9674 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208075 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9192 | 0.965 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208076 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9199 | 0.9674 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208077 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.9176 | 0.964 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208078 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9199 | 0.9649 | 0.92 | 1.05 | 620 | G_1G2LEWIS! ID 1+P1_2-184_4PORTER%,6PORTER% | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-184_4PORTER%,6PORTER% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208079 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9165 | 0.9684 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208080 | 23S | Approved | P3 | 38 | 4GOSLIN2! | VL |  |  |  |  | 0.9183 | 0.9674 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334091 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208081 | 23S | Approved | P3 | 38 | 4METRO2! | VL |  |  |  |  | 0.9178 | 0.965 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334092 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208082 | 23S | Approved | P3 | 38 | 4GOSLIN1! | VL |  |  |  |  | 0.9183 | 0.9674 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334098 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208083 | 23S | Approved | P3 | 38 | 4NEWCANY! | VL |  |  |  |  | 0.9193 | 0.9642 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334111 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208084 | 23S | Approved | P3 | 38 | 4HICKORY | VL |  |  |  |  | 0.9159 | 0.964 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334112 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208085 | 23S | Approved | P3 | 38 | 4EASTGAT | VL |  |  |  |  | 0.9197 | 0.9666 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334113 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208086 | 23S | Approved | P3 | 38 | 4HUFFMAN | VL |  |  |  |  | 0.9179 | 0.9649 | 0.92 | 1.05 | 621 | G_1G2LEWIS! ID 1+P1_2-203_6PORTER%,6CHINA% | 334114 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-203_6PORTER%,6CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208087 | 23S | Approved | P3 | 38 | 4LIBERTY-SR | VL |  |  |  |  | 0.9186 | 0.9661 | 0.92 | 1.05 | 622 | G_1G2LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334212 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-216_4RAYWOOD!,4CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208088 | 23S | Approved | P3 | 38 | 4RAYWOOD! | VL |  |  |  |  | 0.9195 | 0.9752 | 0.92 | 1.05 | 622 | G_1G2LEWIS! ID 1+P1_2-216_4RAYWOOD!,4CHINA% | 334213 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-216_4RAYWOOD!,4CHINA% | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208089 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9132 | 0.9814 | 0.92 | 1.05 | 627 | G_1G2LEWIS! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208090 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9148 | 0.9832 | 0.92 | 1.05 | 627 | G_1G2LEWIS! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G2LEWIS! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208095 | 23S | Approved | P3 | 38 | 4STALEY! | VL |  |  |  |  | 0.8949 | 0.9838 | 0.92 | 1.05 | 632 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208096 | 23S | Approved | P3 | 38 | 4MAGROVE | VL |  |  |  |  | 0.9054 | 0.9843 | 0.92 | 1.05 | 632 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334126 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208097 | 23S | Approved | P3 | 38 | 4L111T411 | VL |  |  |  |  | 0.9145 | 0.9855 | 0.92 | 1.05 | 632 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334127 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208098 | 23S | Approved | P3 | 38 | 4KICKAPO | VL |  |  |  |  | 0.9144 | 0.9854 | 0.92 | 1.05 | 632 | G_4RAYBURN% ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334128 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_4RAYBURN% ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208099 | 23S | Approved | P3 | 38 | 4MILLCR! | VL |  |  |  |  | 0.9151 | 0.9941 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334283 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208100 | 23S | Approved | P3 | 38 | 4PINELND | VL |  |  |  |  | 0.9069 | 0.9758 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334284 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208101 | 23S | Approved | P3 | 38 | 4BROADUS | VL |  |  |  |  | 0.9023 | 0.9717 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334285 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208102 | 23S | Approved | P3 | 38 | 4ETOIL | VL |  |  |  |  | 0.9004 | 0.97 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334286 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208103 | 23S | Approved | P3 | 38 | 4HRTNHIL | VL |  |  |  |  | 0.9097 | 0.9838 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334287 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208104 | 23S | Approved | P3 | 38 | 2TEMPLE1 | VL |  |  |  |  | 0.9199 | 0.9819 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208105 | 23S | Approved | P3 | 38 | 2TEMPL2* | VL |  |  |  |  | 0.9199 | 0.982 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208106 | 23S | Approved | P3 | 38 | 2TEMPLE2 | VL |  |  |  |  | 0.9198 | 0.9818 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208107 | 23S | Approved | P3 | 38 | 2TMPLSWC | VL |  |  |  |  | 0.9199 | 0.9819 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208108 | 23S | Approved | P3 | 38 | 2WEIRGAT | VL |  |  |  |  | 0.9088 | 0.9719 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208109 | 23S | Approved | P3 | 38 | 4PEACH! | VL |  |  |  |  | 0.9034 | 0.9925 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334300 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208110 | 23S | Approved | P3 | 38 | 4UNONGSU! | VL |  |  |  |  | 0.8903 | 0.9914 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334301 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208111 | 23S | Approved | P3 | 38 | 4KIRBY | VL |  |  |  |  | 0.882 | 0.9913 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334302 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208112 | 23S | Approved | P3 | 38 | 4CALL! | VL |  |  |  |  | 0.8775 | 0.9921 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334303 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208113 | 23S | Approved | P3 | 38 | 4NBUNA | VL |  |  |  |  | 0.871 | 0.9957 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334304 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208114 | 23S | Approved | P3 | 38 | 4BUNASW | VL |  |  |  |  | 0.871 | 0.9958 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334305 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208115 | 23S | Approved | P3 | 38 | 4TEMPLE | VL |  |  |  |  | 0.871 | 0.9958 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334306 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208116 | 23S | Approved | P3 | 38 | 4BUNA! | VL |  |  |  |  | 0.8702 | 0.9975 | 0.92 | 1.05 | 633 | G_4RAYBURN% ID 1+P1_2-247_4BUNA!,4EVADALE! | 334307 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed |  | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
208117 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9098 | 0.9814 | 0.92 | 1.05 | 635 | G_4RAYBURN% ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208118 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9114 | 0.9832 | 0.92 | 1.05 | 635 | G_4RAYBURN% ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_4RAYBURN% ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208121 | 23S | Approved | P3 | 38 | 4STALEY! | VL |  |  |  |  | 0.9168 | 0.9838 | 0.92 | 1.05 | 638 | G_1EXXONGT1! ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_1EXXONGT1! ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208122 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9174 | 0.9396 | 0.92 | 1.05 | 639 | G_1EXXONGT1! ID 1+P1_2-251_4EVADALE!,47NECHES! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-251_4EVADALE!,47NECHES! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208123 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9149 | 0.9396 | 0.92 | 1.05 | 640 | G_1EXXONGT1! ID 1+P1_2-255_4KOUNTZE%,4CYPRESS% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-255_4KOUNTZE%,4CYPRESS% | G_1EXXONGT1! ID 1 |  | Facility: Radial
208124 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9136 | 0.9396 | 0.92 | 1.05 | 641 | G_1EXXONGT1! ID 1+P1_2-259_8CYPRESS%,8HARTBRG% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-259_8CYPRESS%,8HARTBRG% | G_1EXXONGT1! ID 1 |  | Facility: Radial
208125 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.908 | 0.9396 | 0.92 | 1.05 | 644 | G_1EXXONGT1! ID 1+P1_2-293_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-293_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208126 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9068 | 0.9396 | 0.92 | 1.05 | 645 | G_1EXXONGT1! ID 1+P1_2-294_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208127 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9124 | 0.9396 | 0.92 | 1.05 | 646 | G_1EXXONGT1! ID 1+P1_2-298_4CENTRAL-TX!,4UNION! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-298_4CENTRAL-TX!,4UNION! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208128 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9097 | 0.9396 | 0.92 | 1.05 | 647 | G_1EXXONGT1! ID 1+P1_2-299_4UNION!,4STONGAT! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-299_4UNION!,4STONGAT! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208129 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.9082 | 0.9396 | 0.92 | 1.05 | 648 | G_1EXXONGT1! ID 1+P1_2-300_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-300_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
208130 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.917 | 0.9396 | 0.92 | 1.05 | 649 | G_1EXXONGT1! ID 1+P1_2-317_6SABINE%,1G4SABIN! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-317_6SABINE%,1G4SABIN! | G_1EXXONGT1! ID 1 |  | Facility: Radial
208131 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9151 | 0.9814 | 0.92 | 1.05 | 650 | G_1EXXONGT1! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208132 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9167 | 0.9832 | 0.92 | 1.05 | 650 | G_1EXXONGT1! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1EXXONGT1! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208137 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9146 | 0.9814 | 0.92 | 1.05 | 653 | G_1G3SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G3SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208138 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9162 | 0.9832 | 0.92 | 1.05 | 653 | G_1G3SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G3SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208139 | 23S | Approved | P3 | 38 | 4STALEY! | VL |  |  |  |  | 0.9155 | 0.9838 | 0.92 | 1.05 | 655 | G_1G4SABIN! ID 1+P1_2-149_4RIVTRIN%,4STALEY! | 334125 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-149_4RIVTRIN%,4STALEY! | G_1G4SABIN! ID 1 | Project Proposed |  | 13-ETI-006-CP | 2015-06-01 | Install 25.1 Mvar capacitor bank at Magnolia Groveton 138 kV
208140 | 23S | Approved | P3 | 38 | 4ALDEN! | VL |  |  |  |  | 0.9176 | 0.9684 | 0.92 | 1.05 | 658 | G_1G4SABIN! ID 1+P1_2-160_4LEWIS%,4ALDEN! | 334090 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-160_4LEWIS%,4ALDEN! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-042-CP | 2014-06-01 | Install 50.2 Mvar capacitor bank at Parkway 138 kV
208141 | 23S | Approved | P3 | 38 | 2NECHESO | VL |  |  |  |  | 0.917 | 0.9396 | 0.92 | 1.05 | 660 | G_1G4SABIN! ID 1+P1_2-288_4CARROLS%,1EXXONGT1! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-288_4CARROLS%,1EXXONGT1! | G_1G4SABIN! ID 1 |  | Facility: Radial
208142 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9127 | 0.9814 | 0.92 | 1.05 | 663 | G_1G4SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208143 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9143 | 0.9832 | 0.92 | 1.05 | 663 | G_1G4SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G4SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208144 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9144 | 0.9814 | 0.92 | 1.05 | 667 | G_1G5SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G5SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208145 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.916 | 0.9832 | 0.92 | 1.05 | 667 | G_1G5SABIN! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1G5SABIN! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208168 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9151 | 0.9814 | 0.92 | 1.05 | 687 | G_1NELSON_G6! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1NELSON_G6! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208169 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9168 | 0.9832 | 0.92 | 1.05 | 687 | G_1NELSON_G6! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_1NELSON_G6! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208185 | 23S | Approved | P3 | 38 | 4KROTZ_SPRG! | VL |  |  |  |  | 0.911 | 0.9569 | 0.92 | 1.05 | 708 | G_1WILL_GL_G2! ID 1+362 | 303153 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-114_4KROTZ_SPRG!,4CHAMPAGNE! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
208186 | 23S | Approved | P3 | 38 | 4LINE-642_TP | VL |  |  |  |  | 0.9111 | 0.9569 | 0.92 | 1.05 | 708 | G_1WILL_GL_G2! ID 1+362 | 335456 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-114_4KROTZ_SPRG!,4CHAMPAGNE! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
208187 | 23S | Approved | P3 | 38 | 4COL_SPRINGS | VL |  |  |  |  | 0.911 | 0.9568 | 0.92 | 1.05 | 708 | G_1WILL_GL_G2! ID 1+362 | 335457 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-114_4KROTZ_SPRG!,4CHAMPAGNE! | G_1WILL_GL_G2! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
208199 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9168 | 0.9281 | 0.92 | 1.05 | 730 | G_1RVR_BND_G1! ID 1+1235 | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208200 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9168 | 0.9281 | 0.92 | 1.05 | 730 | G_1RVR_BND_G1! ID 1+1235 | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208201 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9168 | 0.9281 | 0.92 | 1.05 | 730 | G_1RVR_BND_G1! ID 1+1235 | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1RVR_BND_G1! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208207 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9149 | 0.9281 | 0.92 | 1.05 | 744 | G_1WAT U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208208 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9149 | 0.9281 | 0.92 | 1.05 | 744 | G_1WAT U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208209 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9149 | 0.9281 | 0.92 | 1.05 | 744 | G_1WAT U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1WAT U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208220 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.918 | 0.9281 | 0.92 | 1.05 | 755 | G_1GYP U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208221 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.918 | 0.9281 | 0.92 | 1.05 | 755 | G_1GYP U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208222 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.918 | 0.9281 | 0.92 | 1.05 | 755 | G_1GYP U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208223 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9176 | 0.9281 | 0.92 | 1.05 | 757 | G_1GYP U3! ID 1+P1_2-1175_3PLANTATION! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1175_3PLANTATION! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208224 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9176 | 0.9281 | 0.92 | 1.05 | 757 | G_1GYP U3! ID 1+P1_2-1175_3PLANTATION! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1175_3PLANTATION! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208225 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9176 | 0.9281 | 0.92 | 1.05 | 757 | G_1GYP U3! ID 1+P1_2-1175_3PLANTATION! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1175_3PLANTATION! | G_1GYP U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208238 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9172 | 0.9281 | 0.92 | 1.05 | 774 | G_1NMIL U4! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208239 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9172 | 0.9281 | 0.92 | 1.05 | 774 | G_1NMIL U4! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208240 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9172 | 0.9281 | 0.92 | 1.05 | 774 | G_1NMIL U4! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208241 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9162 | 0.9281 | 0.92 | 1.05 | 776 | G_1NMIL U4! ID 1+P1_2-1175_3PLANTATION! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1175_3PLANTATION! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208242 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9162 | 0.9281 | 0.92 | 1.05 | 776 | G_1NMIL U4! ID 1+P1_2-1175_3PLANTATION! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1175_3PLANTATION! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208243 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9162 | 0.9281 | 0.92 | 1.05 | 776 | G_1NMIL U4! ID 1+P1_2-1175_3PLANTATION! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1175_3PLANTATION! | G_1NMIL U4! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208246 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9171 | 0.9281 | 0.92 | 1.05 | 781 | G_1NMIL U5! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208247 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9171 | 0.9281 | 0.92 | 1.05 | 781 | G_1NMIL U5! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208248 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9171 | 0.9281 | 0.92 | 1.05 | 781 | G_1NMIL U5! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1NMIL U5! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208254 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9178 | 0.9281 | 0.92 | 1.05 | 794 | G_1MICH U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208255 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9179 | 0.9281 | 0.92 | 1.05 | 794 | G_1MICH U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208256 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9179 | 0.9281 | 0.92 | 1.05 | 794 | G_1MICH U3! ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208257 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9173 | 0.9281 | 0.92 | 1.05 | 796 | G_1MICH U3! ID 1+P1_2-1175_3PLANTATION! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1175_3PLANTATION! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208258 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9173 | 0.9281 | 0.92 | 1.05 | 796 | G_1MICH U3! ID 1+P1_2-1175_3PLANTATION! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1175_3PLANTATION! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208259 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9173 | 0.9281 | 0.92 | 1.05 | 796 | G_1MICH U3! ID 1+P1_2-1175_3PLANTATION! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-1175_3PLANTATION! | G_1MICH U3! ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208268 | 23S | Approved | P3 | 38 | 3BLACK_RIV | VL |  |  |  |  | 0.9163 | 0.9281 | 0.92 | 1.05 | 812 | G_1B.WLSN U2 ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 303320 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208269 | 23S | Approved | P3 | 38 | 3BLACK_RIVER | VL |  |  |  |  | 0.9163 | 0.9281 | 0.92 | 1.05 | 812 | G_1B.WLSN U2 ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 337318 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208270 | 23S | Approved | P3 | 38 | JNESVIL3 | VL |  |  |  |  | 0.9163 | 0.9281 | 0.92 | 1.05 | 812 | G_1B.WLSN U2 ID 1+P1_2-987_3NATCHEZSES%,3RED_GUM! | 503308 |  |  |  | 115 | 115 | 504 | LEPA |  |  | P1_2-987_3NATCHEZSES%,3RED_GUM! | G_1B.WLSN U2 ID 1 | Project Proposed |  | 14-EMI-003-CP | 2018-06-01 | Construct Baxter Wilson-Natchez SES 115 kV, 230 kV construction (Natchez Improvement Project Phase 1
208352 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.918 | 1.0153 | 0.92 | 1.05 | 905 | G_1ANO U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208353 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9194 | 1.0155 | 0.92 | 1.05 | 905 | G_1ANO U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208356 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9174 | 1.0153 | 0.92 | 1.05 | 911 | G_1ANO U2 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U2 ID 1 | Turn on switch shunt at Couch 69 kV sub
208357 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9189 | 1.0155 | 0.92 | 1.05 | 911 | G_1ANO U2 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ANO U2 ID 1 | Turn on switch shunt at Couch 69 kV sub
208363 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.918 | 0.9991 | 0.92 | 1.05 | 924 | G_1ISES U1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1ISES U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208364 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.916 | 1.0153 | 0.92 | 1.05 | 925 | G_1ISES U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ISES U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208365 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9174 | 1.0155 | 0.92 | 1.05 | 925 | G_1ISES U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1ISES U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208370 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9196 | 1.0153 | 0.92 | 1.05 | 939 | G_1PLUM PT U1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1PLUM PT U1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208374 | 23S | Approved | P3 | 38 | 3CAMDEN.N! | VL |  |  |  |  | 0.9185 | 0.9993 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337531 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208375 | 23S | Approved | P3 | 38 | 3SMACKOVER | VL |  |  |  |  | 0.9116 | 1.0185 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337536 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208376 | 23S | Approved | P3 | 38 | 3SMACKOVER+ | VL |  |  |  |  | 0.9118 | 1.021 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337537 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208377 | 23S | Approved | P3 | 38 | 3HAYS CITY | VL |  |  |  |  | 0.9091 | 1.0186 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337538 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208378 | 23S | Approved | P3 | 38 | 3EL DORADO! | VL |  |  |  |  | 0.9134 | 1.0331 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337539 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208379 | 23S | Approved | P3 | 38 | 3ELD DONAN | VL |  |  |  |  | 0.9117 | 1.0277 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337540 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208380 | 23S | Approved | P3 | 38 | 3T.E.P/S-ELD | VL |  |  |  |  | 0.9113 | 1.0274 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337541 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208381 | 23S | Approved | P3 | 38 | 3ELD MONSNTO | VL |  |  |  |  | 0.9131 | 1.0248 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337542 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208382 | 23S | Approved | P3 | 38 | 3ELDORADO.W | VL |  |  |  |  | 0.9165 | 1.0217 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337543 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208383 | 23S | Approved | P3 | 38 | 3ELD PARKERS | VL |  |  |  |  | 0.9165 | 1.0201 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337550 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208384 | 23S | Approved | P3 | 38 | 3ELD LION | VL |  |  |  |  | 0.9123 | 1.0187 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337551 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208385 | 23S | Approved | P3 | 38 | 3ELD JACKSON | VL |  |  |  |  | 0.9118 | 1.0195 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337552 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208386 | 23S | Approved | P3 | 38 | 3ELDORADO.E! | VL |  |  |  |  | 0.9134 | 1.0236 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337553 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208387 | 23S | Approved | P3 | 38 | 3T.E.P/S-F+ | VL |  |  |  |  | 0.915 | 1.0202 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337554 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208388 | 23S | Approved | P3 | 38 | 3T.E.P/S-F | VL |  |  |  |  | 0.9109 | 1.0165 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337555 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208389 | 23S | Approved | P3 | 38 | 3ELD QUINN | VL |  |  |  |  | 0.9134 | 1.033 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337560 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208390 | 23S | Approved | P3 | 38 | 3ELD MILL RD | VL |  |  |  |  | 0.9176 | 1.0206 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 337563 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208391 | 23S | Approved | P3 | 38 | 3MCCLELLAN#! | VL |  |  |  |  | 0.9167 | 1 | 0.92 | 1.05 | 944 | G_1MCCLELAN U1 ID 1+1523 | 338823 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1275_3EL DORADO!,8EL DORADO% | G_1MCCLELAN U1 ID 1 | Project Proposed |  | 13-EAI-003-CP | 2015-06-01 | Construct Monticello East-Reed 115 kV, constructed to 230 kV
208405 | 23S | Approved | P3 | 38 | 5MOSES% | VL |  |  |  |  | 0.918 | 0.9687 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338022 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208406 | 23S | Approved | P3 | 38 | 5FORSTCTY.S | VL |  |  |  |  | 0.9143 | 0.9713 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338027 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208407 | 23S | Approved | P3 | 38 | 5HUGHES | VL |  |  |  |  | 0.9109 | 0.9892 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338028 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208408 | 23S | Approved | P3 | 38 | 5FORSTCTY.N+ | VL |  |  |  |  | 0.917 | 0.9693 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338029 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208409 | 23S | Approved | P3 | 38 | 5FORSTCTY.N | VL |  |  |  |  | 0.9165 | 0.9687 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338030 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208410 | 23S | Approved | P3 | 38 | 5WYNNE.S | VL |  |  |  |  | 0.9157 | 0.9736 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338031 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208411 | 23S | Approved | P3 | 38 | 5WYNNE IND | VL |  |  |  |  | 0.9147 | 0.9726 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338032 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208412 | 23S | Approved | P3 | 38 | 5KUHN RD! | VL |  |  |  |  | 0.9172 | 1.0036 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338040 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208413 | 23S | Approved | P3 | 38 | 5EBONY% | VL |  |  |  |  | 0.9156 | 1.0047 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338160 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208414 | 23S | Approved | P3 | 38 | 5W.MEMPHIS! | VL |  |  |  |  | 0.9126 | 1.0093 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338161 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208415 | 23S | Approved | P3 | 38 | 5MARION AR | VL |  |  |  |  | 0.9169 | 1.0037 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338164 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208416 | 23S | Approved | P3 | 38 | 5WM DOVER RD | VL |  |  |  |  | 0.9119 | 1.0014 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338410 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208417 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9094 | 0.9991 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208418 | 23S | Approved | P3 | 38 | 5WM LEHI-W | VL |  |  |  |  | 0.9145 | 1.0058 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338412 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208419 | 23S | Approved | P3 | 38 | 5WM LEHI-E | VL |  |  |  |  | 0.9141 | 1.0048 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338413 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208420 | 23S | Approved | P3 | 38 | 5WM POLK AVE | VL |  |  |  |  | 0.9122 | 1.007 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338414 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208421 | 23S | Approved | P3 | 38 | 5PALESTINE# | VL |  |  |  |  | 0.9183 | 0.9675 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338882 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208422 | 23S | Approved | P3 | 38 | 5WYNNE.E# | VL |  |  |  |  | 0.9178 | 0.9771 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338883 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208423 | 23S | Approved | P3 | 38 | 5FORSTCTY.W# | VL |  |  |  |  | 0.915 | 0.9698 | 0.92 | 1.05 | 961 | G_1BAILEY U1 ID 1+1748 | 338884 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_1BAILEY U1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208426 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9145 | 1.0153 | 0.92 | 1.05 | 967 | G_1CAL G1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1CAL G1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208427 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9159 | 1.0155 | 0.92 | 1.05 | 967 | G_1CAL G1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_1CAL G1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208438 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9138 | 0.9814 | 0.92 | 1.05 | 991 | G_G1DOLHIL! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_G1DOLHIL! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208439 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9155 | 0.9832 | 0.92 | 1.05 | 991 | G_G1DOLHIL! ID 1+P1_2-414_2ECHO!,2DEWEYVL! | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | G_G1DOLHIL! ID 1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208440 | 23S | Approved | P3 | 38 | TENRUSK7 | VH |  |  |  |  | 1.0508 | 1.0147 | 0.92 | 1.05 | 995 | G_G1DOLHIL! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_G1DOLHIL! ID 1 |  | VH
208441 | 23S | Approved | P3 | 38 | TENGEN 7 | VH |  |  |  |  | 1.0508 | 1.0147 | 0.92 | 1.05 | 995 | G_G1DOLHIL! ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_G1DOLHIL! ID 1 |  | VH
208444 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9155 | 0.9802 | 0.92 | 1.05 | 1005 | G_G3TECHE! ID 1+2143 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 | turn on switch shunt at BEADLE 230kV sub
208445 | 23S | Approved | P3 | 38 | BEADLE 6 | VL |  |  |  |  | 0.916 | 0.9819 | 0.92 | 1.05 | 1005 | G_G3TECHE! ID 1+2143 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1
208460 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9105 | 0.9802 | 0.92 | 1.05 | 1016 | G_HARGIS1 ID 1+2143 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
208461 | 23S | Approved | P3 | 38 | BEADLE 6 | VL |  |  |  |  | 0.911 | 0.9819 | 0.92 | 1.05 | 1016 | G_HARGIS1 ID 1+2143 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1
208463 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9105 | 0.9802 | 0.92 | 1.05 | 1018 | G_HARGIS2 ID 1+2143 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
208464 | 23S | Approved | P3 | 38 | BEADLE 6 | VL |  |  |  |  | 0.911 | 0.9819 | 0.92 | 1.05 | 1018 | G_HARGIS2 ID 1+2143 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1
208466 | 23S | Approved | P3 | 38 | ELKS 6 | VL |  |  |  |  | 0.9163 | 0.9802 | 0.92 | 1.05 | 1020 | G_BONIN2 ID 1+2143 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1 | turn on switch shunt at BEADLE 230kV sub
208467 | 23S | Approved | P3 | 38 | BEADLE 6 | VL |  |  |  |  | 0.9168 | 0.9819 | 0.92 | 1.05 | 1020 | G_BONIN2 ID 1+2143 | 502425 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_BONIN2 ID 1
208474 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9181 | 0.9991 | 0.92 | 1.05 | 1025 | G_JBOGA&B1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208475 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9181 | 0.9991 | 0.92 | 1.05 | 1026 | G_JBOGA&B1 ID 2+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGA&B1 ID 2 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208477 | 23S | Approved | P3 | 38 | 5W.MEMPHIS! | VL |  |  |  |  | 0.9193 | 1.0093 | 0.92 | 1.05 | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338161 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208478 | 23S | Approved | P3 | 38 | 5WM DOVER RD | VL |  |  |  |  | 0.9182 | 1.0014 | 0.92 | 1.05 | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338410 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208479 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9157 | 0.9991 | 0.92 | 1.05 | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208480 | 23S | Approved | P3 | 38 | 5WM POLK AVE | VL |  |  |  |  | 0.9188 | 1.007 | 0.92 | 1.05 | 1028 | G_JBOGENC1 ID 1+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338414 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID 1 | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208483 | 23S | Approved | P3 | 38 | 5HUGHES | VL |  |  |  |  | 0.9185 | 0.9892 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338028 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208484 | 23S | Approved | P3 | 38 | 5EBONY% | VL |  |  |  |  | 0.9185 | 1.0047 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338160 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208485 | 23S | Approved | P3 | 38 | 5W.MEMPHIS! | VL |  |  |  |  | 0.9161 | 1.0093 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338161 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208486 | 23S | Approved | P3 | 38 | 5MARION AR | VL |  |  |  |  | 0.9194 | 1.0037 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338164 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208487 | 23S | Approved | P3 | 38 | 5WM DOVER RD | VL |  |  |  |  | 0.9149 | 1.0014 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338410 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208488 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9124 | 0.9991 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208489 | 23S | Approved | P3 | 38 | 5WM LEHI-W | VL |  |  |  |  | 0.9176 | 1.0058 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338412 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208490 | 23S | Approved | P3 | 38 | 5WM LEHI-E | VL |  |  |  |  | 0.9171 | 1.0048 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338413 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208491 | 23S | Approved | P3 | 38 | 5WM POLK AVE | VL |  |  |  |  | 0.9156 | 1.007 | 0.92 | 1.05 | 1031 | G_JBOGENC1 ID C+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338414 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENC1 ID C | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208497 | 23S | Approved | P3 | 38 | 5HUGHES | VL |  |  |  |  | 0.9164 | 0.9892 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338028 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208498 | 23S | Approved | P3 | 38 | 5KUHN RD! | VL |  |  |  |  | 0.9175 | 1.0036 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338040 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208499 | 23S | Approved | P3 | 38 | 5EBONY% | VL |  |  |  |  | 0.9158 | 1.0047 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338160 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208500 | 23S | Approved | P3 | 38 | 5W.MEMPHIS! | VL |  |  |  |  | 0.9135 | 1.0093 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338161 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208501 | 23S | Approved | P3 | 38 | 5MARION AR | VL |  |  |  |  | 0.9166 | 1.0037 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338164 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208502 | 23S | Approved | P3 | 38 | 5WM DOVER RD | VL |  |  |  |  | 0.9122 | 1.0014 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338410 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208503 | 23S | Approved | P3 | 38 | 5WM GATEWAY | VL |  |  |  |  | 0.9097 | 0.9991 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338411 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208504 | 23S | Approved | P3 | 38 | 5WM LEHI-W | VL |  |  |  |  | 0.9149 | 1.0058 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338412 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208505 | 23S | Approved | P3 | 38 | 5WM LEHI-E | VL |  |  |  |  | 0.9144 | 1.0048 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338413 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208506 | 23S | Approved | P3 | 38 | 5WM POLK AVE | VL |  |  |  |  | 0.9129 | 1.007 | 0.92 | 1.05 | 1039 | G_JBOGENE1 ID E+P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | 338414 |  |  |  | 161 | 161 | 334 | WMU |  |  | P1_2-1503_5W.MEMPHIS!,8W.MEMPHIS% | G_JBOGENE1 ID E | Project Horizon |  | 14-EAI-007-HZ | 2022-06-01 | Wynne S: Install 24 Mvar capacitor bank
208507 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9173 | 1.0153 | 0.92 | 1.05 | 1040 | G_JBOGENE1 ID E+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JBOGENE1 ID E | Turn on switch shunt at Couch 69 kV sub
208508 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9188 | 1.0155 | 0.92 | 1.05 | 1040 | G_JBOGENE1 ID E+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JBOGENE1 ID E | Turn on switch shunt at Couch 69 kV sub
208536 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9177 | 1.0153 | 0.92 | 1.05 | 1068 | G_FLINTCR1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_FLINTCR1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208537 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.9191 | 1.0155 | 0.92 | 1.05 | 1068 | G_FLINTCR1 ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_FLINTCR1 ID 1 | Turn on switch shunt at Couch 69 kV sub
208540 | 23S | Approved | P3 | 38 | TENRUSK7 | VH |  |  |  |  | 1.0517 | 1.0147 | 0.92 | 1.05 | 1078 | G_PIRKEY 1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_PIRKEY 1 ID 1 |  | VH
208541 | 23S | Approved | P3 | 38 | TENGEN 7 | VH |  |  |  |  | 1.0517 | 1.0147 | 0.92 | 1.05 | 1078 | G_PIRKEY 1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_PIRKEY 1 ID 1 |  | VH
208544 | 23S | Approved | P3 | 38 | TENRUSK7 | VH |  |  |  |  | 1.051 | 1.0147 | 0.92 | 1.05 | 1084 | G_WELSH2-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH2-1 ID 1 |  | VH
208545 | 23S | Approved | P3 | 38 | TENGEN 7 | VH |  |  |  |  | 1.051 | 1.0147 | 0.92 | 1.05 | 1084 | G_WELSH2-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH2-1 ID 1 |  | VH
208548 | 23S | Approved | P3 | 38 | TENRUSK7 | VH |  |  |  |  | 1.051 | 1.0147 | 0.92 | 1.05 | 1090 | G_WELSH3-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH3-1 ID 1 |  | VH
208549 | 23S | Approved | P3 | 38 | TENGEN 7 | VH |  |  |  |  | 1.051 | 1.0147 | 0.92 | 1.05 | 1090 | G_WELSH3-1 ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_WELSH3-1 ID 1 |  | VH
208552 | 23S | Approved | P3 | 38 | TENRUSK7 | VH |  |  |  |  | 1.0509 | 1.0147 | 0.92 | 1.05 | 1097 | G_TURKCOAL ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508585 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_TURKCOAL ID 1 |  | VH
208553 | 23S | Approved | P3 | 38 | TENGEN 7 | VH |  |  |  |  | 1.0509 | 1.0147 | 0.92 | 1.05 | 1097 | G_TURKCOAL ID 1+P1_2-1863_LEBROCK7!,TENRUSK7! | 508586 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1863_LEBROCK7!,TENRUSK7! | G_TURKCOAL ID 1 |  | VH
208556 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9196 | 1.0153 | 0.92 | 1.05 | 1101 | G_MUSKOG4G ID 1+P1_2-1534_5THAYER.S!,2THAYER.S! | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_MUSKOG4G ID 1 | Turn on switch shunt at Couch 69 kV sub
208559 | 23S | Approved | P3 | 38 | 2THAYER.S! | VL |  |  |  |  | 0.9156 | 1.0153 | 0.92 | 1.05 | 1103 | G_JTEC GEN#2 1 ID 2+1779 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JTEC GEN#2 1 ID 2 | Turn on switch shunt at Couch 69 kV sub
208560 | 23S | Approved | P3 | 38 | 2THAYER.N | VL |  |  |  |  | 0.917 | 1.0155 | 0.92 | 1.05 | 1103 | G_JTEC GEN#2 1 ID 2+1779 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_5THAYER.S!,2THAYER.S! | G_JTEC GEN#2 1 ID 2 | Turn on switch shunt at Couch 69 kV sub
208561 | 23S | Approved | P3 | 38 | 2DEWEYVL! | VL |  |  |  |  | 0.9173 | 0.9814 | 0.92 | 1.05 | 1104 | Unit:303032 1S1INTHB13.8 Id:1+662 | 334705 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | Unit:303032 1S1INTHB13.8 Id:1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208562 | 23S | Approved | P3 | 38 | 2SKBVREG | VL |  |  |  |  | 0.9189 | 0.9832 | 0.92 | 1.05 | 1104 | Unit:303032 1S1INTHB13.8 Id:1+662 | 334706 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-414_2ECHO!,2DEWEYVL! | Unit:303032 1S1INTHB13.8 Id:1 | Project Proposed |  | 11-ETI-003-CP | 2013-12-01 | Install capacitor bank at Deweyville 69 kV (JNEC)
208563 | 15S | Proposed | P0 | 39 | 5HORN LAKE% | VH |  |  |  |  | 1.0575 | 1.0575 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
208564 | 15S | Proposed | P0 | 39 | 8E POINT AL | VH |  |  |  |  | 1.0538 | 1.0538 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
208565 | 15S | Proposed | P0 | 39 | 8WID CRK FP | VH |  |  |  |  | 1.0525 | 1.0525 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
208566 | 15S | Proposed | P3 | 39 | 3GILBERT | VH |  |  |  |  | 1.0569 | 1.0086 | 0.92 | 1.05 | 1 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G3MADISN! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G3MADISN! ID 1 |  | VH
208567 | 15S | Proposed | P3 | 39 | 3METROPOLIS | VH |  |  |  |  | 1.0526 | 1.0124 | 0.92 | 1.05 | 1 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G3MADISN! ID 1 | 337328 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G3MADISN! ID 1 |  | VH
208568 | 15S | Proposed | P3 | 39 | 3WISNER | VH |  |  |  |  | 1.0557 | 1.0135 | 0.92 | 1.05 | 1 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G3MADISN! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G3MADISN! ID 1 |  | VH
208569 | 15S | Proposed | P3 | 39 | 3WINNSBORO! | VH |  |  |  |  | 1.0626 | 1.0025 | 0.92 | 1.05 | 1 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G3MADISN! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G3MADISN! ID 1 |  | VH
208570 | 15S | Proposed | P3 | 39 | 3GILBERT | VH |  |  |  |  | 1.0541 | 1.0086 | 0.92 | 1.05 | 2 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-1COUGH! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-1COUGH! ID 1 |  | VH
208571 | 15S | Proposed | P3 | 39 | 3WISNER | VH |  |  |  |  | 1.0529 | 1.0135 | 0.92 | 1.05 | 2 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-1COUGH! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-1COUGH! ID 1 |  | VH
208572 | 15S | Proposed | P3 | 39 | 3WINNSBORO! | VH |  |  |  |  | 1.0597 | 1.0025 | 0.92 | 1.05 | 2 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-1COUGH! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-1COUGH! ID 1 |  | VH
208573 | 15S | Proposed | P3 | 39 | 3GILBERT | VH |  |  |  |  | 1.0541 | 1.0086 | 0.92 | 1.05 | 3 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-2COUGH! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-2COUGH! ID 1 |  | VH
208574 | 15S | Proposed | P3 | 39 | 3WISNER | VH |  |  |  |  | 1.0529 | 1.0135 | 0.92 | 1.05 | 3 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-2COUGH! ID 1 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-2COUGH! ID 1 |  | VH
208575 | 15S | Proposed | P3 | 39 | 3WINNSBORO! | VH |  |  |  |  | 1.0597 | 1.0025 | 0.92 | 1.05 | 3 | P1_2-1173_3WINNSBORO!,3SWARTZ!+G_G7-2COUGH! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | G_G7-2COUGH! ID 1 |  | VH
208576 | 15S | Proposed | P3 | 39 | 3GILBERT | VH |  |  |  |  | 1.0541 | 1.0086 | 0.92 | 1.05 | 4 | P1_2-1173_3WINNSBORO!,3SWARTZ!+232 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | Unit:501961 G6-1COUGH 23.8 Id:1 |  | VH
208577 | 15S | Proposed | P3 | 39 | 3WISNER | VH |  |  |  |  | 1.053 | 1.0135 | 0.92 | 1.05 | 4 | P1_2-1173_3WINNSBORO!,3SWARTZ!+232 | 337329 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | Unit:501961 G6-1COUGH 23.8 Id:1 |  | VH
208578 | 15S | Proposed | P3 | 39 | 3WINNSBORO! | VH |  |  |  |  | 1.0597 | 1.0025 | 0.92 | 1.05 | 4 | P1_2-1173_3WINNSBORO!,3SWARTZ!+232 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1173_3WINNSBORO!,3SWARTZ! | Unit:501961 G6-1COUGH 23.8 Id:1 |  | VH
208579 | 15S | Proposed | P3 | 39 | 3MT PINE.S% | VL |  |  |  |  | 0.8474 | 0.9938 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208580 | 15S | Proposed | P3 | 39 | 3ROYAL | VL |  |  |  |  | 0.8574 | 0.9913 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208581 | 15S | Proposed | P3 | 39 | 3MILTON | VL |  |  |  |  | 0.8814 | 0.9887 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208582 | 15S | Proposed | P3 | 39 | 3HS.W | VL |  |  |  |  | 0.8354 | 0.9904 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208583 | 15S | Proposed | P3 | 39 | 3HS.S | VL |  |  |  |  | 0.8285 | 0.9899 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208584 | 15S | Proposed | P3 | 39 | 3ALBRIGHT | VL |  |  |  |  | 0.9123 | 0.9894 | 0.92 | 1.05 | 22 | P1_2-1336_3BLAKELY!,3CARPENTER!+129 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
208585 | 15S | Proposed | P3 | 39 | 3MT PINE.S% | VL |  |  |  |  | 0.8472 | 0.9938 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337713 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208586 | 15S | Proposed | P3 | 39 | 3ROYAL | VL |  |  |  |  | 0.8572 | 0.9913 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337714 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208587 | 15S | Proposed | P3 | 39 | 3MILTON | VL |  |  |  |  | 0.8812 | 0.9887 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337715 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208588 | 15S | Proposed | P3 | 39 | 3HS.W | VL |  |  |  |  | 0.8352 | 0.9904 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208589 | 15S | Proposed | P3 | 39 | 3HS.S | VL |  |  |  |  | 0.8283 | 0.9899 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208590 | 15S | Proposed | P3 | 39 | 3ALBRIGHT | VL |  |  |  |  | 0.9121 | 0.9894 | 0.92 | 1.05 | 23 | P1_2-1336_3BLAKELY!,3CARPENTER!+130 | 337721 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1336_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
208671 | 15S | Proposed | P3 | 39 | 3STUTGART.N+ | VL |  |  |  |  | 0.9183 | 1.0132 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337965 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208672 | 15S | Proposed | P3 | 39 | 3STUTGART.N | VL |  |  |  |  | 0.9162 | 1.0113 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337966 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208673 | 15S | Proposed | P3 | 39 | 3RICUSKEY! | VL |  |  |  |  | 0.9178 | 1.0179 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208674 | 15S | Proposed | P3 | 39 | 3STUTGART IN | VL |  |  |  |  | 0.9171 | 1.012 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337969 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208675 | 15S | Proposed | P3 | 39 | 3ALMYRA | VL |  |  |  |  | 0.9129 | 1.0007 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337972 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208676 | 15S | Proposed | P3 | 39 | 3DEWITT | VL |  |  |  |  | 0.9124 | 0.9909 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337973 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208677 | 15S | Proposed | P3 | 39 | 3GILLETT! | VL |  |  |  |  | 0.9188 | 0.9878 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 337974 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208678 | 15S | Proposed | P3 | 39 | 3DELUCE# | VL |  |  |  |  | 0.9147 | 0.9869 | 0.92 | 1.05 | 35 | P1_2-1436_3RICUSKEY!,6RICUSKEY%+G_1ISES U1 ID 1 | 338752 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1436_3RICUSKEY!,6RICUSKEY% | G_1ISES U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208995 | 15S | Proposed | P3 | 39 | 3ELAINE | VL |  |  |  |  | 0.9083 | 0.9844 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337980 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208996 | 15S | Proposed | P3 | 39 | 3MARVELL | VL |  |  |  |  | 0.9009 | 0.9846 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337981 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208997 | 15S | Proposed | P3 | 39 | 3BARTON | VL |  |  |  |  | 0.8983 | 0.9845 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337982 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208998 | 15S | Proposed | P3 | 39 | 3HELENA.W+ | VL |  |  |  |  | 0.894 | 0.9842 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337983 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
208999 | 15S | Proposed | P3 | 39 | 3HELENA.C | VL |  |  |  |  | 0.8922 | 0.984 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 337984 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
209000 | 15S | Proposed | P3 | 39 | 3HELENA IN#! | VL |  |  |  |  | 0.892 | 0.9856 | 0.92 | 1.05 | 88 | P1_2-1443_3RITCHIE!,3HELENA IN#!+G_1ANDRUS U1 ID 1 | 338880 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1443_3RITCHIE!,3HELENA IN#! | G_1ANDRUS U1 ID 1 | Project Proposed |  | 11-EAI-027-CP | 2016-06-01 | Construct AECC L&D 2-Gillett 115 kV
209271 | 15S | Proposed | P3 | 39 | 8DANIEL | VH |  |  |  |  | 1.0757 | 1.0445 | 0.92 | 1.05 | 141 | P1_2-1599_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1599_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
209276 | 15S | Proposed | P3 | 39 | 4CANEY | VL |  |  |  |  | 0.8706 | 0.9944 | 0.92 | 1.05 | 292 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
209277 | 15S | Proposed | P3 | 39 | CENTNL 4 | VL |  |  |  |  | 0.9181 | 0.9936 | 0.92 | 1.05 | 292 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500160 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
209278 | 15S | Proposed | P3 | 39 | OAKDALE4 | VL |  |  |  |  | 0.8725 | 0.9927 | 0.92 | 1.05 | 292 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
209279 | 15S | Proposed | P3 | 39 | PNPRARIE 4 | VL |  |  |  |  | 0.8634 | 1.0063 | 0.92 | 1.05 | 292 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
209280 | 15S | Proposed | P3 | 39 | WSTBAY 4 | VL |  |  |  |  | 0.8844 | 0.9918 | 0.92 | 1.05 | 292 | P1_2-1648_COUGH 4!,PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1648_COUGH 4!,PNPRARIE 4% | G_1NELSON_G6! ID 1
209304 | 15S | Proposed | P3 | 39 | 4VEAZIE | VL |  |  |  |  | 0.8929 | 0.9776 | 0.92 | 1.05 | 299 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209305 | 15S | Proposed | P3 | 39 | GUIDRY 4 | VL |  |  |  |  | 0.8915 | 0.9764 | 0.92 | 1.05 | 299 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209306 | 15S | Proposed | P3 | 39 | PLAISAN4 | VL |  |  |  |  | 0.9065 | 0.99 | 0.92 | 1.05 | 299 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1RVR_BND_G1! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1RVR_BND_G1! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209307 | 15S | Proposed | P3 | 39 | 4VEAZIE | VL |  |  |  |  | 0.8922 | 0.9776 | 0.92 | 1.05 | 300 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209308 | 15S | Proposed | P3 | 39 | GUIDRY 4 | VL |  |  |  |  | 0.8908 | 0.9764 | 0.92 | 1.05 | 300 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209309 | 15S | Proposed | P3 | 39 | PLAISAN4 | VL |  |  |  |  | 0.9059 | 0.99 | 0.92 | 1.05 | 300 | P1_2-1649_COUGH 4!,PLAISAN4!+G_1WAT U3! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_1WAT U3! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209322 | 15S | Proposed | P3 | 39 | 4VEAZIE | VL |  |  |  |  | 0.8916 | 0.9776 | 0.92 | 1.05 | 305 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 303135 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209323 | 15S | Proposed | P3 | 39 | GUIDRY 4 | VL |  |  |  |  | 0.8902 | 0.9764 | 0.92 | 1.05 | 305 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500380 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209324 | 15S | Proposed | P3 | 39 | PLAISAN4 | VL |  |  |  |  | 0.9053 | 0.99 | 0.92 | 1.05 | 305 | P1_2-1649_COUGH 4!,PLAISAN4!+G_G3TECHE! ID 1 | 500720 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1649_COUGH 4!,PLAISAN4! | G_G3TECHE! ID 1 | Project Horizon |  | 14-EGL-008-HZ | 2019-06-01 | Krotz Springs - New capacitor bank
209325 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9195 | 0.9878 | 0.92 | 1.05 | 320 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+173 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 | turn on switch shunt at BEADLE 230kV sub
209326 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9199 | 0.9878 | 0.92 | 1.05 | 321 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+183 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 | turn on switch shunt at BEADLE 230kV sub
209327 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9199 | 0.9878 | 0.92 | 1.05 | 322 | 502401 FLANDER6 230 502425 BEADLE 6 230 1+184 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502401 FLANDER6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 | turn on switch shunt at BEADLE 230kV sub
209328 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9036 | 0.9878 | 0.92 | 1.05 | 323 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+173 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | Facility: Radial
209329 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9033 | 0.9878 | 0.92 | 1.05 | 324 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+183 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS1 ID 1 |  | Facility: Radial
209330 | 15S | Proposed | P3 | 39 | ELKS 6 | VL |  |  |  |  | 0.9033 | 0.9878 | 0.92 | 1.05 | 325 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+184 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_HARGIS2 ID 1 |  | Facility: Radial
209331 | 15S | Proposed | P3 | 39 | 2NECHESO | VL |  |  |  |  | 0.915 | 0.9442 | 0.92 | 1.05 | 341 | G_1EXXONGT1! ID 1+P1_2-287_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-287_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
209332 | 15S | Proposed | P3 | 39 | 2NECHESO | VL |  |  |  |  | 0.9147 | 0.9442 | 0.92 | 1.05 | 342 | G_1EXXONGT1! ID 1+P1_2-288_47NECHES!,4SABINE! | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-288_47NECHES!,4SABINE! | G_1EXXONGT1! ID 1 |  | Facility: Radial
209333 | 15S | Proposed | P3 | 39 | 2NECHESO | VL |  |  |  |  | 0.9142 | 0.9442 | 0.92 | 1.05 | 343 | G_1EXXONGT1! ID 1+P1_2-294_4STONGAT!,4MID CO% | 334681 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-294_4STONGAT!,4MID CO% | G_1EXXONGT1! ID 1 |  | Facility: Radial
209334 | 15S | Proposed | P3 | 39 | MAURICE2 | VL |  |  |  |  | 0.918 | 0.9921 | 0.92 | 1.05 | 401 | G_G1WKRAFT! ID 3+P1_2-1166_6MONTGOMERY!,CLARN 6! | 500565 |  |  |  | 69 | 69 | 502 | CLEC |  |  | P1_2-1166_6MONTGOMERY!,CLARN 6! | G_G1WKRAFT! ID 3 | Project External |  | Messick 500/230
209335 | 15S | Proposed | P3 | 39 | 4NEW_IBERIA! | VL |  |  |  |  | 0.9015 | 0.9922 | 0.92 | 1.05 | 411 | G_G3TECHE! ID 1+P1_2-562_4MORIL!,4CECELIA! | 335393 |  |  |  | 138 | 138 | 351 | EES |  |  | P1_2-562_4MORIL!,4CECELIA! | G_G3TECHE! ID 1 |  | Contingency: Trip bus as result of con
209336 | 15S | Proposed | P3 | 39 | 2WEIRGAT | VL |  |  |  |  | 0.9171 | 0.9873 | 0.92 | 1.05 | 419 | G_PIRKEY 1 ID 1+P1_2-233_4MILLCR! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-233_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209337 | 18L | Proposed | P0 | 40 | 8GPDELL | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 |  | ** Base Case ** | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | ** Base Case ** |  |  | VH
209338 | 18L | Proposed | P0 | 40 | 5HORN LAKE% | VH |  |  |  |  | 1.0621 | 1.0621 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
209339 | 18L | Proposed | P0 | 40 | 8DELL% | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 |  | ** Base Case ** | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
209340 | 18L | Proposed | P0 | 40 | 8SANS SOUCI% | VH |  |  |  |  | 1.0572 | 1.0572 | 0.92 | 1.05 |  | ** Base Case ** | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
209341 | 18L | Proposed | P0 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0664 | 1.0664 | 0.92 | 1.05 |  | ** Base Case ** | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
209342 | 18L | Proposed | P0 | 40 | 2OPPELLO | VH |  |  |  |  | 1.0541 | 1.0541 | 0.92 | 1.05 |  | ** Base Case ** | 338578 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
209343 | 18L | Proposed | P0 | 40 | 5DELL# | VH |  |  |  |  | 1.0503 | 1.0503 | 0.92 | 1.05 |  | ** Base Case ** | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | ** Base Case ** |  |  | VH
209344 | 18L | Proposed | P0 | 40 | 8SHAWNEE FP | VH |  |  |  |  | 1.0834 | 1.0834 | 0.92 | 1.05 |  | ** Base Case ** | 360001 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209345 | 18L | Proposed | P0 | 40 | 7SHAWNEE FP | VH |  |  |  |  | 1.0762 | 1.0762 | 0.92 | 1.05 |  | ** Base Case ** | 360002 |  |  |  | 345 | 345 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209346 | 18L | Proposed | P0 | 40 | 8RUTHERFORD | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 |  | ** Base Case ** | 360010 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209347 | 18L | Proposed | P0 | 40 | 8MARSHALL KY | VH |  |  |  |  | 1.0812 | 1.0812 | 0.92 | 1.05 |  | ** Base Case ** | 360015 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209348 | 18L | Proposed | P0 | 40 | 8WEAKLEY TN | VH |  |  |  |  | 1.0752 | 1.0752 | 0.92 | 1.05 |  | ** Base Case ** | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209349 | 18L | Proposed | P0 | 40 | 8JACKSON TN | VH |  |  |  |  | 1.0637 | 1.0637 | 0.92 | 1.05 |  | ** Base Case ** | 360019 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209350 | 18L | Proposed | P0 | 40 | 8SHELBY TN | VH |  |  |  |  | 1.056 | 1.056 | 0.92 | 1.05 |  | ** Base Case ** | 360021 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209351 | 18L | Proposed | P0 | 40 | 8CORDOVA TN | VH |  |  |  |  | 1.0513 | 1.0513 | 0.92 | 1.05 |  | ** Base Case ** | 360025 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209352 | 18L | Proposed | P0 | 40 | 8JVILLE FP | VH |  |  |  |  | 1.0807 | 1.0807 | 0.92 | 1.05 |  | ** Base Case ** | 360037 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209353 | 18L | Proposed | P0 | 40 | 8CUMBERLAND | VH |  |  |  |  | 1.0861 | 1.0861 | 0.92 | 1.05 |  | ** Base Case ** | 360040 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209354 | 18L | Proposed | P0 | 40 | 8PARADISE FP | VH |  |  |  |  | 1.086 | 1.086 | 0.92 | 1.05 |  | ** Base Case ** | 360042 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209355 | 18L | Proposed | P0 | 40 | 8MONTGOMERY | VH |  |  |  |  | 1.0795 | 1.0795 | 0.92 | 1.05 |  | ** Base Case ** | 360044 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209356 | 18L | Proposed | P0 | 40 | 8DAVIDSON TN | VH |  |  |  |  | 1.0786 | 1.0786 | 0.92 | 1.05 |  | ** Base Case ** | 360048 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209357 | 18L | Proposed | P0 | 40 | 8MAURY TN | VH |  |  |  |  | 1.0672 | 1.0672 | 0.92 | 1.05 |  | ** Base Case ** | 360050 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209358 | 18L | Proposed | P0 | 40 | 8FRANKLIN TN | VH |  |  |  |  | 1.0518 | 1.0518 | 0.92 | 1.05 |  | ** Base Case ** | 360069 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209359 | 18L | Proposed | P0 | 40 | 8WILSON TN | VH |  |  |  |  | 1.0759 | 1.0759 | 0.92 | 1.05 |  | ** Base Case ** | 360071 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209360 | 18L | Proposed | P0 | 40 | 8PLATEAU TN | VH |  |  |  |  | 1.0607 | 1.0607 | 0.92 | 1.05 |  | ** Base Case ** | 360077 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209361 | 18L | Proposed | P0 | 40 | 8BULL RUN FP | VH |  |  |  |  | 1.0508 | 1.0508 | 0.92 | 1.05 |  | ** Base Case ** | 360093 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209362 | 18L | Proposed | P0 | 40 | 8VOLUNTEER | VH |  |  |  |  | 1.0561 | 1.0561 | 0.92 | 1.05 |  | ** Base Case ** | 360097 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209363 | 18L | Proposed | P0 | 40 | 8PHIPPS B NP | VH |  |  |  |  | 1.0674 | 1.0674 | 0.92 | 1.05 |  | ** Base Case ** | 360102 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209364 | 18L | Proposed | P0 | 40 | 8SULLIVAN TN | VH |  |  |  |  | 1.0608 | 1.0608 | 0.92 | 1.05 |  | ** Base Case ** | 360106 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209365 | 18L | Proposed | P0 | 40 | 8HAYWOOD TN | VH |  |  |  |  | 1.0613 | 1.0613 | 0.92 | 1.05 |  | ** Base Case ** | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209366 | 18L | Proposed | P0 | 40 | 8LAG CRK CT | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 |  | ** Base Case ** | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209367 | 18L | Proposed | P0 | 40 | 8PIN HOOK TN | VH |  |  |  |  | 1.0766 | 1.0766 | 0.92 | 1.05 |  | ** Base Case ** | 360581 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209368 | 18L | Proposed | P0 | 40 | 8GLEASON CT | VH |  |  |  |  | 1.0778 | 1.0778 | 0.92 | 1.05 |  | ** Base Case ** | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209369 | 18L | Proposed | P0 | 40 | 8LAG CRK CC | VH |  |  |  |  | 1.0679 | 1.0679 | 0.92 | 1.05 |  | ** Base Case ** | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
209370 | 18L | Proposed | P3 | 40 | 8GPDELL | VH |  |  |  |  | 1.0605 | 1.0503 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209371 | 18L | Proposed | P3 | 40 | 8NEWMAD | VH |  |  |  |  | 1.0641 | 1.0427 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300035 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209372 | 18L | Proposed | P3 | 40 | 7ESSEX | VH |  |  |  |  | 1.0633 | 1.0449 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209373 | 18L | Proposed | P3 | 40 | 7NEWMAD | VH |  |  |  |  | 1.0633 | 1.0351 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300046 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209374 | 18L | Proposed | P3 | 40 | 7STFRAN | VH |  |  |  |  | 1.0685 | 1.0455 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209375 | 18L | Proposed | P3 | 40 | 7GOBKNOB | VH |  |  |  |  | 1.0684 | 1.05 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209376 | 18L | Proposed | P3 | 40 | 8WNEWMADRID | VH |  |  |  |  | 1.0641 | 1.0427 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 301406 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209377 | 18L | Proposed | P3 | 40 | 7WNEWMADRID | VH |  |  |  |  | 1.0633 | 1.0352 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209378 | 18L | Proposed | P3 | 40 | 5JONESBORO! | VH |  |  |  |  | 1.0516 | 1.0408 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209379 | 18L | Proposed | P3 | 40 | 8DELL% | VH |  |  |  |  | 1.0605 | 1.0503 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209380 | 18L | Proposed | P3 | 40 | 5PORTAGEVLE | VH |  |  |  |  | 1.052 | 1.0296 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338201 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209381 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0501 | 1.0401 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209382 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0506 | 1.0403 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209383 | 18L | Proposed | P3 | 40 | 3DATTO | VH |  |  |  |  | 1.0659 | 1.05 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338227 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209384 | 18L | Proposed | P3 | 40 | 3CORNING | VH |  |  |  |  | 1.061 | 1.0437 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209385 | 18L | Proposed | P3 | 40 | 3T.E.P/S-8 | VH |  |  |  |  | 1.0532 | 1.0372 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338229 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209386 | 18L | Proposed | P3 | 40 | 3JIM HILL! | VH |  |  |  |  | 1.0519 | 1.0351 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338230 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209387 | 18L | Proposed | P3 | 40 | 2JONSBORO.W | VH |  |  |  |  | 1.0516 | 1.0408 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209388 | 18L | Proposed | P3 | 40 | 5DELL# | VH |  |  |  |  | 1.0605 | 1.0503 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209389 | 18L | Proposed | P3 | 40 | 3CORNING.N# | VH |  |  |  |  | 1.0616 | 1.0444 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209390 | 18L | Proposed | P3 | 40 | 5JONSBORO.W# | VH |  |  |  |  | 1.0516 | 1.0408 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209391 | 18L | Proposed | P3 | 40 | 5JONSBORO.N# | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338703 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209392 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0503 | 1.0402 | 0.92 | 1.05 | 1 | P1_2-1_1NM G2, 7NEWMAD%+G_1NM G1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1NM G1 ID 1 |  | VH
209400 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0585 | 1.0485 | 0.92 | 1.05 | 2 | P1_2-1_1NM G2, 7NEWMAD%+G_1WHT BLUF U1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1WHT BLUF U1 ID 1 |  | VH
209415 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0504 | 1.0388 | 0.92 | 1.05 | 4 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U1 ID 1 |  | VH
209416 | 18L | Proposed | P3 | 40 | 8GPDELL | VH |  |  |  |  | 1.0625 | 1.0503 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 300030 |  |  |  | 500 | 500 | 330 | AECI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209424 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0563 | 1.0377 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209425 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0563 | 1.0378 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209426 | 18L | Proposed | P3 | 40 | 8DELL% | VH |  |  |  |  | 1.0625 | 1.0503 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338187 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209427 | 18L | Proposed | P3 | 40 | 5DELL# | VH |  |  |  |  | 1.0625 | 1.0503 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338596 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209428 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0508 | 1.0388 | 0.92 | 1.05 | 5 | P1_2-1_1NM G2, 7NEWMAD%+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1ISES U2 ID 1 |  | VH
209436 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0574 | 1.0256 | 0.92 | 1.05 | 6 | P1_2-1_1NM G2, 7NEWMAD%+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1_1NM G2, 7NEWMAD% | G_1MCCLELAN U1 ID 1 |  | VH
209521 | 18L | Proposed | P3 | 40 | 7STFRAN | VH |  |  |  |  | 1.0724 | 1.0455 | 0.92 | 1.05 | 19 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U1 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U1 ID 1 |  | VH
209522 | 18L | Proposed | P3 | 40 | 7GOBKNOB | VH |  |  |  |  | 1.0704 | 1.05 | 0.92 | 1.05 | 19 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U1 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U1 ID 1 |  | VH
209523 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.052 | 1.0388 | 0.92 | 1.05 | 19 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U1 ID 1 |  | VH
209524 | 18L | Proposed | P3 | 40 | 7STFRAN | VH |  |  |  |  | 1.0722 | 1.0455 | 0.92 | 1.05 | 20 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U2 ID 1 | 300048 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U2 ID 1 |  | VH
209525 | 18L | Proposed | P3 | 40 | 7GOBKNOB | VH |  |  |  |  | 1.0703 | 1.05 | 0.92 | 1.05 | 20 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U2 ID 1 | 300054 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U2 ID 1 |  | VH
209526 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0519 | 1.0377 | 0.92 | 1.05 | 20 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U2 ID 1 |  | VH
209527 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.052 | 1.0378 | 0.92 | 1.05 | 20 | P1_2-7_7NEWMAD%, 7STFRAN!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-7_7NEWMAD%, 7STFRAN! | G_1ISES U2 ID 1 |  | VH
209528 | 18L | Proposed | P3 | 40 | 7ESSEX | VH |  |  |  |  | 1.0557 | 1.0449 | 0.92 | 1.05 | 21 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ISES U2 ID 1 | 300038 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%, 7WNEWMADRID | G_1ISES U2 ID 1 |  | VH
209529 | 18L | Proposed | P3 | 40 | 7WNEWMADRID | VH |  |  |  |  | 1.0538 | 1.0352 | 0.92 | 1.05 | 21 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ISES U2 ID 1 | 301407 |  |  |  | 345 | 345 | 330 | AECI |  |  | P1_2-11_7NEWMAD%, 7WNEWMADRID | G_1ISES U2 ID 1 |  | VH
209530 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0542 | 1.0377 | 0.92 | 1.05 | 21 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-11_7NEWMAD%, 7WNEWMADRID | G_1ISES U2 ID 1 |  | VH
209531 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0543 | 1.0378 | 0.92 | 1.05 | 21 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-11_7NEWMAD%, 7WNEWMADRID | G_1ISES U2 ID 1 |  | VH
209532 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0503 | 1.0388 | 0.92 | 1.05 | 21 | P1_2-11_7NEWMAD%, 7WNEWMADRID+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-11_7NEWMAD%, 7WNEWMADRID | G_1ISES U2 ID 1 |  | VH
209533 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 22 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 1 |  | VH
209534 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0535 | 1.0403 | 0.92 | 1.05 | 22 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 1 |  | VH
209535 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 22 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 1 |  | VH
209536 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0502 | 1.0401 | 0.92 | 1.05 | 22 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 1 |  | VH
209537 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 22 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 1 |  | VH
209538 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 23 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 2 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 2 |  | VH
209539 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0536 | 1.0403 | 0.92 | 1.05 | 23 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 2 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 2 |  | VH
209540 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 23 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 2 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 2 |  | VH
209541 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0503 | 1.0401 | 0.92 | 1.05 | 23 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 2 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 2 |  | VH
209542 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 23 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 2 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 2 |  | VH
209543 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0512 | 1.0401 | 0.92 | 1.05 | 24 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 3 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 3 |  | VH
209544 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0536 | 1.0403 | 0.92 | 1.05 | 24 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 3 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 3 |  | VH
209545 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 24 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 3 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 3 |  | VH
209546 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0503 | 1.0401 | 0.92 | 1.05 | 24 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 3 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 3 |  | VH
209547 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 24 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 3 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 3 |  | VH
209548 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 25 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 4 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 4 |  | VH
209549 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0536 | 1.0403 | 0.92 | 1.05 | 25 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 4 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 4 |  | VH
209550 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 25 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 4 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 4 |  | VH
209551 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0503 | 1.0401 | 0.92 | 1.05 | 25 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 4 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 4 |  | VH
209552 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 25 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 4 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 4 |  | VH
209553 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 26 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 5 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 5 |  | VH
209554 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0536 | 1.0403 | 0.92 | 1.05 | 26 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 5 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 5 |  | VH
209555 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 26 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 5 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 5 |  | VH
209556 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0503 | 1.0401 | 0.92 | 1.05 | 26 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 5 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 5 |  | VH
209557 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 26 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 5 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 5 |  | VH
209558 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0511 | 1.0401 | 0.92 | 1.05 | 27 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 6 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 6 |  | VH
209559 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0535 | 1.0403 | 0.92 | 1.05 | 27 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 6 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 6 |  | VH
209560 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0502 | 1.0386 | 0.92 | 1.05 | 27 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 6 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 6 |  | VH
209561 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0502 | 1.0401 | 0.92 | 1.05 | 27 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 6 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 6 |  | VH
209562 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0521 | 1.0402 | 0.92 | 1.05 | 27 | P1_2-38_5WPLAIN!, 5KOSH!+G_6DOW_COGEN% ID 6 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_6DOW_COGEN% ID 6 |  | VH
209563 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0545 | 1.0401 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209564 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0564 | 1.0403 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209565 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0518 | 1.0386 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209566 | 18L | Proposed | P3 | 40 | 2THAYER.N | VH |  |  |  |  | 1.0505 | 1.0379 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209567 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0783 | 1.0664 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209568 | 18L | Proposed | P3 | 40 | 5BLACK ROCK# | VH |  |  |  |  | 1.0513 | 1.0398 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338708 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209569 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0538 | 1.0401 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209570 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0552 | 1.0402 | 0.92 | 1.05 | 28 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U1 ID 1 |  | VH
209571 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0544 | 1.0401 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209572 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0563 | 1.0403 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209573 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0519 | 1.0386 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209574 | 18L | Proposed | P3 | 40 | 2THAYER.N | VH |  |  |  |  | 1.0506 | 1.0379 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209575 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0782 | 1.0664 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209576 | 18L | Proposed | P3 | 40 | 5BLACK ROCK# | VH |  |  |  |  | 1.0513 | 1.0398 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338708 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209577 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0537 | 1.0401 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209578 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0552 | 1.0402 | 0.92 | 1.05 | 29 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WHT BLUF U2 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WHT BLUF U2 ID 1 |  | VH
209579 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0519 | 1.0377 | 0.92 | 1.05 | 30 | P1_2-38_5WPLAIN!, 5KOSH!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1ISES U2 ID 1 |  | VH
209580 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0519 | 1.0378 | 0.92 | 1.05 | 30 | P1_2-38_5WPLAIN!, 5KOSH!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1ISES U2 ID 1 |  | VH
209581 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0518 | 1.0401 | 0.92 | 1.05 | 31 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S1 ID 1 |  | VH
209582 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0541 | 1.0403 | 0.92 | 1.05 | 31 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S1 ID 1 |  | VH
209583 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0506 | 1.0386 | 0.92 | 1.05 | 31 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S1 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S1 ID 1 |  | VH
209584 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0509 | 1.0401 | 0.92 | 1.05 | 31 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S1 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S1 ID 1 |  | VH
209585 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0527 | 1.0402 | 0.92 | 1.05 | 31 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S1 ID 1 |  | VH
209586 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0519 | 1.0401 | 0.92 | 1.05 | 32 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS C7 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS C7 ID 1 |  | VH
209587 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0542 | 1.0403 | 0.92 | 1.05 | 32 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS C7 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS C7 ID 1 |  | VH
209588 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0507 | 1.0386 | 0.92 | 1.05 | 32 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS C7 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS C7 ID 1 |  | VH
209589 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.051 | 1.0401 | 0.92 | 1.05 | 32 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS C7 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS C7 ID 1 |  | VH
209590 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0528 | 1.0402 | 0.92 | 1.05 | 32 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS C7 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS C7 ID 1 |  | VH
209591 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0518 | 1.0401 | 0.92 | 1.05 | 33 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S2 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S2 ID 1 |  | VH
209592 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0541 | 1.0403 | 0.92 | 1.05 | 33 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S2 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S2 ID 1 |  | VH
209593 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0506 | 1.0386 | 0.92 | 1.05 | 33 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S2 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S2 ID 1 |  | VH
209594 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0509 | 1.0401 | 0.92 | 1.05 | 33 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S2 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S2 ID 1 |  | VH
209595 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0527 | 1.0402 | 0.92 | 1.05 | 33 | P1_2-38_5WPLAIN!, 5KOSH!+G_1WRIGHTS S2 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_1WRIGHTS S2 ID 1 |  | VH
209596 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0518 | 1.0401 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209597 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0542 | 1.0403 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209598 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0514 | 1.0386 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209599 | 18L | Proposed | P3 | 40 | 2THAYER.N | VH |  |  |  |  | 1.0503 | 1.0379 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338217 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209600 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0509 | 1.0401 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209601 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0528 | 1.0402 | 0.92 | 1.05 | 34 | P1_2-38_5WPLAIN!, 5KOSH!+G_NFK #1 1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_NFK #1 1 ID 1 |  | VH
209602 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0512 | 1.0401 | 0.92 | 1.05 | 35 | P1_2-38_5WPLAIN!, 5KOSH!+G_JTEC GEN#2 1 ID 2 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_JTEC GEN#2 1 ID 2 |  | VH
209603 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0537 | 1.0403 | 0.92 | 1.05 | 35 | P1_2-38_5WPLAIN!, 5KOSH!+G_JTEC GEN#2 1 ID 2 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_JTEC GEN#2 1 ID 2 |  | VH
209604 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0509 | 1.0386 | 0.92 | 1.05 | 35 | P1_2-38_5WPLAIN!, 5KOSH!+G_JTEC GEN#2 1 ID 2 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_JTEC GEN#2 1 ID 2 |  | VH
209605 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0503 | 1.0401 | 0.92 | 1.05 | 35 | P1_2-38_5WPLAIN!, 5KOSH!+G_JTEC GEN#2 1 ID 2 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_JTEC GEN#2 1 ID 2 |  | VH
209606 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0522 | 1.0402 | 0.92 | 1.05 | 35 | P1_2-38_5WPLAIN!, 5KOSH!+G_JTEC GEN#2 1 ID 2 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-38_5WPLAIN!, 5KOSH! | G_JTEC GEN#2 1 ID 2 |  | VH
209607 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0535 | 1.0401 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209608 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0552 | 1.0403 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209609 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0511 | 1.0386 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209610 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0777 | 1.0664 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209611 | 18L | Proposed | P3 | 40 | 5BLACK ROCK# | VH |  |  |  |  | 1.0507 | 1.0398 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338708 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209612 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0529 | 1.0401 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209613 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0542 | 1.0402 | 0.92 | 1.05 | 36 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U1 ID 1 |  | VH
209614 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0534 | 1.0401 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209615 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0551 | 1.0403 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209616 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.051 | 1.0386 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209617 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0775 | 1.0664 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209618 | 18L | Proposed | P3 | 40 | 5BLACK ROCK# | VH |  |  |  |  | 1.0506 | 1.0398 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338708 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209619 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0528 | 1.0401 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209620 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0541 | 1.0402 | 0.92 | 1.05 | 37 | P1_2-59_5KOSH!, 5COXCRK%+G_1WHT BLUF U2 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WHT BLUF U2 ID 1 |  | VH
209621 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0516 | 1.0388 | 0.92 | 1.05 | 38 | P1_2-59_5KOSH!, 5COXCRK%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1ISES U1 ID 1 |  | VH
209622 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0518 | 1.0377 | 0.92 | 1.05 | 39 | P1_2-59_5KOSH!, 5COXCRK%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1ISES U2 ID 1 |  | VH
209623 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0519 | 1.0378 | 0.92 | 1.05 | 39 | P1_2-59_5KOSH!, 5COXCRK%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1ISES U2 ID 1 |  | VH
209624 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0508 | 1.0401 | 0.92 | 1.05 | 40 | P1_2-59_5KOSH!, 5COXCRK%+G_1WRIGHTS C7 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WRIGHTS C7 ID 1 |  | VH
209625 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0529 | 1.0403 | 0.92 | 1.05 | 40 | P1_2-59_5KOSH!, 5COXCRK%+G_1WRIGHTS C7 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WRIGHTS C7 ID 1 |  | VH
209626 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0517 | 1.0402 | 0.92 | 1.05 | 40 | P1_2-59_5KOSH!, 5COXCRK%+G_1WRIGHTS C7 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_1WRIGHTS C7 ID 1 |  | VH
209627 | 18L | Proposed | P3 | 40 | 5HARDY.N | VH |  |  |  |  | 1.0509 | 1.0401 | 0.92 | 1.05 | 41 | P1_2-59_5KOSH!, 5COXCRK%+G_NFK #1 1 ID 1 | 338214 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_NFK #1 1 ID 1 |  | VH
209628 | 18L | Proposed | P3 | 40 | 5THAYER.S! | VH |  |  |  |  | 1.0531 | 1.0403 | 0.92 | 1.05 | 41 | P1_2-59_5KOSH!, 5COXCRK%+G_NFK #1 1 ID 1 | 338215 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_NFK #1 1 ID 1 |  | VH
209629 | 18L | Proposed | P3 | 40 | 2THAYER.S! | VH |  |  |  |  | 1.0508 | 1.0386 | 0.92 | 1.05 | 41 | P1_2-59_5KOSH!, 5COXCRK%+G_NFK #1 1 ID 1 | 338216 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_NFK #1 1 ID 1 |  | VH
209630 | 18L | Proposed | P3 | 40 | 5HARDY.E# | VH |  |  |  |  | 1.0501 | 1.0401 | 0.92 | 1.05 | 41 | P1_2-59_5KOSH!, 5COXCRK%+G_NFK #1 1 ID 1 | 338812 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_NFK #1 1 ID 1 |  | VH
209631 | 18L | Proposed | P3 | 40 | 5MAMMOTH# | VH |  |  |  |  | 1.0518 | 1.0402 | 0.92 | 1.05 | 41 | P1_2-59_5KOSH!, 5COXCRK%+G_NFK #1 1 ID 1 | 338815 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-59_5KOSH!, 5COXCRK% | G_NFK #1 1 ID 1 |  | VH
209632 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9152 | 0.9465 | 0.92 | 1.05 | 42 | P1_2-237_4RAYBURN%, 4MILLCR!+G_4TOLEDO% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_4TOLEDO% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209633 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9105 | 0.9465 | 0.92 | 1.05 | 43 | P1_2-237_4RAYBURN%, 4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209634 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.917 | 0.9465 | 0.92 | 1.05 | 44 | P1_2-237_4RAYBURN%, 4MILLCR!+G_1RVR_BND_G1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_1RVR_BND_G1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209635 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9175 | 0.9465 | 0.92 | 1.05 | 45 | P1_2-237_4RAYBURN%, 4MILLCR!+G_1WAT U3! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_1WAT U3! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209636 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9167 | 0.9465 | 0.92 | 1.05 | 46 | P1_2-237_4RAYBURN%, 4MILLCR!+G_1GGNS U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_1GGNS U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209637 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9092 | 0.9465 | 0.92 | 1.05 | 47 | P1_2-237_4RAYBURN%, 4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209638 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9169 | 0.9465 | 0.92 | 1.05 | 48 | P1_2-237_4RAYBURN%, 4MILLCR!+G_G1NESBIT! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_G1NESBIT! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209639 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9168 | 0.9465 | 0.92 | 1.05 | 49 | P1_2-237_4RAYBURN%, 4MILLCR!+G_G2RODEMR! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_G2RODEMR! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209640 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.9176 | 0.9465 | 0.92 | 1.05 | 50 | P1_2-237_4RAYBURN%, 4MILLCR!+G_G3MADISN! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%, 4MILLCR! | G_G3MADISN! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209711 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0512 | 1.0388 | 0.92 | 1.05 | 60 | P1_2-239_4MILLCR!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-239_4MILLCR! | G_1ISES U1 ID 1 |  | VH
209719 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 61 | P1_2-239_4MILLCR!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-239_4MILLCR! | G_1ISES U2 ID 1 |  | VH
209720 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0533 | 1.0378 | 0.92 | 1.05 | 61 | P1_2-239_4MILLCR!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-239_4MILLCR! | G_1ISES U2 ID 1 |  | VH
209742 | 18L | Proposed | P3 | 40 | 2PINELND | VL |  |  |  |  | 0.9033 | 0.9647 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209743 | 18L | Proposed | P3 | 40 | 2TEMPL1* | VL |  |  |  |  | 0.9014 | 0.9629 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209744 | 18L | Proposed | P3 | 40 | 2TEMPLE1 | VL |  |  |  |  | 0.9011 | 0.9627 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209745 | 18L | Proposed | P3 | 40 | 2TEMPL2* | VL |  |  |  |  | 0.9011 | 0.9626 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209746 | 18L | Proposed | P3 | 40 | 2TEMPLE2 | VL |  |  |  |  | 0.9009 | 0.9625 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209747 | 18L | Proposed | P3 | 40 | 2TMPLSWC | VL |  |  |  |  | 0.9009 | 0.9625 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209748 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.8837 | 0.9465 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209770 | 18L | Proposed | P3 | 40 | 2PINELND | VL |  |  |  |  | 0.9081 | 0.9647 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209771 | 18L | Proposed | P3 | 40 | 2TEMPL1* | VL |  |  |  |  | 0.9063 | 0.9629 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209772 | 18L | Proposed | P3 | 40 | 2TEMPLE1 | VL |  |  |  |  | 0.906 | 0.9627 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209773 | 18L | Proposed | P3 | 40 | 2TEMPL2* | VL |  |  |  |  | 0.9059 | 0.9626 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209774 | 18L | Proposed | P3 | 40 | 2TEMPLE2 | VL |  |  |  |  | 0.9057 | 0.9625 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209775 | 18L | Proposed | P3 | 40 | 2TMPLSWC | VL |  |  |  |  | 0.9058 | 0.9625 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209776 | 18L | Proposed | P3 | 40 | 2WEIRGAT | VL |  |  |  |  | 0.8887 | 0.9465 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
209777 | 18L | Proposed | P3 | 40 | 2FELICIANA | VL |  |  |  |  | 0.9129 | 0.9761 | 0.92 | 1.05 | 70 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1WAT U3! ID 1 | 335786 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!, 2JACKSON! | G_1WAT U3! ID 1 |  | Solution: Adjust caps
209778 | 18L | Proposed | P3 | 40 | 2MCMANUS | VL |  |  |  |  | 0.9081 | 0.9716 | 0.92 | 1.05 | 70 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1WAT U3! ID 1 | 335787 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!, 2JACKSON! | G_1WAT U3! ID 1 |  | Solution: Adjust caps
209779 | 18L | Proposed | P3 | 40 | 2BRADY_HGHTS | VL |  |  |  |  | 0.9021 | 0.966 | 0.92 | 1.05 | 70 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1WAT U3! ID 1 | 335788 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!, 2JACKSON! | G_1WAT U3! ID 1 |  | Solution: Adjust caps
209780 | 18L | Proposed | P3 | 40 | 2CLINTON | VL |  |  |  |  | 0.9016 | 0.9655 | 0.92 | 1.05 | 70 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1WAT U3! ID 1 | 335789 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!, 2JACKSON! | G_1WAT U3! ID 1 |  | Solution: Adjust caps
209781 | 18L | Proposed | P3 | 40 | 2CLINTON_REA | VL |  |  |  |  | 0.9021 | 0.966 | 0.92 | 1.05 | 70 | P1_2-758_2PORT_HUD_A!, 2JACKSON!+G_1WAT U3! ID 1 | 335790 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-758_2PORT_HUD_A!, 2JACKSON! | G_1WAT U3! ID 1 |  | Solution: Adjust caps
209782 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0513 | 1.0388 | 0.92 | 1.05 | 86 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+112 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1ISES U1 ID 1 |  | VH
209783 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 87 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1ISES U2 ID 1 |  | VH
209784 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0533 | 1.0378 | 0.92 | 1.05 | 87 | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1137_3CLRKD MUNI!, 3CLARKSDALE! | G_1ISES U2 ID 1 |  | VH
209785 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.051 | 1.0388 | 0.92 | 1.05 | 92 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+112 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1ISES U1 ID 1 |  | VH
209786 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.053 | 1.0377 | 0.92 | 1.05 | 93 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1ISES U2 ID 1 |  | VH
209787 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0531 | 1.0378 | 0.92 | 1.05 | 93 | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1138_3CLRKD MUNI!, 6CROSSROADS! | G_1ISES U2 ID 1 |  | VH
209788 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0512 | 1.0388 | 0.92 | 1.05 | 100 | P1_2-1194_3MINDEN_LA!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1194_3MINDEN_LA! | G_1ISES U1 ID 1 |  | VH
209789 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 101 | P1_2-1194_3MINDEN_LA!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1194_3MINDEN_LA! | G_1ISES U2 ID 1 |  | VH
209790 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0532 | 1.0378 | 0.92 | 1.05 | 101 | P1_2-1194_3MINDEN_LA!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1194_3MINDEN_LA! | G_1ISES U2 ID 1 |  | VH
209791 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.056 | 1.0256 | 0.92 | 1.05 | 102 | P1_2-1194_3MINDEN_LA!+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1194_3MINDEN_LA! | G_1MCCLELAN U1 ID 1 |  | VH
209792 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0516 | 1.0388 | 0.92 | 1.05 | 108 | P1_2-1208_7SAREPTA%, LONGWD 7+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1208_7SAREPTA%, LONGWD 7 | G_1ISES U1 ID 1 |  | VH
209793 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0536 | 1.0377 | 0.92 | 1.05 | 109 | P1_2-1208_7SAREPTA%, LONGWD 7+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1208_7SAREPTA%, LONGWD 7 | G_1ISES U2 ID 1 |  | VH
209794 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 109 | P1_2-1208_7SAREPTA%, LONGWD 7+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1208_7SAREPTA%, LONGWD 7 | G_1ISES U2 ID 1 |  | VH
209795 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0579 | 1.0256 | 0.92 | 1.05 | 110 | P1_2-1208_7SAREPTA%, LONGWD 7+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1208_7SAREPTA%, LONGWD 7 | G_1MCCLELAN U1 ID 1 |  | VH
209796 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.0601 | 1.032 | 0.92 | 1.05 | 121 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
209797 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.0601 | 1.032 | 0.92 | 1.05 | 121 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
209798 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.0601 | 1.032 | 0.92 | 1.05 | 121 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U1 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U1 ID 1 |  | VH
209799 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.06 | 1.032 | 0.92 | 1.05 | 122 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
209800 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.06 | 1.032 | 0.92 | 1.05 | 122 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
209801 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.06 | 1.032 | 0.92 | 1.05 | 122 | P1_2-1350_8HS EHV%, 8ETTA%+G_1WHT BLUF U2 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1WHT BLUF U2 ID 1 |  | VH
209802 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 123 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U1 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U1 ID 1 |  | VH
209803 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 123 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U1 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U1 ID 1 |  | VH
209804 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 123 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U1 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U1 ID 1 |  | VH
209805 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 124 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U2 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U2 ID 1 |  | VH
209806 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 124 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U2 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U2 ID 1 |  | VH
209807 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 124 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ANO U2 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ANO U2 ID 1 |  | VH
209808 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 125 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ISES U2 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ISES U2 ID 1 |  | VH
209809 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 125 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ISES U2 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ISES U2 ID 1 |  | VH
209810 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.0577 | 1.032 | 0.92 | 1.05 | 125 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ISES U2 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ISES U2 ID 1 |  | VH
209811 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0511 | 1.0377 | 0.92 | 1.05 | 125 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ISES U2 ID 1 |  | VH
209812 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0512 | 1.0378 | 0.92 | 1.05 | 125 | P1_2-1350_8HS EHV%, 8ETTA%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1ISES U2 ID 1 |  | VH
209813 | 18L | Proposed | P3 | 40 | 8ETTA% | VH |  |  |  |  | 1.0595 | 1.032 | 0.92 | 1.05 | 126 | P1_2-1350_8HS EHV%, 8ETTA%+G_1MCCLELAN U1 ID 1 | 337754 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1MCCLELAN U1 ID 1 |  | VH
209814 | 18L | Proposed | P3 | 40 | 8DUKE HS-1! | VH |  |  |  |  | 1.0595 | 1.032 | 0.92 | 1.05 | 126 | P1_2-1350_8HS EHV%, 8ETTA%+G_1MCCLELAN U1 ID 1 | 337755 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1MCCLELAN U1 ID 1 |  | VH
209815 | 18L | Proposed | P3 | 40 | 8DUKE HS-2! | VH |  |  |  |  | 1.0595 | 1.032 | 0.92 | 1.05 | 126 | P1_2-1350_8HS EHV%, 8ETTA%+G_1MCCLELAN U1 ID 1 | 337756 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1MCCLELAN U1 ID 1 |  | VH
209816 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0611 | 1.0256 | 0.92 | 1.05 | 126 | P1_2-1350_8HS EHV%, 8ETTA%+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1350_8HS EHV%, 8ETTA% | G_1MCCLELAN U1 ID 1 |  | VH
209817 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0502 | 1.0377 | 0.92 | 1.05 | 130 | P1_2-1461_3SRCY PRICE!, 5SRCY PRICE!+113 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1461_3SRCY PRICE!, 5SRCY PRICE! | G_1ISES U2 ID 1 |  | VH
209818 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0503 | 1.0378 | 0.92 | 1.05 | 130 | P1_2-1461_3SRCY PRICE!, 5SRCY PRICE!+113 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1461_3SRCY PRICE!, 5SRCY PRICE! | G_1ISES U2 ID 1 |  | VH
209819 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0518 | 1.0388 | 0.92 | 1.05 | 134 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1NM G1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1NM G1 ID 1 |  | VH
209820 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 135 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1WHT BLUF U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1WHT BLUF U1 ID 1 |  | VH
209821 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0537 | 1.0377 | 0.92 | 1.05 | 137 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1ISES U2 ID 1 |  | VH
209822 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 137 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1ISES U2 ID 1 |  | VH
209823 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0532 | 1.0388 | 0.92 | 1.05 | 137 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1ISES U2 ID 1 |  | VH
209824 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0581 | 1.0256 | 0.92 | 1.05 | 138 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1MCCLELAN U1 ID 1 |  | VH
209825 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0518 | 1.0388 | 0.92 | 1.05 | 138 | P1_2-1492_5ISES-1!, 5ISES-2!+G_1MCCLELAN U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_1MCCLELAN U1 ID 1 |  | VH
209826 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.052 | 1.0388 | 0.92 | 1.05 | 139 | P1_2-1492_5ISES-1!, 5ISES-2!+G_NFK #1 1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1492_5ISES-1!, 5ISES-2! | G_NFK #1 1 ID 1 |  | VH
209827 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0522 | 1.0377 | 0.92 | 1.05 | 140 | P1_2-1494_8ISES%+G_1NM G1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1NM G1 ID 1 |  | VH
209828 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0523 | 1.0378 | 0.92 | 1.05 | 140 | P1_2-1494_8ISES%+G_1NM G1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1NM G1 ID 1 |  | VH
209829 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.056 | 1.0377 | 0.92 | 1.05 | 141 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
209830 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0561 | 1.0378 | 0.92 | 1.05 | 141 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
209831 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0611 | 1.0485 | 0.92 | 1.05 | 141 | P1_2-1494_8ISES%+G_1WHT BLUF U1 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U1 ID 1 |  | VH
209832 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0557 | 1.0377 | 0.92 | 1.05 | 142 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
209833 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0557 | 1.0378 | 0.92 | 1.05 | 142 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
209834 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0607 | 1.0485 | 0.92 | 1.05 | 142 | P1_2-1494_8ISES%+G_1WHT BLUF U2 ID 1 | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WHT BLUF U2 ID 1 |  | VH
209835 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0537 | 1.0377 | 0.92 | 1.05 | 143 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
209836 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 143 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
209837 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0532 | 1.0388 | 0.92 | 1.05 | 143 | P1_2-1494_8ISES%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1ISES U1 ID 1 |  | VH
209838 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0538 | 1.0377 | 0.92 | 1.05 | 144 | P1_2-1494_8ISES%+G_1MCCLELAN U1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1MCCLELAN U1 ID 1 |  | VH
209839 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0538 | 1.0378 | 0.92 | 1.05 | 144 | P1_2-1494_8ISES%+G_1MCCLELAN U1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1MCCLELAN U1 ID 1 |  | VH
209840 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0592 | 1.0256 | 0.92 | 1.05 | 144 | P1_2-1494_8ISES%+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1MCCLELAN U1 ID 1 |  | VH
209841 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.05 | 1.0388 | 0.92 | 1.05 | 144 | P1_2-1494_8ISES%+G_1MCCLELAN U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1MCCLELAN U1 ID 1 |  | VH
209842 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 145 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 1 |  | VH
209843 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 145 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 1 |  | VH
209844 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 145 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 1 |  | VH
209845 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 146 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 2 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 2 |  | VH
209846 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 146 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 2 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 2 |  | VH
209847 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 146 | P1_2-1494_8ISES%+G_1WRIGHTS C1 ID 2 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C1 ID 2 |  | VH
209848 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 147 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 1 |  | VH
209849 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 147 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 1 |  | VH
209850 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 147 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 1 |  | VH
209851 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 148 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 2 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 2 |  | VH
209852 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 148 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 2 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 2 |  | VH
209853 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 148 | P1_2-1494_8ISES%+G_1WRIGHTS C3 ID 2 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C3 ID 2 |  | VH
209854 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 149 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 1 |  | VH
209855 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 149 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 1 |  | VH
209856 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 149 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 1 |  | VH
209857 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 150 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 2 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 2 |  | VH
209858 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 150 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 2 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 2 |  | VH
209859 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 150 | P1_2-1494_8ISES%+G_1WRIGHTS C5 ID 2 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C5 ID 2 |  | VH
209860 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0543 | 1.0377 | 0.92 | 1.05 | 151 | P1_2-1494_8ISES%+G_1WRIGHTS S1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S1 ID 1 |  | VH
209861 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0544 | 1.0378 | 0.92 | 1.05 | 151 | P1_2-1494_8ISES%+G_1WRIGHTS S1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S1 ID 1 |  | VH
209862 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0504 | 1.0388 | 0.92 | 1.05 | 151 | P1_2-1494_8ISES%+G_1WRIGHTS S1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S1 ID 1 |  | VH
209863 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0546 | 1.0377 | 0.92 | 1.05 | 152 | P1_2-1494_8ISES%+G_1WRIGHTS C7 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C7 ID 1 |  | VH
209864 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0547 | 1.0378 | 0.92 | 1.05 | 152 | P1_2-1494_8ISES%+G_1WRIGHTS C7 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C7 ID 1 |  | VH
209865 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0507 | 1.0388 | 0.92 | 1.05 | 152 | P1_2-1494_8ISES%+G_1WRIGHTS C7 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS C7 ID 1 |  | VH
209866 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0543 | 1.0377 | 0.92 | 1.05 | 153 | P1_2-1494_8ISES%+G_1WRIGHTS S2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S2 ID 1 |  | VH
209867 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0544 | 1.0378 | 0.92 | 1.05 | 153 | P1_2-1494_8ISES%+G_1WRIGHTS S2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S2 ID 1 |  | VH
209868 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0504 | 1.0388 | 0.92 | 1.05 | 153 | P1_2-1494_8ISES%+G_1WRIGHTS S2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_1WRIGHTS S2 ID 1 |  | VH
209869 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0522 | 1.0377 | 0.92 | 1.05 | 154 | P1_2-1494_8ISES%+G_NFK #1 1 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_NFK #1 1 ID 1 |  | VH
209870 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0523 | 1.0378 | 0.92 | 1.05 | 154 | P1_2-1494_8ISES%+G_NFK #1 1 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1494_8ISES% | G_NFK #1 1 ID 1 |  | VH
209871 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0513 | 1.0388 | 0.92 | 1.05 | 157 | P1_2-1532_5JIM HILL%, 3JIM HILL!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%, 3JIM HILL! | G_1ISES U1 ID 1 |  | VH
209872 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 158 | P1_2-1532_5JIM HILL%, 3JIM HILL!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%, 3JIM HILL! | G_1ISES U2 ID 1 |  | VH
209873 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0533 | 1.0378 | 0.92 | 1.05 | 158 | P1_2-1532_5JIM HILL%, 3JIM HILL!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%, 3JIM HILL! | G_1ISES U2 ID 1 |  | VH
209874 | 18L | Proposed | P3 | 40 | 3CORNING | VH |  |  |  |  | 1.0547 | 1.0437 | 0.92 | 1.05 | 158 | P1_2-1532_5JIM HILL%, 3JIM HILL!+G_1ISES U2 ID 1 | 338228 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%, 3JIM HILL! | G_1ISES U2 ID 1 |  | VH
209875 | 18L | Proposed | P3 | 40 | 3CORNING.N# | VH |  |  |  |  | 1.0551 | 1.0444 | 0.92 | 1.05 | 158 | P1_2-1532_5JIM HILL%, 3JIM HILL!+G_1ISES U2 ID 1 | 338691 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1532_5JIM HILL%, 3JIM HILL! | G_1ISES U2 ID 1 |  | VH
209876 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.063 | 1.0256 | 0.92 | 1.05 | 160 | P1_2-1551_3MCCLELLAN#!+G_1WHT BLUF U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1WHT BLUF U1 ID 1 |  | VH
209877 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0627 | 1.0256 | 0.92 | 1.05 | 161 | P1_2-1551_3MCCLELLAN#!+G_1WHT BLUF U2 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1WHT BLUF U2 ID 1 |  | VH
209878 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0581 | 1.0256 | 0.92 | 1.05 | 162 | P1_2-1551_3MCCLELLAN#!+G_1ISES U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U1 ID 1 |  | VH
209879 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0518 | 1.0388 | 0.92 | 1.05 | 162 | P1_2-1551_3MCCLELLAN#!+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U1 ID 1 |  | VH
209880 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0538 | 1.0377 | 0.92 | 1.05 | 163 | P1_2-1551_3MCCLELLAN#!+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U2 ID 1 |  | VH
209881 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0538 | 1.0378 | 0.92 | 1.05 | 163 | P1_2-1551_3MCCLELLAN#!+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U2 ID 1 |  | VH
209882 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0592 | 1.0256 | 0.92 | 1.05 | 163 | P1_2-1551_3MCCLELLAN#!+G_1ISES U2 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U2 ID 1 |  | VH
209883 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.05 | 1.0388 | 0.92 | 1.05 | 163 | P1_2-1551_3MCCLELLAN#!+G_1ISES U2 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1551_3MCCLELLAN#! | G_1ISES U2 ID 1 |  | VH
209884 | 18L | Proposed | P3 | 40 | 8WEAKLEY TN | VH |  |  |  |  | 1.094 | 1.0752 | 0.92 | 1.05 | 164 | P1_2-1565_8SHELBYTN!, 8LAG CRK CT%+114 | 360017 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | G_1PLUM PT U1 ID 1 |  | VH
209885 | 18L | Proposed | P3 | 40 | 8LAG CRK CT | VH |  |  |  |  | 1.1012 | 1.0679 | 0.92 | 1.05 | 164 | P1_2-1565_8SHELBYTN!, 8LAG CRK CT%+114 | 360568 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | G_1PLUM PT U1 ID 1 |  | VH
209886 | 18L | Proposed | P3 | 40 | 8GLEASON CT | VH |  |  |  |  | 1.0939 | 1.0778 | 0.92 | 1.05 | 164 | P1_2-1565_8SHELBYTN!, 8LAG CRK CT%+114 | 360582 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | G_1PLUM PT U1 ID 1 |  | VH
209887 | 18L | Proposed | P3 | 40 | 8LAG CRK CC | VH |  |  |  |  | 1.1012 | 1.0679 | 0.92 | 1.05 | 164 | P1_2-1565_8SHELBYTN!, 8LAG CRK CT%+114 | 360615 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1565_8SHELBYTN!, 8LAG CRK CT% | G_1PLUM PT U1 ID 1 |  | VH
209888 | 18L | Proposed | P3 | 40 | 8DANIEL | VH |  |  |  |  | 1.0826 | 1.0287 | 0.92 | 1.05 | 165 | P1_2-1607_8DANIEL%, 6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%, 6DANIEL! | G_1GGNS U1 ID 1 |  | VH
209889 | 18L | Proposed | P3 | 40 | CLARN 4 | VH |  |  |  |  | 1.0549 | 1.0444 | 0.92 | 1.05 | 173 | P1_2-1640_CLARN 4!, NATCH 4!+G_G1NESBIT! ID 1 | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!, NATCH 4! | G_G1NESBIT! ID 1 |  | VH
209890 | 18L | Proposed | P3 | 40 | CLARN 4 | VH |  |  |  |  | 1.0547 | 1.0444 | 0.92 | 1.05 | 174 | P1_2-1640_CLARN 4!, NATCH 4!+G_G2RODEMR! ID 1 | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!, NATCH 4! | G_G2RODEMR! ID 1 |  | VH
209891 | 18L | Proposed | P3 | 40 | CLARN 4 | VH |  |  |  |  | 1.0556 | 1.0444 | 0.92 | 1.05 | 175 | P1_2-1640_CLARN 4!, NATCH 4!+G_G3MADISN! ID 1 | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!, NATCH 4! | G_G3MADISN! ID 1 |  | VH
209906 | 18L | Proposed | P3 | 40 | 4CANEY | VL |  |  |  |  | 0.9188 | 0.9929 | 0.92 | 1.05 | 190 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
209907 | 18L | Proposed | P3 | 40 | PNPRARIE 4 | VL |  |  |  |  | 0.912 | 0.9978 | 0.92 | 1.05 | 190 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_4RAYBURN% ID 1 | Project External |  | Messick 500/230
209923 | 18L | Proposed | P3 | 40 | 4CANEY | VL |  |  |  |  | 0.9197 | 0.9929 | 0.92 | 1.05 | 206 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G4! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1NELSON_G4! ID 1 | Project External |  | Messick 500/230
209925 | 18L | Proposed | P3 | 40 | 4CANEY | VL |  |  |  |  | 0.918 | 0.9929 | 0.92 | 1.05 | 207 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1NELSON_G6! ID 1 | Project External |  | Messick 500/230
209926 | 18L | Proposed | P3 | 40 | OAKDALE4 | VL |  |  |  |  | 0.9198 | 0.9925 | 0.92 | 1.05 | 207 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1NELSON_G6! ID 1 | Project External |  | Messick 500/230
209927 | 18L | Proposed | P3 | 40 | PNPRARIE 4 | VL |  |  |  |  | 0.9112 | 0.9978 | 0.92 | 1.05 | 207 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1NELSON_G6! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1NELSON_G6! ID 1 | Project External |  | Messick 500/230
209965 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0512 | 1.0388 | 0.92 | 1.05 | 245 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1ISES U1 ID 1 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1ISES U1 ID 1 |  | VH
209967 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 246 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1ISES U2 ID 1 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1ISES U2 ID 1 |  | VH
209968 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0533 | 1.0378 | 0.92 | 1.05 | 246 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_1ISES U2 ID 1 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_1ISES U2 ID 1 |  | VH
209973 | 18L | Proposed | P3 | 40 | 4CANEY | VL |  |  |  |  | 0.9195 | 0.9929 | 0.92 | 1.05 | 250 | P1_2-1656_COUGH 4!, PNPRARIE 4%+G_G1DOLHIL! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!, PNPRARIE 4% | G_G1DOLHIL! ID 1 | Project External |  | Messick 500/230
209981 | 18L | Proposed | P3 | 40 | FTSMITH7 | VH |  |  |  |  | 1.0571 | 1.0376 | 0.92 | 1.05 | 268 | P1_2-1892_FTSMITH7%, FTSMITH8%+G_MUSKOG4G ID 1 | 515302 |  |  |  | 345 | 345 | 524 | OKGE |  |  | P1_2-1892_FTSMITH7%, FTSMITH8% | G_MUSKOG4G ID 1 |  | VH
209982 | 18L | Proposed | P3 | 40 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0516 | 1.0384 | 0.92 | 1.05 | 281 | G_1WHT BLUF U1 ID 1+1299 | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1WHT BLUF U1 ID 1 |  | VH
209983 | 18L | Proposed | P3 | 40 | 3BRINKLEY.W | VH |  |  |  |  | 1.0504 | 1.0375 | 0.92 | 1.05 | 281 | G_1WHT BLUF U1 ID 1+1299 | 338014 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1WHT BLUF U1 ID 1 |  | VH
209984 | 18L | Proposed | P3 | 40 | 3HORN LAKE! | VH |  |  |  |  | 1.0514 | 1.0403 | 0.92 | 1.05 | 282 | G_1WHT BLUF U1 ID 1+1307 | 337150 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1WHT BLUF U1 ID 1 |  | VH
209985 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0515 | 1.0355 | 0.92 | 1.05 | 284 | G_1WHT BLUF U1 ID 1+1439 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1284_3MONTCELO.E!, 3CROSSETT.N! | G_1WHT BLUF U1 ID 1 |  | VH
209986 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0513 | 1.0355 | 0.92 | 1.05 | 285 | G_1WHT BLUF U1 ID 1+P1_2-1286_3CROSSETT.N! | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1286_3CROSSETT.N! | G_1WHT BLUF U1 ID 1 |  | VH
209987 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0506 | 1.0355 | 0.92 | 1.05 | 286 | G_1WHT BLUF U1 ID 1+1462 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
209988 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0506 | 1.0355 | 0.92 | 1.05 | 287 | G_1WHT BLUF U1 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1WHT BLUF U1 ID 1 |  | VH
209989 | 18L | Proposed | P3 | 40 | 3RICUSKEY! | VH |  |  |  |  | 1.0507 | 1.0356 | 0.92 | 1.05 | 288 | G_1WHT BLUF U1 ID 1+1599 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!, 3GILLETT! | G_1WHT BLUF U1 ID 1 |  | VH
209990 | 18L | Proposed | P3 | 40 | 3RICUSKEY! | VH |  |  |  |  | 1.053 | 1.0356 | 0.92 | 1.05 | 289 | G_1WHT BLUF U1 ID 1+1600 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1WHT BLUF U1 ID 1 |  | VH
209991 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0547 | 1.0388 | 0.92 | 1.05 | 290 | G_1WHT BLUF U1 ID 1+1612 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WHT BLUF U1 ID 1 |  | VH
209992 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0596 | 1.0439 | 0.92 | 1.05 | 290 | G_1WHT BLUF U1 ID 1+1612 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WHT BLUF U1 ID 1 |  | VH
209993 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0587 | 1.0485 | 0.92 | 1.05 | 291 | G_1WHT BLUF U1 ID 1+P1_2-1561_8SHELBYTN! | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1561_8SHELBYTN! | G_1WHT BLUF U1 ID 1 |  | VH
209994 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0585 | 1.0485 | 0.92 | 1.05 | 292 | G_1WHT BLUF U1 ID 1+P1_2-1562_8SHELBYTN! | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1562_8SHELBYTN! | G_1WHT BLUF U1 ID 1 |  | VH
209995 | 18L | Proposed | P3 | 40 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0514 | 1.0384 | 0.92 | 1.05 | 294 | G_1WHT BLUF U2 ID 1+1299 | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1WHT BLUF U2 ID 1 |  | VH
209996 | 18L | Proposed | P3 | 40 | 3BRINKLEY.W | VH |  |  |  |  | 1.0502 | 1.0375 | 0.92 | 1.05 | 294 | G_1WHT BLUF U2 ID 1+1299 | 338014 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1WHT BLUF U2 ID 1 |  | VH
209997 | 18L | Proposed | P3 | 40 | 3HORN LAKE! | VH |  |  |  |  | 1.0513 | 1.0403 | 0.92 | 1.05 | 295 | G_1WHT BLUF U2 ID 1+1307 | 337150 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1WHT BLUF U2 ID 1 |  | VH
209998 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0513 | 1.0355 | 0.92 | 1.05 | 296 | G_1WHT BLUF U2 ID 1+1439 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1284_3MONTCELO.E!, 3CROSSETT.N! | G_1WHT BLUF U2 ID 1 |  | VH
209999 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0511 | 1.0355 | 0.92 | 1.05 | 297 | G_1WHT BLUF U2 ID 1+P1_2-1286_3CROSSETT.N! | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1286_3CROSSETT.N! | G_1WHT BLUF U2 ID 1 |  | VH
210000 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0504 | 1.0355 | 0.92 | 1.05 | 298 | G_1WHT BLUF U2 ID 1+1462 | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
210001 | 18L | Proposed | P3 | 40 | 2GLENDALE-1 | VH |  |  |  |  | 1.0504 | 1.0355 | 0.92 | 1.05 | 299 | G_1WHT BLUF U2 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338544 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1WHT BLUF U2 ID 1 |  | VH
210002 | 18L | Proposed | P3 | 40 | 3RICUSKEY! | VH |  |  |  |  | 1.0504 | 1.0356 | 0.92 | 1.05 | 300 | G_1WHT BLUF U2 ID 1+1599 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!, 3GILLETT! | G_1WHT BLUF U2 ID 1 |  | VH
210003 | 18L | Proposed | P3 | 40 | 3RICUSKEY! | VH |  |  |  |  | 1.0527 | 1.0356 | 0.92 | 1.05 | 301 | G_1WHT BLUF U2 ID 1+1600 | 337967 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1WHT BLUF U2 ID 1 |  | VH
210004 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0545 | 1.0388 | 0.92 | 1.05 | 302 | G_1WHT BLUF U2 ID 1+1612 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WHT BLUF U2 ID 1 |  | VH
210005 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0594 | 1.0439 | 0.92 | 1.05 | 302 | G_1WHT BLUF U2 ID 1+1612 | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WHT BLUF U2 ID 1 |  | VH
210006 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0514 | 1.0388 | 0.92 | 1.05 | 308 | G_1ISES U1 ID 1+P1_2-12_7STFRAN!, 7GOBKNOB% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-12_7STFRAN!, 7GOBKNOB% | G_1ISES U1 ID 1 |  | VH
210007 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0518 | 1.0388 | 0.92 | 1.05 | 309 | G_1ISES U1 ID 1+P1_2-28_5NEWMAD! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-28_5NEWMAD! | G_1ISES U1 ID 1 |  | VH
210008 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0545 | 1.0664 | 0.92 | 1.05 | 310 | G_1ISES U1 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%, 5THAYER.S! | G_1ISES U1 ID 1 |  | VH
210009 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0505 | 1.0388 | 0.92 | 1.05 | 310 | G_1ISES U1 ID 1+P1_2-64_5COXCRK%, 5THAYER.S! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-64_5COXCRK%, 5THAYER.S! | G_1ISES U1 ID 1 |  | VH
210010 | 18L | Proposed | P3 | 40 | 3BRINKLEY.E! | VH |  |  |  |  | 1.0502 | 1.0384 | 0.92 | 1.05 | 311 | G_1ISES U1 ID 1+P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | 337996 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1ISES U1 ID 1 |  | VH
210011 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.053 | 1.0388 | 0.92 | 1.05 | 311 | G_1ISES U1 ID 1+P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1ISES U1 ID 1 |  | VH
210012 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0524 | 1.0388 | 0.92 | 1.05 | 312 | G_1ISES U1 ID 1+P1_2-1152_3GETWELL!, 3HORN LAKE! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1ISES U1 ID 1 |  | VH
210013 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0528 | 1.0388 | 0.92 | 1.05 | 313 | G_1ISES U1 ID 1+P1_2-1308_3PB IP SS%, 3PB ENERGY! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
210014 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0528 | 1.0388 | 0.92 | 1.05 | 314 | G_1ISES U1 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1ISES U1 ID 1 |  | VH
210015 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 315 | G_1ISES U1 ID 1+P1_2-1319_8WHT BLUFF% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U1 ID 1 |  | VH
210016 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0505 | 1.0388 | 0.92 | 1.05 | 317 | G_1ISES U1 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%, 8KEO% | G_1ISES U1 ID 1 |  | VH
210017 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0534 | 1.0388 | 0.92 | 1.05 | 318 | G_1ISES U1 ID 1+P1_2-1396_8WRIGHTSVLE% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
210018 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0532 | 1.0388 | 0.92 | 1.05 | 319 | G_1ISES U1 ID 1+P1_2-1397_8WRIGHTSVLE% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
210019 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0533 | 1.0388 | 0.92 | 1.05 | 320 | G_1ISES U1 ID 1+P1_2-1398_8WRIGHTSVLE% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U1 ID 1 |  | VH
210020 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0544 | 1.0388 | 0.92 | 1.05 | 321 | G_1ISES U1 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%, 8KEO% | G_1ISES U1 ID 1 |  | VH
210021 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0541 | 1.0439 | 0.92 | 1.05 | 321 | G_1ISES U1 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%, 8KEO% | G_1ISES U1 ID 1 |  | VH
210022 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0521 | 1.0388 | 0.92 | 1.05 | 322 | G_1ISES U1 ID 1+P1_2-1419_5QUITMAN!, GREERSF5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1419_5QUITMAN!, GREERSF5! | G_1ISES U1 ID 1 |  | VH
210023 | 18L | Proposed | P3 | 40 | 8HOLND BTM% | VH |  |  |  |  | 1.0512 | 1.031 | 0.92 | 1.05 | 323 | G_1ISES U1 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
210024 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0528 | 1.0377 | 0.92 | 1.05 | 323 | G_1ISES U1 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
210025 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0529 | 1.0378 | 0.92 | 1.05 | 323 | G_1ISES U1 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
210026 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0526 | 1.0388 | 0.92 | 1.05 | 323 | G_1ISES U1 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U1 ID 1 |  | VH
210027 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0527 | 1.0388 | 0.92 | 1.05 | 324 | G_1ISES U1 ID 1+P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1ISES U1 ID 1 |  | VH
210028 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0525 | 1.0388 | 0.92 | 1.05 | 325 | G_1ISES U1 ID 1+P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | G_1ISES U1 ID 1 |  | VH
210029 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0616 | 1.0388 | 0.92 | 1.05 | 326 | G_1ISES U1 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U1 ID 1 |  | VH
210030 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0625 | 1.0439 | 0.92 | 1.05 | 326 | G_1ISES U1 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U1 ID 1 |  | VH
210031 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0599 | 1.0388 | 0.92 | 1.05 | 328 | G_1ISES U1 ID 1+P1_2-1468_5MOSES%, 5BAILEY#! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1468_5MOSES%, 5BAILEY#! | G_1ISES U1 ID 1 |  | VH
210032 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0528 | 1.0388 | 0.92 | 1.05 | 330 | G_1ISES U1 ID 1+P1_2-1486_5SAGE!, 5ISES-1! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1486_5SAGE!, 5ISES-1! | G_1ISES U1 ID 1 |  | VH
210033 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0526 | 1.0388 | 0.92 | 1.05 | 331 | G_1ISES U1 ID 1+P1_2-1502_5EBONY% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1502_5EBONY% | G_1ISES U1 ID 1 |  | VH
210034 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0519 | 1.0388 | 0.92 | 1.05 | 332 | G_1ISES U1 ID 1+P1_2-1510_5JONESBORO! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1510_5JONESBORO! | G_1ISES U1 ID 1 |  | VH
210035 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0515 | 1.0388 | 0.92 | 1.05 | 333 | G_1ISES U1 ID 1+P1_2-1511_5JONESBORO!, 5PARAGOULD% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1511_5JONESBORO!, 5PARAGOULD% | G_1ISES U1 ID 1 |  | VH
210036 | 18L | Proposed | P3 | 40 | 5JONESBORO! | VH |  |  |  |  | 1.0526 | 1.0408 | 0.92 | 1.05 | 334 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!, HERGETT5! | G_1ISES U1 ID 1 |  | VH
210037 | 18L | Proposed | P3 | 40 | 2JONSBORO.W | VH |  |  |  |  | 1.0526 | 1.0408 | 0.92 | 1.05 | 334 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!, HERGETT5! | G_1ISES U1 ID 1 |  | VH
210038 | 18L | Proposed | P3 | 40 | 5JONSBORO.W# | VH |  |  |  |  | 1.0526 | 1.0408 | 0.92 | 1.05 | 334 | G_1ISES U1 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!, HERGETT5! | G_1ISES U1 ID 1 |  | VH
210039 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0516 | 1.0388 | 0.92 | 1.05 | 335 | G_1ISES U1 ID 1+P1_2-1531_5JIM HILL%, 5PARAGOULD% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1531_5JIM HILL%, 5PARAGOULD% | G_1ISES U1 ID 1 |  | VH
210040 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0511 | 1.0388 | 0.92 | 1.05 | 336 | G_1ISES U1 ID 1+P1_2-1533_5PARAGOULD%, 3PARAGOULD! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1533_5PARAGOULD%, 3PARAGOULD! | G_1ISES U1 ID 1 |  | VH
210041 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0515 | 1.0388 | 0.92 | 1.05 | 337 | G_1ISES U1 ID 1+1685 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!, 3WALNUT RDG! | G_1ISES U1 ID 1 |  | VH
210042 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0513 | 1.0388 | 0.92 | 1.05 | 338 | G_1ISES U1 ID 1+1686 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG% | G_1ISES U1 ID 1 |  | VH
210043 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0506 | 1.0388 | 0.92 | 1.05 | 339 | G_1ISES U1 ID 1+P1_2-1536_5WALNUT RDG%, 5THAYER.S! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1536_5WALNUT RDG%, 5THAYER.S! | G_1ISES U1 ID 1 |  | VH
210044 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.054 | 1.0388 | 0.92 | 1.05 | 340 | G_1ISES U1 ID 1+P1_2-1561_8SHELBYTN! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1561_8SHELBYTN! | G_1ISES U1 ID 1 |  | VH
210045 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0545 | 1.0439 | 0.92 | 1.05 | 340 | G_1ISES U1 ID 1+P1_2-1561_8SHELBYTN! | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1561_8SHELBYTN! | G_1ISES U1 ID 1 |  | VH
210046 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0538 | 1.0388 | 0.92 | 1.05 | 341 | G_1ISES U1 ID 1+P1_2-1562_8SHELBYTN! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1562_8SHELBYTN! | G_1ISES U1 ID 1 |  | VH
210047 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0543 | 1.0439 | 0.92 | 1.05 | 341 | G_1ISES U1 ID 1+P1_2-1562_8SHELBYTN! | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1562_8SHELBYTN! | G_1ISES U1 ID 1 |  | VH
210048 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0533 | 1.0388 | 0.92 | 1.05 | 342 | G_1ISES U1 ID 1+P1_2-1569_8CORDOVA TN! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1569_8CORDOVA TN! | G_1ISES U1 ID 1 |  | VH
210049 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.053 | 1.0388 | 0.92 | 1.05 | 343 | G_1ISES U1 ID 1+P1_2-1570_8CORDOVA TN! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1570_8CORDOVA TN! | G_1ISES U1 ID 1 |  | VH
210050 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0519 | 1.0388 | 0.92 | 1.05 | 344 | G_1ISES U1 ID 1+P1_2-1755_PARAGLD5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1755_PARAGLD5! | G_1ISES U1 ID 1 |  | VH
210051 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0521 | 1.0388 | 0.92 | 1.05 | 345 | G_1ISES U1 ID 1+P1_2-1757_PARAGLD5!, CENTR H5 | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1757_PARAGLD5!, CENTR H5 | G_1ISES U1 ID 1 |  | VH
210052 | 18L | Proposed | P3 | 40 | 5JONESBORO! | VH |  |  |  |  | 1.0515 | 1.0408 | 0.92 | 1.05 | 346 | G_1ISES U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U1 ID 1 |  | VH
210053 | 18L | Proposed | P3 | 40 | 2JONSBORO.W | VH |  |  |  |  | 1.0515 | 1.0408 | 0.92 | 1.05 | 346 | G_1ISES U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U1 ID 1 |  | VH
210054 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0524 | 1.0388 | 0.92 | 1.05 | 346 | G_1ISES U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U1 ID 1 |  | VH
210055 | 18L | Proposed | P3 | 40 | 5JONSBORO.W# | VH |  |  |  |  | 1.0515 | 1.0408 | 0.92 | 1.05 | 346 | G_1ISES U1 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U1 ID 1 |  | VH
210056 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0517 | 1.0388 | 0.92 | 1.05 | 347 | G_1ISES U1 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U1 ID 1 |  | VH
210057 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0519 | 1.0388 | 0.92 | 1.05 | 348 | G_1ISES U1 ID 1+P1_2-1769_INDEPCO5!, GREERSF5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1769_INDEPCO5!, GREERSF5! | G_1ISES U1 ID 1 |  | VH
210058 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.052 | 1.0388 | 0.92 | 1.05 | 349 | G_1ISES U1 ID 1+P1_2-1779_NORFORK5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1779_NORFORK5! | G_1ISES U1 ID 1 |  | VH
210059 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0526 | 1.0388 | 0.92 | 1.05 | 350 | G_1ISES U1 ID 1+P1_2-1783_NORFORK5!, BULL SH5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1783_NORFORK5!, BULL SH5! | G_1ISES U1 ID 1 |  | VH
210060 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0516 | 1.0388 | 0.92 | 1.05 | 351 | G_1ISES U1 ID 1+P1_2-1784_BULL SH5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1784_BULL SH5! | G_1ISES U1 ID 1 |  | VH
210061 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0522 | 1.0377 | 0.92 | 1.05 | 352 | G_1ISES U2 ID 1+P1_2-28_5NEWMAD! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-28_5NEWMAD! | G_1ISES U2 ID 1 |  | VH
210062 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0523 | 1.0378 | 0.92 | 1.05 | 352 | G_1ISES U2 ID 1+P1_2-28_5NEWMAD! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-28_5NEWMAD! | G_1ISES U2 ID 1 |  | VH
210063 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0527 | 1.0377 | 0.92 | 1.05 | 353 | G_1ISES U2 ID 1+P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1ISES U2 ID 1 |  | VH
210064 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0527 | 1.0378 | 0.92 | 1.05 | 353 | G_1ISES U2 ID 1+P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1144_6MOONLAKE%, 6RITCHIE-2! | G_1ISES U2 ID 1 |  | VH
210065 | 18L | Proposed | P3 | 40 | 3HORN LAKE! | VH |  |  |  |  | 1.0511 | 1.0403 | 0.92 | 1.05 | 354 | G_1ISES U2 ID 1+P1_2-1152_3GETWELL!, 3HORN LAKE! | 337150 |  |  |  | 115 | 115 | 326 | EES-EMI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1ISES U2 ID 1 |  | VH
210066 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 354 | G_1ISES U2 ID 1+P1_2-1152_3GETWELL!, 3HORN LAKE! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1ISES U2 ID 1 |  | VH
210067 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 354 | G_1ISES U2 ID 1+P1_2-1152_3GETWELL!, 3HORN LAKE! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1ISES U2 ID 1 |  | VH
210068 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0507 | 1.0388 | 0.92 | 1.05 | 354 | G_1ISES U2 ID 1+P1_2-1152_3GETWELL!, 3HORN LAKE! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1152_3GETWELL!, 3HORN LAKE! | G_1ISES U2 ID 1 |  | VH
210069 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0545 | 1.0377 | 0.92 | 1.05 | 355 | G_1ISES U2 ID 1+P1_2-1241_8STERLING%, 8EL DORADO% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1241_8STERLING%, 8EL DORADO% | G_1ISES U2 ID 1 |  | VH
210070 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0545 | 1.0378 | 0.92 | 1.05 | 355 | G_1ISES U2 ID 1+P1_2-1241_8STERLING%, 8EL DORADO% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1241_8STERLING%, 8EL DORADO% | G_1ISES U2 ID 1 |  | VH
210071 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0507 | 1.0388 | 0.92 | 1.05 | 355 | G_1ISES U2 ID 1+P1_2-1241_8STERLING%, 8EL DORADO% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1241_8STERLING%, 8EL DORADO% | G_1ISES U2 ID 1 |  | VH
210072 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0546 | 1.0377 | 0.92 | 1.05 | 356 | G_1ISES U2 ID 1+P1_2-1308_3PB IP SS%, 3PB ENERGY! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210073 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0547 | 1.0378 | 0.92 | 1.05 | 356 | G_1ISES U2 ID 1+P1_2-1308_3PB IP SS%, 3PB ENERGY! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210074 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0511 | 1.0388 | 0.92 | 1.05 | 356 | G_1ISES U2 ID 1+P1_2-1308_3PB IP SS%, 3PB ENERGY! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210075 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0546 | 1.0377 | 0.92 | 1.05 | 357 | G_1ISES U2 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210076 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0547 | 1.0378 | 0.92 | 1.05 | 357 | G_1ISES U2 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210077 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0511 | 1.0388 | 0.92 | 1.05 | 357 | G_1ISES U2 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1ISES U2 ID 1 |  | VH
210078 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.056 | 1.0377 | 0.92 | 1.05 | 358 | G_1ISES U2 ID 1+P1_2-1319_8WHT BLUFF% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210079 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0561 | 1.0378 | 0.92 | 1.05 | 358 | G_1ISES U2 ID 1+P1_2-1319_8WHT BLUFF% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210080 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0611 | 1.0485 | 0.92 | 1.05 | 358 | G_1ISES U2 ID 1+P1_2-1319_8WHT BLUFF% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210081 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0557 | 1.0377 | 0.92 | 1.05 | 359 | G_1ISES U2 ID 1+P1_2-1320_8WHT BLUFF% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210082 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0557 | 1.0378 | 0.92 | 1.05 | 359 | G_1ISES U2 ID 1+P1_2-1320_8WHT BLUFF% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210083 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0607 | 1.0485 | 0.92 | 1.05 | 359 | G_1ISES U2 ID 1+P1_2-1320_8WHT BLUFF% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1ISES U2 ID 1 |  | VH
210084 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0564 | 1.0377 | 0.92 | 1.05 | 360 | G_1ISES U2 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210085 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0565 | 1.0378 | 0.92 | 1.05 | 360 | G_1ISES U2 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210086 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0609 | 1.0485 | 0.92 | 1.05 | 360 | G_1ISES U2 ID 1+P1_2-1321_8WHT BLUFF%, 8KEO% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1321_8WHT BLUFF%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210087 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0542 | 1.0377 | 0.92 | 1.05 | 361 | G_1ISES U2 ID 1+P1_2-1396_8WRIGHTSVLE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210088 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0543 | 1.0378 | 0.92 | 1.05 | 361 | G_1ISES U2 ID 1+P1_2-1396_8WRIGHTSVLE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210089 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0588 | 1.0485 | 0.92 | 1.05 | 361 | G_1ISES U2 ID 1+P1_2-1396_8WRIGHTSVLE% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210090 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.054 | 1.0377 | 0.92 | 1.05 | 362 | G_1ISES U2 ID 1+P1_2-1397_8WRIGHTSVLE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210091 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 362 | G_1ISES U2 ID 1+P1_2-1397_8WRIGHTSVLE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210092 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 363 | G_1ISES U2 ID 1+P1_2-1398_8WRIGHTSVLE% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210093 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 363 | G_1ISES U2 ID 1+P1_2-1398_8WRIGHTSVLE% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210094 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0586 | 1.0485 | 0.92 | 1.05 | 363 | G_1ISES U2 ID 1+P1_2-1398_8WRIGHTSVLE% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1ISES U2 ID 1 |  | VH
210095 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0558 | 1.0377 | 0.92 | 1.05 | 364 | G_1ISES U2 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210096 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0559 | 1.0378 | 0.92 | 1.05 | 364 | G_1ISES U2 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210097 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0593 | 1.0485 | 0.92 | 1.05 | 364 | G_1ISES U2 ID 1+P1_2-1399_8WRIGHTSVLE%, 8KEO% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1399_8WRIGHTSVLE%, 8KEO% | G_1ISES U2 ID 1 |  | VH
210098 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0536 | 1.0377 | 0.92 | 1.05 | 365 | G_1ISES U2 ID 1+P1_2-1419_5QUITMAN!, GREERSF5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1419_5QUITMAN!, GREERSF5! | G_1ISES U2 ID 1 |  | VH
210099 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 365 | G_1ISES U2 ID 1+P1_2-1419_5QUITMAN!, GREERSF5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1419_5QUITMAN!, GREERSF5! | G_1ISES U2 ID 1 |  | VH
210100 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 366 | G_1ISES U2 ID 1+P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | G_1ISES U2 ID 1 |  | VH
210101 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 366 | G_1ISES U2 ID 1+P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | G_1ISES U2 ID 1 |  | VH
210102 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0591 | 1.0485 | 0.92 | 1.05 | 366 | G_1ISES U2 ID 1+P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | G_1ISES U2 ID 1 |  | VH
210103 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0503 | 1.0388 | 0.92 | 1.05 | 366 | G_1ISES U2 ID 1+P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1438_3JAXNVLE.N!, 3LYNCH-E! | G_1ISES U2 ID 1 |  | VH
210104 | 18L | Proposed | P3 | 40 | 5HOLND BTM! | VH |  |  |  |  | 1.0502 | 1.0311 | 0.92 | 1.05 | 367 | G_1ISES U2 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338015 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
210105 | 18L | Proposed | P3 | 40 | 8HOLND BTM% | VH |  |  |  |  | 1.0584 | 1.031 | 0.92 | 1.05 | 367 | G_1ISES U2 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338140 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
210106 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0617 | 1.0377 | 0.92 | 1.05 | 367 | G_1ISES U2 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
210107 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0618 | 1.0378 | 0.92 | 1.05 | 367 | G_1ISES U2 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
210108 | 18L | Proposed | P3 | 40 | 2WARD | VH |  |  |  |  | 1.0596 | 1.0485 | 0.92 | 1.05 | 367 | G_1ISES U2 ID 1+P1_2-1442_8KEO%, 8HOLND BTM% | 338583 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1442_8KEO%, 8HOLND BTM% | G_1ISES U2 ID 1 |  | VH
210109 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0536 | 1.0377 | 0.92 | 1.05 | 368 | G_1ISES U2 ID 1+P1_2-1445_3RICUSKEY!, 3GILLETT! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!, 3GILLETT! | G_1ISES U2 ID 1 |  | VH
210110 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 368 | G_1ISES U2 ID 1+P1_2-1445_3RICUSKEY!, 3GILLETT! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!, 3GILLETT! | G_1ISES U2 ID 1 |  | VH
210111 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 368 | G_1ISES U2 ID 1+P1_2-1445_3RICUSKEY!, 3GILLETT! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1445_3RICUSKEY!, 3GILLETT! | G_1ISES U2 ID 1 |  | VH
210112 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0538 | 1.0377 | 0.92 | 1.05 | 369 | G_1ISES U2 ID 1+P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210113 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0539 | 1.0378 | 0.92 | 1.05 | 369 | G_1ISES U2 ID 1+P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210114 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0509 | 1.0388 | 0.92 | 1.05 | 369 | G_1ISES U2 ID 1+P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1446_3RICUSKEY!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210115 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0535 | 1.0377 | 0.92 | 1.05 | 370 | G_1ISES U2 ID 1+P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210116 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0535 | 1.0378 | 0.92 | 1.05 | 370 | G_1ISES U2 ID 1+P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210117 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0506 | 1.0388 | 0.92 | 1.05 | 370 | G_1ISES U2 ID 1+P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1452_3HELENA.W!, 3BRINKLEY.E! | G_1ISES U2 ID 1 |  | VH
210118 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0537 | 1.0377 | 0.92 | 1.05 | 371 | G_1ISES U2 ID 1+P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
210119 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0537 | 1.0378 | 0.92 | 1.05 | 371 | G_1ISES U2 ID 1+P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
210120 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0502 | 1.0388 | 0.92 | 1.05 | 371 | G_1ISES U2 ID 1+P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1455_6RITCHIE-2!, 6RITCHIE-1! | G_1ISES U2 ID 1 |  | VH
210121 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0533 | 1.0377 | 0.92 | 1.05 | 372 | G_1ISES U2 ID 1+P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | G_1ISES U2 ID 1 |  | VH
210122 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0534 | 1.0378 | 0.92 | 1.05 | 372 | G_1ISES U2 ID 1+P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | G_1ISES U2 ID 1 |  | VH
210123 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0507 | 1.0388 | 0.92 | 1.05 | 372 | G_1ISES U2 ID 1+P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1456_3BRINKLEY.E!, 3CARLISLE! | G_1ISES U2 ID 1 |  | VH
210124 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0526 | 1.0377 | 0.92 | 1.05 | 373 | G_1ISES U2 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U2 ID 1 |  | VH
210125 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0527 | 1.0378 | 0.92 | 1.05 | 373 | G_1ISES U2 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U2 ID 1 |  | VH
210126 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.057 | 1.0388 | 0.92 | 1.05 | 373 | G_1ISES U2 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U2 ID 1 |  | VH
210127 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0609 | 1.0439 | 0.92 | 1.05 | 373 | G_1ISES U2 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1ISES U2 ID 1 |  | VH
210128 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0501 | 1.0378 | 0.92 | 1.05 | 374 | G_1ISES U2 ID 1+1613 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1460_3SRCY PRICE!, 3HOLND BTM! | G_1ISES U2 ID 1 |  | VH
210129 | 18L | Proposed | P3 | 40 | 2BLACK ROCK | VH |  |  |  |  | 1.0564 | 1.0664 | 0.92 | 1.05 | 374 | G_1ISES U2 ID 1+1613 | 338570 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1460_3SRCY PRICE!, 3HOLND BTM! | G_1ISES U2 ID 1 |  | VH
210130 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.053 | 1.0377 | 0.92 | 1.05 | 375 | G_1ISES U2 ID 1+P1_2-1468_5MOSES%, 5BAILEY#! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1468_5MOSES%, 5BAILEY#! | G_1ISES U2 ID 1 |  | VH
210131 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0531 | 1.0378 | 0.92 | 1.05 | 375 | G_1ISES U2 ID 1+P1_2-1468_5MOSES%, 5BAILEY#! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1468_5MOSES%, 5BAILEY#! | G_1ISES U2 ID 1 |  | VH
210132 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0573 | 1.0388 | 0.92 | 1.05 | 375 | G_1ISES U2 ID 1+P1_2-1468_5MOSES%, 5BAILEY#! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1468_5MOSES%, 5BAILEY#! | G_1ISES U2 ID 1 |  | VH
210133 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.051 | 1.0377 | 0.92 | 1.05 | 376 | G_1ISES U2 ID 1+1626 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!, 5SOUTHSIDE! | G_1ISES U2 ID 1 |  | VH
210134 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.051 | 1.0378 | 0.92 | 1.05 | 376 | G_1ISES U2 ID 1+1626 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1475_5SRCY PRICE!, 5SOUTHSIDE! | G_1ISES U2 ID 1 |  | VH
210135 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0568 | 1.0377 | 0.92 | 1.05 | 377 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%, 8ISES% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%, 8ISES% | G_1ISES U2 ID 1 |  | VH
210136 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0569 | 1.0378 | 0.92 | 1.05 | 377 | G_1ISES U2 ID 1+P1_2-1488_8HOLND BTM%, 8ISES% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1488_8HOLND BTM%, 8ISES% | G_1ISES U2 ID 1 |  | VH
210137 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0607 | 1.0378 | 0.92 | 1.05 | 378 | G_1ISES U2 ID 1+1640 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1489_5ISES-1!, 8ISES%,5ISES-2! | G_1ISES U2 ID 1 |  | VH
210138 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0538 | 1.0377 | 0.92 | 1.05 | 379 | G_1ISES U2 ID 1+P1_2-1502_5EBONY% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1502_5EBONY% | G_1ISES U2 ID 1 |  | VH
210139 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0538 | 1.0378 | 0.92 | 1.05 | 379 | G_1ISES U2 ID 1+P1_2-1502_5EBONY% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1502_5EBONY% | G_1ISES U2 ID 1 |  | VH
210140 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0509 | 1.0388 | 0.92 | 1.05 | 379 | G_1ISES U2 ID 1+P1_2-1502_5EBONY% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1502_5EBONY% | G_1ISES U2 ID 1 |  | VH
210141 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0537 | 1.0377 | 0.92 | 1.05 | 380 | G_1ISES U2 ID 1+P1_2-1504_5EBONY%, 5W.MEMPHIS! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1504_5EBONY%, 5W.MEMPHIS! | G_1ISES U2 ID 1 |  | VH
210142 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0538 | 1.0378 | 0.92 | 1.05 | 380 | G_1ISES U2 ID 1+P1_2-1504_5EBONY%, 5W.MEMPHIS! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1504_5EBONY%, 5W.MEMPHIS! | G_1ISES U2 ID 1 |  | VH
210143 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0507 | 1.0388 | 0.92 | 1.05 | 380 | G_1ISES U2 ID 1+P1_2-1504_5EBONY%, 5W.MEMPHIS! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1504_5EBONY%, 5W.MEMPHIS! | G_1ISES U2 ID 1 |  | VH
210144 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0536 | 1.0377 | 0.92 | 1.05 | 381 | G_1ISES U2 ID 1+P1_2-1509_5MARKEDTREE!, HERGETT5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1509_5MARKEDTREE!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210145 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0536 | 1.0378 | 0.92 | 1.05 | 381 | G_1ISES U2 ID 1+P1_2-1509_5MARKEDTREE!, HERGETT5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1509_5MARKEDTREE!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210146 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0509 | 1.0388 | 0.92 | 1.05 | 381 | G_1ISES U2 ID 1+P1_2-1509_5MARKEDTREE!, HERGETT5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1509_5MARKEDTREE!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210147 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0554 | 1.0439 | 0.92 | 1.05 | 381 | G_1ISES U2 ID 1+P1_2-1509_5MARKEDTREE!, HERGETT5! | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1509_5MARKEDTREE!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210148 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0532 | 1.0377 | 0.92 | 1.05 | 382 | G_1ISES U2 ID 1+P1_2-1511_5JONESBORO!, 5PARAGOULD% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1511_5JONESBORO!, 5PARAGOULD% | G_1ISES U2 ID 1 |  | VH
210149 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0533 | 1.0378 | 0.92 | 1.05 | 382 | G_1ISES U2 ID 1+P1_2-1511_5JONESBORO!, 5PARAGOULD% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1511_5JONESBORO!, 5PARAGOULD% | G_1ISES U2 ID 1 |  | VH
210150 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0517 | 1.0377 | 0.92 | 1.05 | 383 | G_1ISES U2 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210151 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0518 | 1.0378 | 0.92 | 1.05 | 383 | G_1ISES U2 ID 1+P1_2-1513_5JONESBORO!, HERGETT5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1513_5JONESBORO!, HERGETT5! | G_1ISES U2 ID 1 |  | VH
210152 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0518 | 1.0377 | 0.92 | 1.05 | 384 | G_1ISES U2 ID 1+1685 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!, 3WALNUT RDG! | G_1ISES U2 ID 1 |  | VH
210153 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0519 | 1.0378 | 0.92 | 1.05 | 384 | G_1ISES U2 ID 1+1685 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1534_3PARAGOULD!, 3WALNUT RDG! | G_1ISES U2 ID 1 |  | VH
210154 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0516 | 1.0377 | 0.92 | 1.05 | 385 | G_1ISES U2 ID 1+1686 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
210155 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0517 | 1.0378 | 0.92 | 1.05 | 385 | G_1ISES U2 ID 1+1686 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1535_3WALNUT RDG!, 5WALNUT RDG% | G_1ISES U2 ID 1 |  | VH
210156 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0512 | 1.0377 | 0.92 | 1.05 | 386 | G_1ISES U2 ID 1+P1_2-1536_5WALNUT RDG%, 5THAYER.S! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1536_5WALNUT RDG%, 5THAYER.S! | G_1ISES U2 ID 1 |  | VH
210157 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0513 | 1.0378 | 0.92 | 1.05 | 386 | G_1ISES U2 ID 1+P1_2-1536_5WALNUT RDG%, 5THAYER.S! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1536_5WALNUT RDG%, 5THAYER.S! | G_1ISES U2 ID 1 |  | VH
210158 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0543 | 1.0377 | 0.92 | 1.05 | 387 | G_1ISES U2 ID 1+P1_2-1561_8SHELBYTN! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1561_8SHELBYTN! | G_1ISES U2 ID 1 |  | VH
210159 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0544 | 1.0378 | 0.92 | 1.05 | 387 | G_1ISES U2 ID 1+P1_2-1561_8SHELBYTN! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1561_8SHELBYTN! | G_1ISES U2 ID 1 |  | VH
210160 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0541 | 1.0377 | 0.92 | 1.05 | 388 | G_1ISES U2 ID 1+P1_2-1562_8SHELBYTN! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1562_8SHELBYTN! | G_1ISES U2 ID 1 |  | VH
210161 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0541 | 1.0378 | 0.92 | 1.05 | 388 | G_1ISES U2 ID 1+P1_2-1562_8SHELBYTN! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1562_8SHELBYTN! | G_1ISES U2 ID 1 |  | VH
210162 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0527 | 1.0377 | 0.92 | 1.05 | 389 | G_1ISES U2 ID 1+P1_2-1569_8CORDOVA TN! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1569_8CORDOVA TN! | G_1ISES U2 ID 1 |  | VH
210163 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0528 | 1.0378 | 0.92 | 1.05 | 389 | G_1ISES U2 ID 1+P1_2-1569_8CORDOVA TN! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1569_8CORDOVA TN! | G_1ISES U2 ID 1 |  | VH
210164 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0533 | 1.0377 | 0.92 | 1.05 | 390 | G_1ISES U2 ID 1+P1_2-1570_8CORDOVA TN! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1570_8CORDOVA TN! | G_1ISES U2 ID 1 |  | VH
210165 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0534 | 1.0378 | 0.92 | 1.05 | 390 | G_1ISES U2 ID 1+P1_2-1570_8CORDOVA TN! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1570_8CORDOVA TN! | G_1ISES U2 ID 1 |  | VH
210166 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0521 | 1.0377 | 0.92 | 1.05 | 391 | G_1ISES U2 ID 1+P1_2-1755_PARAGLD5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1755_PARAGLD5! | G_1ISES U2 ID 1 |  | VH
210167 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0521 | 1.0378 | 0.92 | 1.05 | 391 | G_1ISES U2 ID 1+P1_2-1755_PARAGLD5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1755_PARAGLD5! | G_1ISES U2 ID 1 |  | VH
210168 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0522 | 1.0377 | 0.92 | 1.05 | 392 | G_1ISES U2 ID 1+P1_2-1757_PARAGLD5!, CENTR H5 | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1757_PARAGLD5!, CENTR H5 | G_1ISES U2 ID 1 |  | VH
210169 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0522 | 1.0378 | 0.92 | 1.05 | 392 | G_1ISES U2 ID 1+P1_2-1757_PARAGLD5!, CENTR H5 | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1757_PARAGLD5!, CENTR H5 | G_1ISES U2 ID 1 |  | VH
210170 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0525 | 1.0377 | 0.92 | 1.05 | 393 | G_1ISES U2 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U2 ID 1 |  | VH
210171 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0525 | 1.0378 | 0.92 | 1.05 | 393 | G_1ISES U2 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U2 ID 1 |  | VH
210172 | 18L | Proposed | P3 | 40 | 5JONESBORO! | VH |  |  |  |  | 1.0509 | 1.0408 | 0.92 | 1.05 | 393 | G_1ISES U2 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U2 ID 1 |  | VH
210173 | 18L | Proposed | P3 | 40 | 2JONSBORO.W | VH |  |  |  |  | 1.0509 | 1.0408 | 0.92 | 1.05 | 393 | G_1ISES U2 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U2 ID 1 |  | VH
210174 | 18L | Proposed | P3 | 40 | 5JONSBORO.W# | VH |  |  |  |  | 1.0509 | 1.0408 | 0.92 | 1.05 | 393 | G_1ISES U2 ID 1+P1_2-1759_CENTR H5, JONESBO5% | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1759_CENTR H5, JONESBO5% | G_1ISES U2 ID 1 |  | VH
210175 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0534 | 1.0377 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210176 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0535 | 1.0378 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210177 | 18L | Proposed | P3 | 40 | 5JONESBORO! | VH |  |  |  |  | 1.0511 | 1.0408 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338170 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210178 | 18L | Proposed | P3 | 40 | 2JONSBORO.W | VH |  |  |  |  | 1.0511 | 1.0408 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338566 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210179 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.05 | 1.0388 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210180 | 18L | Proposed | P3 | 40 | 5JONSBORO.W# | VH |  |  |  |  | 1.0511 | 1.0408 | 0.92 | 1.05 | 394 | G_1ISES U2 ID 1+P1_2-1761_JONESBO5%, WATER V5! | 338702 |  |  |  | 161 | 161 | 327 | EES-EAI |  |  | P1_2-1761_JONESBO5%, WATER V5! | G_1ISES U2 ID 1 |  | VH
210181 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0519 | 1.0377 | 0.92 | 1.05 | 395 | G_1ISES U2 ID 1+P1_2-1769_INDEPCO5!, GREERSF5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1769_INDEPCO5!, GREERSF5! | G_1ISES U2 ID 1 |  | VH
210182 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.052 | 1.0378 | 0.92 | 1.05 | 395 | G_1ISES U2 ID 1+P1_2-1769_INDEPCO5!, GREERSF5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1769_INDEPCO5!, GREERSF5! | G_1ISES U2 ID 1 |  | VH
210183 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0522 | 1.0377 | 0.92 | 1.05 | 396 | G_1ISES U2 ID 1+P1_2-1779_NORFORK5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1779_NORFORK5! | G_1ISES U2 ID 1 |  | VH
210184 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0523 | 1.0378 | 0.92 | 1.05 | 396 | G_1ISES U2 ID 1+P1_2-1779_NORFORK5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1779_NORFORK5! | G_1ISES U2 ID 1 |  | VH
210185 | 18L | Proposed | P3 | 40 | 8ISES-XF | VH |  |  |  |  | 1.0525 | 1.0377 | 0.92 | 1.05 | 397 | G_1ISES U2 ID 1+P1_2-1783_NORFORK5!, BULL SH5! | 338144 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1783_NORFORK5!, BULL SH5! | G_1ISES U2 ID 1 |  | VH
210186 | 18L | Proposed | P3 | 40 | 8ISES% | VH |  |  |  |  | 1.0526 | 1.0378 | 0.92 | 1.05 | 397 | G_1ISES U2 ID 1+P1_2-1783_NORFORK5!, BULL SH5! | 338145 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1783_NORFORK5!, BULL SH5! | G_1ISES U2 ID 1 |  | VH
210187 | 18L | Proposed | P3 | 40 | 8HAYWOOD TN | VH |  |  |  |  | 1.0747 | 1.0613 | 0.92 | 1.05 | 400 | G_1PLUM PT U1 ID 1+1722 | 360542 |  |  |  | 500 | 500 | 347 | TVA |  |  | P1_2-1571_8CORDOVA TN!, 8HAYWOOD TN | G_1PLUM PT U1 ID 1 |  | VH
210188 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0598 | 1.0256 | 0.92 | 1.05 | 402 | G_1MCCLELAN U1 ID 1+1387 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1232_3STERL2%, 3ELDORADO.E! | G_1MCCLELAN U1 ID 1 |  | VH
210189 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0608 | 1.0256 | 0.92 | 1.05 | 403 | G_1MCCLELAN U1 ID 1+1396 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1241_8STERLING%, 8EL DORADO% | G_1MCCLELAN U1 ID 1 |  | VH
210190 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0584 | 1.0256 | 0.92 | 1.05 | 404 | G_1MCCLELAN U1 ID 1+P1_2-1270_3MCNEIL!, 3WYATT! | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1270_3MCNEIL!, 3WYATT! | G_1MCCLELAN U1 ID 1 |  | VH
210191 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0581 | 1.0256 | 0.92 | 1.05 | 405 | G_1MCCLELAN U1 ID 1+1427 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1272_3CAMDEN MAG!, 3EL DORADO! | G_1MCCLELAN U1 ID 1 |  | VH
210192 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0588 | 1.0256 | 0.92 | 1.05 | 406 | G_1MCCLELAN U1 ID 1+P1_2-1276_3EL DORADO!, 3WYATT! | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1276_3EL DORADO!, 3WYATT! | G_1MCCLELAN U1 ID 1 |  | VH
210193 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0591 | 1.0256 | 0.92 | 1.05 | 407 | G_1MCCLELAN U1 ID 1+1435 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1280_3WYATT!, 3JNCTN CITY! | G_1MCCLELAN U1 ID 1 |  | VH
210194 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0603 | 1.0256 | 0.92 | 1.05 | 408 | G_1MCCLELAN U1 ID 1+1436 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1281_3WYATT!, 3ELDORADO.E! | G_1MCCLELAN U1 ID 1 |  | VH
210195 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0606 | 1.0256 | 0.92 | 1.05 | 409 | G_1MCCLELAN U1 ID 1+1462 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1308_3PB IP SS%, 3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
210196 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0606 | 1.0256 | 0.92 | 1.05 | 410 | G_1MCCLELAN U1 ID 1+P1_2-1309_3PB IP!, 3PB ENERGY! | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1309_3PB IP!, 3PB ENERGY! | G_1MCCLELAN U1 ID 1 |  | VH
210197 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.063 | 1.0256 | 0.92 | 1.05 | 411 | G_1MCCLELAN U1 ID 1+P1_2-1319_8WHT BLUFF% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1319_8WHT BLUFF% | G_1MCCLELAN U1 ID 1 |  | VH
210198 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0627 | 1.0256 | 0.92 | 1.05 | 412 | G_1MCCLELAN U1 ID 1+P1_2-1320_8WHT BLUFF% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1320_8WHT BLUFF% | G_1MCCLELAN U1 ID 1 |  | VH
210199 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0588 | 1.0256 | 0.92 | 1.05 | 413 | G_1MCCLELAN U1 ID 1+P1_2-1396_8WRIGHTSVLE% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1396_8WRIGHTSVLE% | G_1MCCLELAN U1 ID 1 |  | VH
210200 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0586 | 1.0256 | 0.92 | 1.05 | 414 | G_1MCCLELAN U1 ID 1+P1_2-1397_8WRIGHTSVLE% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1397_8WRIGHTSVLE% | G_1MCCLELAN U1 ID 1 |  | VH
210201 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0586 | 1.0256 | 0.92 | 1.05 | 415 | G_1MCCLELAN U1 ID 1+P1_2-1398_8WRIGHTSVLE% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1398_8WRIGHTSVLE% | G_1MCCLELAN U1 ID 1 |  | VH
210202 | 18L | Proposed | P3 | 40 | 2MCCLELLAN | VH |  |  |  |  | 1.0582 | 1.0256 | 0.92 | 1.05 | 416 | G_1MCCLELAN U1 ID 1+P1_2-1846_HOPE 3!, TURK 4% | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1846_HOPE 3!, TURK 4% | G_1MCCLELAN U1 ID 1 |  | VH
210203 | 18L | Proposed | P3 | 40 | 2BAILEY | VH |  |  |  |  | 1.0506 | 1.0388 | 0.92 | 1.05 | 417 | G_1WRIGHTS C7 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338628 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WRIGHTS C7 ID 1 |  | VH
210204 | 18L | Proposed | P3 | 40 | 2WYNNE.E | VH |  |  |  |  | 1.0563 | 1.0439 | 0.92 | 1.05 | 417 | G_1WRIGHTS C7 ID 1+P1_2-1458_3BRINKLEY.E!, 5MOSES% | 338632 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1458_3BRINKLEY.E!, 5MOSES% | G_1WRIGHTS C7 ID 1 |  | VH
210205 | 18L | Proposed | P3 | 40 | VALIANT7 | VH |  |  |  |  | 1.0514 | 1.0385 | 0.92 | 1.05 | 442 | G_TURKCOAL ID 1+P1_2-1853_LYDIA 7, WELSH 7! | 510911 |  |  |  | 345 | 345 | 520 | AEPW |  |  | P1_2-1853_LYDIA 7, WELSH 7! | G_TURKCOAL ID 1 |  | VH
210206 | 18W | Proposed | P0 | 41 | 5HORN LAKE% | VH |  |  |  |  | 1.0586 | 1.0586 | 0.92 | 1.05 |  | ** Base Case ** | 337181 |  |  |  | 161 | 161 | 326 | EES-EMI |  |  | ** Base Case ** |  |  | VH
210207 | 18W | Proposed | P0 | 41 | 8E POINT AL | VH |  |  |  |  | 1.0517 | 1.0517 | 0.92 | 1.05 |  | ** Base Case ** | 360058 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
210208 | 18W | Proposed | P0 | 41 | 8WID CRK FP | VH |  |  |  |  | 1.0501 | 1.0501 | 0.92 | 1.05 |  | ** Base Case ** | 360065 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
210209 | 18W | Proposed | P0 | 41 | 8PLEASANT HL | VH |  |  |  |  | 1.0505 | 1.0505 | 0.92 | 1.05 |  | ** Base Case ** | 360541 |  |  |  | 500 | 500 | 347 | TVA |  |  | ** Base Case ** |  |  | VH
210210 | 18W | Proposed | P3 | 41 | 2HIMEX | VH |  |  |  |  | 1.0559 | 1.0262 | 0.92 | 1.05 | 1 | P1_2-221_4STOWELL!,2STOWELL!+G_1G3SABIN! ID 1 | 334236 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-221_4STOWELL!,2STOWELL! | G_1G3SABIN! ID 1 |  | VH
210217 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8995 | 0.9347 | 0.92 | 1.05 | 2 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210224 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8995 | 0.9347 | 0.92 | 1.05 | 3 | P1_2-237_4RAYBURN%,4MILLCR!+G_1FRNTR 2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210231 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8991 | 0.9347 | 0.92 | 1.05 | 4 | P1_2-237_4RAYBURN%,4MILLCR!+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210232 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9164 | 0.9534 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210233 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9145 | 0.9516 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210234 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9142 | 0.9513 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210235 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9141 | 0.9513 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210236 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.914 | 0.9511 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210237 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.914 | 0.9511 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210238 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9347 | 0.92 | 1.05 | 5 | P1_2-237_4RAYBURN%,4MILLCR!+G_1EXXONGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1EXXONGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210245 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8993 | 0.9347 | 0.92 | 1.05 | 6 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210252 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8992 | 0.9347 | 0.92 | 1.05 | 7 | P1_2-237_4RAYBURN%,4MILLCR!+G_1ANO U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1ANO U2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210259 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8987 | 0.9347 | 0.92 | 1.05 | 8 | P1_2-237_4RAYBURN%,4MILLCR!+G_1CAL G1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_1CAL G1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210266 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8993 | 0.9347 | 0.92 | 1.05 | 9 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1WKRAFT! ID 3 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1WKRAFT! ID 3 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210267 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9103 | 0.9534 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210268 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9084 | 0.9516 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210269 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9081 | 0.9513 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210270 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9081 | 0.9513 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210271 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9079 | 0.9511 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210272 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9079 | 0.9511 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210273 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8907 | 0.9347 | 0.92 | 1.05 | 10 | P1_2-237_4RAYBURN%,4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210280 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8985 | 0.9347 | 0.92 | 1.05 | 11 | P1_2-237_4RAYBURN%,4MILLCR!+G_FULTONU1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210287 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8995 | 0.9347 | 0.92 | 1.05 | 12 | P1_2-237_4RAYBURN%,4MILLCR!+G_BVR #1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_BVR #1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210294 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8984 | 0.9347 | 0.92 | 1.05 | 13 | P1_2-237_4RAYBURN%,4MILLCR!+G_FLINTCR1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210295 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9107 | 0.9534 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210296 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9088 | 0.9516 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210297 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9085 | 0.9513 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210298 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9084 | 0.9513 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210299 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9083 | 0.9511 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210300 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9083 | 0.9511 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210301 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.891 | 0.9347 | 0.92 | 1.05 | 14 | P1_2-237_4RAYBURN%,4MILLCR!+G_PIRKEY 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210302 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.914 | 0.9534 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210303 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9121 | 0.9516 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210304 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9118 | 0.9513 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210305 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9118 | 0.9513 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210306 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9116 | 0.9511 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210307 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9116 | 0.9511 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210308 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8945 | 0.9347 | 0.92 | 1.05 | 15 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH2-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210309 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.914 | 0.9534 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210310 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9121 | 0.9516 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210311 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9118 | 0.9513 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210312 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9118 | 0.9513 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210313 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9116 | 0.9511 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210314 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9116 | 0.9511 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210315 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8945 | 0.9347 | 0.92 | 1.05 | 16 | P1_2-237_4RAYBURN%,4MILLCR!+G_WELSH3-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210316 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.915 | 0.9534 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210317 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9131 | 0.9516 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210318 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9129 | 0.9513 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210319 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9128 | 0.9513 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210320 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9126 | 0.9511 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210321 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9127 | 0.9511 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210322 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8955 | 0.9347 | 0.92 | 1.05 | 17 | P1_2-237_4RAYBURN%,4MILLCR!+G_TURKCOAL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210329 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.898 | 0.9347 | 0.92 | 1.05 | 18 | P1_2-237_4RAYBURN%,4MILLCR!+G_MUSKOG4G ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210336 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8992 | 0.9347 | 0.92 | 1.05 | 19 | P1_2-237_4RAYBURN%,4MILLCR!+G_JTEC GEN#2 1 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-237_4RAYBURN%,4MILLCR! | G_JTEC GEN#2 1 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210343 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 20 | P1_2-239_4MILLCR!+G_1NM G1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1NM G1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210350 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8947 | 0.9347 | 0.92 | 1.05 | 21 | P1_2-239_4MILLCR!+G_1STFRG1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1STFRG1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210357 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8971 | 0.9347 | 0.92 | 1.05 | 22 | P1_2-239_4MILLCR!+G_1BCAJUN2_U1% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1BCAJUN2_U1% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210364 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.897 | 0.9347 | 0.92 | 1.05 | 23 | P1_2-239_4MILLCR!+G_1BCAJUN2_U2% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1BCAJUN2_U2% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210371 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9347 | 0.92 | 1.05 | 24 | P1_2-239_4MILLCR!+G_1BCAJUN2_U3% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1BCAJUN2_U3% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210378 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8941 | 0.9347 | 0.92 | 1.05 | 25 | P1_2-239_4MILLCR!+G_1FRNTR 1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1FRNTR 1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210385 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8941 | 0.9347 | 0.92 | 1.05 | 26 | P1_2-239_4MILLCR!+G_1FRNTR 2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1FRNTR 2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210392 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8958 | 0.9347 | 0.92 | 1.05 | 27 | P1_2-239_4MILLCR!+G_1G1LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1G1LEWIS! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210399 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8958 | 0.9347 | 0.92 | 1.05 | 28 | P1_2-239_4MILLCR!+G_1G2LEWIS! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1G2LEWIS! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210406 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8967 | 0.9347 | 0.92 | 1.05 | 29 | P1_2-239_4MILLCR!+G_1RS_CGN_R5! ID 5 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1RS_CGN_R5! ID 5 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210413 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8967 | 0.9347 | 0.92 | 1.05 | 30 | P1_2-239_4MILLCR!+G_1ACADIA_C25! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ACADIA_C25! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210420 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8967 | 0.9347 | 0.92 | 1.05 | 31 | P1_2-239_4MILLCR!+G_1ACADIA_C24! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ACADIA_C24! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210427 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9347 | 0.92 | 1.05 | 39 | P1_2-239_4MILLCR!+G_1WAT U1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WAT U1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210434 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9347 | 0.92 | 1.05 | 40 | P1_2-239_4MILLCR!+G_1WAT U2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WAT U2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210441 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8968 | 0.9347 | 0.92 | 1.05 | 41 | P1_2-239_4MILLCR!+G_1SOXY U1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1SOXY U1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210448 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8954 | 0.9347 | 0.92 | 1.05 | 42 | P1_2-239_4MILLCR!+G_1UCARBGT1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1UCARBGT1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210455 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8954 | 0.9347 | 0.92 | 1.05 | 43 | P1_2-239_4MILLCR!+G_1UCARBGT2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1UCARBGT2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210462 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8971 | 0.9347 | 0.92 | 1.05 | 44 | P1_2-239_4MILLCR!+G_1GYP U2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1GYP U2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210469 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.896 | 0.9347 | 0.92 | 1.05 | 45 | P1_2-239_4MILLCR!+G_1NMIL6 CT1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1NMIL6 CT1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210476 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.896 | 0.9347 | 0.92 | 1.05 | 46 | P1_2-239_4MILLCR!+G_1NMIL6 CT2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1NMIL6 CT2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210483 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8962 | 0.9347 | 0.92 | 1.05 | 47 | P1_2-239_4MILLCR!+G_1NMIL6 ST1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1NMIL6 ST1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210490 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8954 | 0.9347 | 0.92 | 1.05 | 48 | P1_2-239_4MILLCR!+G_1HINDS G1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1HINDS G1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210497 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.895 | 0.9347 | 0.92 | 1.05 | 49 | P1_2-239_4MILLCR!+G_1SLSBAU3 ID 5 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1SLSBAU3 ID 5 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210504 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.895 | 0.9347 | 0.92 | 1.05 | 50 | P1_2-239_4MILLCR!+G_1CLSBAU3 ID 6 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CLSBAU3 ID 6 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210511 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 51 | P1_2-239_4MILLCR!+G_1WHT BLUF U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WHT BLUF U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210518 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 52 | P1_2-239_4MILLCR!+G_1WHT BLUF U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WHT BLUF U2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210525 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 53 | P1_2-239_4MILLCR!+G_1REMMEL UA ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1REMMEL UA ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210532 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8942 | 0.9347 | 0.92 | 1.05 | 54 | P1_2-239_4MILLCR!+G_1ANO U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ANO U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210539 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.894 | 0.9347 | 0.92 | 1.05 | 55 | P1_2-239_4MILLCR!+G_1ANO U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ANO U2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210546 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 56 | P1_2-239_4MILLCR!+G_1ISES U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ISES U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210553 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 57 | P1_2-239_4MILLCR!+G_1ISES U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1ISES U2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210560 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8951 | 0.9347 | 0.92 | 1.05 | 58 | P1_2-239_4MILLCR!+G_1PLUM PT U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1PLUM PT U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210567 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 59 | P1_2-239_4MILLCR!+G_1LSPWRU1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1LSPWRU1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210574 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.895 | 0.9347 | 0.92 | 1.05 | 60 | P1_2-239_4MILLCR!+G_1MCCLELAN U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1MCCLELAN U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210575 | 18W | Proposed | P3 | 41 | 2MCCLELLAN | VH |  |  |  |  | 1.0538 | 1.0256 | 0.92 | 1.05 | 60 | P1_2-239_4MILLCR!+G_1MCCLELAN U1 ID 1 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-239_4MILLCR! | G_1MCCLELAN U1 ID 1 |  | VH
210582 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 61 | P1_2-239_4MILLCR!+G_1WRIGHTS C1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210589 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 62 | P1_2-239_4MILLCR!+G_1WRIGHTS C1 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C1 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210596 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 63 | P1_2-239_4MILLCR!+G_1WRIGHTS C3 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C3 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210603 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 64 | P1_2-239_4MILLCR!+G_1WRIGHTS C3 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C3 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210610 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 65 | P1_2-239_4MILLCR!+G_1WRIGHTS C5 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C5 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210617 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 66 | P1_2-239_4MILLCR!+G_1WRIGHTS C5 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C5 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210624 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 67 | P1_2-239_4MILLCR!+G_1WRIGHTS S1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS S1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210631 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 68 | P1_2-239_4MILLCR!+G_1WRIGHTS C7 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS C7 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210638 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 69 | P1_2-239_4MILLCR!+G_1WRIGHTS S2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1WRIGHTS S2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210645 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8934 | 0.9347 | 0.92 | 1.05 | 70 | P1_2-239_4MILLCR!+G_1CAL G1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CAL G1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210652 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8952 | 0.9347 | 0.92 | 1.05 | 71 | P1_2-239_4MILLCR!+G_1CUMBRL F1HL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CUMBRL F1HL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210659 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8952 | 0.9347 | 0.92 | 1.05 | 72 | P1_2-239_4MILLCR!+G_1CUMBRL F1HL ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CUMBRL F1HL ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210666 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8952 | 0.9347 | 0.92 | 1.05 | 73 | P1_2-239_4MILLCR!+G_1CUMBRL F2HL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CUMBRL F2HL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210673 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8952 | 0.9347 | 0.92 | 1.05 | 74 | P1_2-239_4MILLCR!+G_1CUMBRL F2HL ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_1CUMBRL F2HL ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210674 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.905 | 0.9534 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210675 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9031 | 0.9516 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210676 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9028 | 0.9513 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210677 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9028 | 0.9513 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210678 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9026 | 0.9511 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210679 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9026 | 0.9511 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210680 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8854 | 0.9347 | 0.92 | 1.05 | 75 | P1_2-239_4MILLCR!+G_G1DOLHIL! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1DOLHIL! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210687 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8969 | 0.9347 | 0.92 | 1.05 | 76 | P1_2-239_4MILLCR!+G_G1 ACAD! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G1 ACAD! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210694 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.897 | 0.9347 | 0.92 | 1.05 | 77 | P1_2-239_4MILLCR!+G_G7-1COUGH! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_G7-1COUGH! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210701 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8935 | 0.9347 | 0.92 | 1.05 | 78 | P1_2-239_4MILLCR!+G_FULTONU1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_FULTONU1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210708 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8947 | 0.9347 | 0.92 | 1.05 | 79 | P1_2-239_4MILLCR!+G_JBOGENC1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_JBOGENC1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210715 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 80 | P1_2-239_4MILLCR!+G_GF #1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_GF #1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210722 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 81 | P1_2-239_4MILLCR!+G_GF #2 2 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_GF #2 2 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210729 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8949 | 0.9347 | 0.92 | 1.05 | 82 | P1_2-239_4MILLCR!+G_NFK #1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_NFK #1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210736 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8946 | 0.9347 | 0.92 | 1.05 | 83 | P1_2-239_4MILLCR!+G_BVR #1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_BVR #1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210743 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8934 | 0.9347 | 0.92 | 1.05 | 84 | P1_2-239_4MILLCR!+G_FLINTCR1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_FLINTCR1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210744 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9041 | 0.9534 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210745 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9022 | 0.9516 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210746 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9019 | 0.9513 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210747 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9018 | 0.9513 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210748 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9016 | 0.9511 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210749 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9017 | 0.9511 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210750 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8843 | 0.9347 | 0.92 | 1.05 | 85 | P1_2-239_4MILLCR!+G_PIRKEY 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210751 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9083 | 0.9534 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210752 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9064 | 0.9516 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210753 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9062 | 0.9513 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210754 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9061 | 0.9513 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210755 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9059 | 0.9511 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210756 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.906 | 0.9511 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210757 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8888 | 0.9347 | 0.92 | 1.05 | 86 | P1_2-239_4MILLCR!+G_WELSH2-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210758 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9083 | 0.9534 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210759 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9064 | 0.9516 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210760 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9062 | 0.9513 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210761 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9061 | 0.9513 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210762 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9059 | 0.9511 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210763 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.906 | 0.9511 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210764 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8887 | 0.9347 | 0.92 | 1.05 | 87 | P1_2-239_4MILLCR!+G_WELSH3-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210765 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9094 | 0.9534 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210766 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9075 | 0.9516 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210767 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9072 | 0.9513 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210768 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9072 | 0.9513 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210769 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.907 | 0.9511 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210770 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.907 | 0.9511 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210771 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8898 | 0.9347 | 0.92 | 1.05 | 88 | P1_2-239_4MILLCR!+G_TURKCOAL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210772 | 18W | Proposed | P3 | 41 | 2PINELND | VL |  |  |  |  | 0.9123 | 0.9534 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334288 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210773 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9104 | 0.9516 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210774 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9101 | 0.9513 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210775 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9101 | 0.9513 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210776 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9099 | 0.9511 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210777 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.9099 | 0.9511 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210778 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8927 | 0.9347 | 0.92 | 1.05 | 89 | P1_2-239_4MILLCR!+G_MUSKOG4G ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210785 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.8941 | 0.9347 | 0.92 | 1.05 | 90 | P1_2-239_4MILLCR!+G_JTEC GEN#2 1 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-239_4MILLCR! | G_JTEC GEN#2 1 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210786 | 18W | Proposed | P3 | 41 | 2TEMPL1* | VL |  |  |  |  | 0.9194 | 0.9516 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334289 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210787 | 18W | Proposed | P3 | 41 | 2TEMPLE1 | VL |  |  |  |  | 0.9192 | 0.9513 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334290 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210788 | 18W | Proposed | P3 | 41 | 2TEMPL2* | VL |  |  |  |  | 0.9191 | 0.9513 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334291 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210789 | 18W | Proposed | P3 | 41 | 2TEMPLE2 | VL |  |  |  |  | 0.9189 | 0.9511 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334292 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210790 | 18W | Proposed | P3 | 41 | 2TMPLSWC | VL |  |  |  |  | 0.919 | 0.9511 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334293 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210791 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9019 | 0.9347 | 0.92 | 1.05 | 93 | P1_2-247_4BUNA!,4EVADALE!+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-247_4BUNA!,4EVADALE! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210792 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9185 | 0.9568 | 0.92 | 1.05 | 105 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1RVR_BND_G1! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1
210793 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9062 | 0.9508 | 0.92 | 1.05 | 105 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1RVR_BND_G1! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1RVR_BND_G1! ID 1 | turn on switch shunt at winnsbord 115kV sub
210794 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9081 | 0.9508 | 0.92 | 1.05 | 106 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1WAT U1! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U1! ID 1 | turn on switch shunt at winnsbord 115kV sub
210795 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9081 | 0.9508 | 0.92 | 1.05 | 107 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1WAT U2! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U2! ID 1 | turn on switch shunt at winnsbord 115kV sub
210796 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9169 | 0.9568 | 0.92 | 1.05 | 108 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1WAT U3! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1
210797 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9045 | 0.9508 | 0.92 | 1.05 | 108 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1WAT U3! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1WAT U3! ID 1 | turn on switch shunt at winnsbord 115kV sub
210798 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9081 | 0.9508 | 0.92 | 1.05 | 109 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1SOXY U1! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1SOXY U1! ID 1 | turn on switch shunt at winnsbord 115kV sub
210799 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9195 | 0.9568 | 0.92 | 1.05 | 110 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1GYP U3! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GYP U3! ID 1
210800 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9072 | 0.9508 | 0.92 | 1.05 | 110 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1GYP U3! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GYP U3! ID 1 | turn on switch shunt at winnsbord 115kV sub
210801 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9079 | 0.9508 | 0.92 | 1.05 | 111 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1GYP U2! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GYP U2! ID 1 | turn on switch shunt at winnsbord 115kV sub
210802 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9083 | 0.9508 | 0.92 | 1.05 | 112 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1NMIL6 ST1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL6 ST1 ID 1 | turn on switch shunt at winnsbord 115kV sub
210803 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.919 | 0.9568 | 0.92 | 1.05 | 113 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1NMIL U4! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1
210804 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9067 | 0.9508 | 0.92 | 1.05 | 113 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1NMIL U4! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U4! ID 1 | turn on switch shunt at winnsbord 115kV sub
210805 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9189 | 0.9568 | 0.92 | 1.05 | 114 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1NMIL U5! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U5! ID 1
210806 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9066 | 0.9508 | 0.92 | 1.05 | 114 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1NMIL U5! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1NMIL U5! ID 1 | turn on switch shunt at winnsbord 115kV sub
210807 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9194 | 0.9568 | 0.92 | 1.05 | 115 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1MICH U3! ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1
210808 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.907 | 0.9508 | 0.92 | 1.05 | 115 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1MICH U3! ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1MICH U3! ID 1 | turn on switch shunt at winnsbord 115kV sub
210809 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9189 | 0.9568 | 0.92 | 1.05 | 116 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1GGNS U1 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1
210810 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9065 | 0.9508 | 0.92 | 1.05 | 116 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1GGNS U1 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1GGNS U1 ID 1 | turn on switch shunt at winnsbord 115kV sub
210811 | 18W | Proposed | P3 | 41 | 3GILBERT | VL |  |  |  |  | 0.9197 | 0.9568 | 0.92 | 1.05 | 117 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1B.WLSN U2 ID 1 | 303322 |  |  |  | 115 | 115 | 332 | LAGN |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1B.WLSN U2 ID 1
210812 | 18W | Proposed | P3 | 41 | 3WINNSBORO! | VL |  |  |  |  | 0.9074 | 0.9508 | 0.92 | 1.05 | 117 | P1_2-1181_3WINNSBORO!,3SWARTZ!+G_1B.WLSN U2 ID 1 | 337330 |  |  |  | 115 | 115 | 351 | EES |  |  | P1_2-1181_3WINNSBORO!,3SWARTZ! | G_1B.WLSN U2 ID 1 | turn on switch shunt at winnsbord 115kV sub
210883 | 18W | Proposed | P3 | 41 | 3HS.W | VL |  |  |  |  | 0.9143 | 0.9988 | 0.92 | 1.05 | 178 | P1_2-1344_3BLAKELY!,3CARPENTER!+127 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
210884 | 18W | Proposed | P3 | 41 | 3HS.S | VL |  |  |  |  | 0.9102 | 1 | 0.92 | 1.05 | 178 | P1_2-1344_3BLAKELY!,3CARPENTER!+127 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344_3BLAKELY!,3CARPENTER! | G_1CARPENTR U1 ID 1 |  | Contingency: invalid after Albright
210885 | 18W | Proposed | P3 | 41 | 3HS.W | VL |  |  |  |  | 0.9141 | 0.9988 | 0.92 | 1.05 | 179 | P1_2-1344_3BLAKELY!,3CARPENTER!+128 | 337716 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
210886 | 18W | Proposed | P3 | 41 | 3HS.S | VL |  |  |  |  | 0.91 | 1 | 0.92 | 1.05 | 179 | P1_2-1344_3BLAKELY!,3CARPENTER!+128 | 337717 |  |  |  | 115 | 115 | 327 | EES-EAI |  |  | P1_2-1344_3BLAKELY!,3CARPENTER! | G_1CARPENTR U2 ID 1 |  | Contingency: invalid after Albright
210893 | 18W | Proposed | P3 | 41 | 2MCCLELLAN | VH |  |  |  |  | 1.0538 | 1.0256 | 0.92 | 1.05 | 182 | P1_2-1344_3BLAKELY!,3CARPENTER!+139 | 338614 |  |  |  | 69 | 69 | 327 | EES-EAI |  |  | P1_2-1344_3BLAKELY!,3CARPENTER! | G_1MCCLELAN U1 ID 1 |  | VH
210964 | 18W | Proposed | P3 | 41 | 8SANS SOUCI% | VH |  |  |  |  | 1.0567 | 1.0457 | 0.92 | 1.05 | 219 | P1_2-1524_8SANS SOUCI%,8SHELBYTN!+G_1ISES U2 ID 1 | 338188 |  |  |  | 500 | 500 | 327 | EES-EAI |  |  | P1_2-1524_8SANS SOUCI%,8SHELBYTN! | G_1ISES U2 ID 1 |  | VH
210965 | 18W | Proposed | P3 | 41 | 8DANIEL | VH |  |  |  |  | 1.0768 | 1.0419 | 0.92 | 1.05 | 220 | P1_2-1607_8DANIEL%,6DANIEL!+G_1GGNS U1 ID 1 | 388700 |  |  |  | 500 | 500 | 346 | SOCO |  |  | P1_2-1607_8DANIEL%,6DANIEL! | G_1GGNS U1 ID 1 |  | VH
210966 | 18W | Proposed | P3 | 41 | 4CANEY | VL |  |  |  |  | 0.8829 | 0.9983 | 0.92 | 1.05 | 221 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
210967 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9171 | 0.9347 | 0.92 | 1.05 | 221 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210968 | 18W | Proposed | P3 | 41 | OAKDALE4 | VL |  |  |  |  | 0.8848 | 0.997 | 0.92 | 1.05 | 221 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
210969 | 18W | Proposed | P3 | 41 | PNPRARIE 4 | VL |  |  |  |  | 0.8758 | 1.0083 | 0.92 | 1.05 | 221 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
210970 | 18W | Proposed | P3 | 41 | WSTBAY 4 | VL |  |  |  |  | 0.8946 | 0.9957 | 0.92 | 1.05 | 221 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_4RAYBURN% ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_4RAYBURN% ID 1
210975 | 18W | Proposed | P3 | 41 | 4CANEY | VL |  |  |  |  | 0.8825 | 0.9983 | 0.92 | 1.05 | 223 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
210976 | 18W | Proposed | P3 | 41 | OAKDALE4 | VL |  |  |  |  | 0.8844 | 0.997 | 0.92 | 1.05 | 223 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
210977 | 18W | Proposed | P3 | 41 | PNPRARIE 4 | VL |  |  |  |  | 0.8754 | 1.0083 | 0.92 | 1.05 | 223 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
210978 | 18W | Proposed | P3 | 41 | WSTBAY 4 | VL |  |  |  |  | 0.8942 | 0.9957 | 0.92 | 1.05 | 223 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_G1DOLHIL! ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_G1DOLHIL! ID 1
210979 | 18W | Proposed | P3 | 41 | 4CANEY | VL |  |  |  |  | 0.8833 | 0.9983 | 0.92 | 1.05 | 224 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_PIRKEY 1 ID 1 | 303137 |  |  |  | 138 | 138 | 332 | LAGN |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_PIRKEY 1 ID 1
210980 | 18W | Proposed | P3 | 41 | OAKDALE4 | VL |  |  |  |  | 0.8852 | 0.997 | 0.92 | 1.05 | 224 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_PIRKEY 1 ID 1 | 500650 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_PIRKEY 1 ID 1
210981 | 18W | Proposed | P3 | 41 | PNPRARIE 4 | VL |  |  |  |  | 0.8762 | 1.0083 | 0.92 | 1.05 | 224 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_PIRKEY 1 ID 1 | 500675 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_PIRKEY 1 ID 1
210982 | 18W | Proposed | P3 | 41 | WSTBAY 4 | VL |  |  |  |  | 0.895 | 0.9957 | 0.92 | 1.05 | 224 | P1_2-1656_COUGH 4!,PNPRARIE 4%+G_PIRKEY 1 ID 1 | 500900 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1656_COUGH 4!,PNPRARIE 4% | G_PIRKEY 1 ID 1
210991 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9166 | 0.9347 | 0.92 | 1.05 | 227 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 1! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 1! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210992 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9166 | 0.9347 | 0.92 | 1.05 | 228 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1FRNTR 2! ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1FRNTR 2! ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210993 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.908 | 0.9347 | 0.92 | 1.05 | 229 | P1_2-1664_DOLHILL7%,SW SHV 7+G_4RAYBURN% ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210994 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9165 | 0.9347 | 0.92 | 1.05 | 230 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210995 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9165 | 0.9347 | 0.92 | 1.05 | 231 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1ANO U2 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1ANO U2 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210996 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9162 | 0.9347 | 0.92 | 1.05 | 232 | P1_2-1664_DOLHILL7%,SW SHV 7+G_1CAL G1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_1CAL G1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210997 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9161 | 0.9347 | 0.92 | 1.05 | 233 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FULTONU1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FULTONU1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210998 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9165 | 0.9347 | 0.92 | 1.05 | 234 | P1_2-1664_DOLHILL7%,SW SHV 7+G_BVR #1 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_BVR #1 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
210999 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.916 | 0.9347 | 0.92 | 1.05 | 235 | P1_2-1664_DOLHILL7%,SW SHV 7+G_FLINTCR1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_FLINTCR1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211000 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9124 | 0.9347 | 0.92 | 1.05 | 236 | P1_2-1664_DOLHILL7%,SW SHV 7+G_PIRKEY 1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_PIRKEY 1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211001 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.914 | 0.9347 | 0.92 | 1.05 | 237 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH2-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH2-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211002 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.914 | 0.9347 | 0.92 | 1.05 | 238 | P1_2-1664_DOLHILL7%,SW SHV 7+G_WELSH3-1 ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_WELSH3-1 ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211003 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9146 | 0.9347 | 0.92 | 1.05 | 239 | P1_2-1664_DOLHILL7%,SW SHV 7+G_TURKCOAL ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_TURKCOAL ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211004 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9158 | 0.9347 | 0.92 | 1.05 | 240 | P1_2-1664_DOLHILL7%,SW SHV 7+G_MUSKOG4G ID 1 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_MUSKOG4G ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211005 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9165 | 0.9347 | 0.92 | 1.05 | 241 | P1_2-1664_DOLHILL7%,SW SHV 7+G_JTEC GEN#2 1 ID 2 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1664_DOLHILL7%,SW SHV 7 | G_JTEC GEN#2 1 ID 2 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211006 | 18W | Proposed | P3 | 41 | ELKS 6 | VL |  |  |  |  | 0.8964 | 0.9975 | 0.92 | 1.05 | 242 | 502417 ELKS 6 230 502425 BEADLE 6 230 1+169 | 502417 |  |  |  | 230 | 230 | 503 | LAFA |  |  | 502417 ELKS 6 230 502425 BEADLE 6 230 1 | G_G3TECHE! ID 1 |  | Facility: Radial
211007 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9183 | 0.9347 | 0.92 | 1.05 | 243 | G_4RAYBURN% ID 1+P1_2-235_4DOUCETT!,4RAYBURN% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-235_4DOUCETT!,4RAYBURN% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211008 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9142 | 0.9347 | 0.92 | 1.05 | 244 | G_4RAYBURN% ID 1+P1_2-238_4RAYBURN%,4NEWTONB! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-238_4RAYBURN%,4NEWTONB! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211009 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9136 | 0.9347 | 0.92 | 1.05 | 245 | G_4RAYBURN% ID 1+P1_2-246_4CALL!,4BUNA! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-246_4CALL!,4BUNA! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211010 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9188 | 0.9347 | 0.92 | 1.05 | 247 | G_4RAYBURN% ID 1+P1_2-255_4KOUNTZE%,4CYPRESS% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-255_4KOUNTZE%,4CYPRESS% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211011 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9116 | 0.9347 | 0.92 | 1.05 | 248 | G_4RAYBURN% ID 1+P1_2-268_4NEWTONB!,4TOLEDO% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-268_4NEWTONB!,4TOLEDO% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211012 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9189 | 0.9347 | 0.92 | 1.05 | 249 | G_4RAYBURN% ID 1+P1_2-1174_6MONTGOMERY!,CLARN 6! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1174_6MONTGOMERY!,CLARN 6! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211013 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.916 | 0.9347 | 0.92 | 1.05 | 250 | G_4RAYBURN% ID 1+P1_2-1175_6MONTGOMERY!,COLFAX 6! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1175_6MONTGOMERY!,COLFAX 6! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211014 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9188 | 0.9347 | 0.92 | 1.05 | 251 | G_4RAYBURN% ID 1+P1_2-1207_7SAREPTA%,8EL DORADO% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1207_7SAREPTA%,8EL DORADO% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211015 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9177 | 0.9347 | 0.92 | 1.05 | 252 | G_4RAYBURN% ID 1+P1_2-1208_7SAREPTA%,LONGWD 7 | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1208_7SAREPTA%,LONGWD 7 | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211016 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9157 | 0.9347 | 0.92 | 1.05 | 253 | G_4RAYBURN% ID 1+P1_2-1649_COLFAX 6!,RODEMR 6% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1649_COLFAX 6!,RODEMR 6% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211017 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.916 | 0.9347 | 0.92 | 1.05 | 254 | G_4RAYBURN% ID 1+P1_2-1663_DOLHILL7%,G1DOLHIL! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1663_DOLHILL7%,G1DOLHIL! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211018 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9187 | 0.9347 | 0.92 | 1.05 | 255 | G_4RAYBURN% ID 1+P1_2-1669_ELEESV 6!,RODEMR 6% | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1669_ELEESV 6!,RODEMR 6% | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211019 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9169 | 0.9347 | 0.92 | 1.05 | 256 | G_4RAYBURN% ID 1+P1_2-1861_PIRKEY 4! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1861_PIRKEY 4! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211020 | 18W | Proposed | P3 | 41 | 2WEIRGAT | VL |  |  |  |  | 0.9192 | 0.9347 | 0.92 | 1.05 | 257 | G_4RAYBURN% ID 1+P1_2-1863_PIRKEY 4!,LEBROCK7! | 334294 |  |  |  | 69 | 69 | 351 | EES |  |  | P1_2-1863_PIRKEY 4!,LEBROCK7! | G_4RAYBURN% ID 1 | Project Proposed | Model: New DTEC Project resolves violation and later on Formerly 12-ETI-010-HZ | 14-ETI-004-CP | 2014-06-01 | Leach 138 kV Substation: DTEC add 138 kV breakers (To accommodate DTEC/TEXLA Tie Project to close normally open point)
211021 | 18W | Proposed | P3 | 41 | CLARN 4 | VH |  |  |  |  | 1.0517 | 1.041 | 0.92 | 1.05 | 259 | G_1RVR_BND_G1! ID 1+P1_2-1640_CLARN 4!,NATCH 4! | 500180 |  |  |  | 138 | 138 | 502 | CLEC |  |  | P1_2-1640_CLARN 4!,NATCH 4! | G_1RVR_BND_G1! ID 1 |  | VH