|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| O.O. | ***16-03099***  **16-00743**  **16-01241** | | | MISO No | ***1-10309101***  **1-10840325**  **1-10840384** | File No. | 240801 |
| **Abnormal Operating Condition:** | | 230 kV Line D16R (Dorsey – Rosser)  115 kV Line CR2 (Rosser – Parkdale) | | | | | |
| **Effective Dates:** | | | 2016-06-07 from 0830 to 2016-06-10 at 1600 CST  (2016-05-07 from 0830 to 2016-06-10 at 1600 EST) | | | | |
| **Standing Guide Reference:** | | | System Study as per L. Ruchkall - Generation Pattern 1 (Summer 451- 591 MW's) | | | | |

|  |  |
| --- | --- |
| **Description of Work:** | D16R – Ratio changes are required on Rosser 230 kV Line D16R and Bank 1 due the replacement of 230 kV Breaker R9.  CR2 – Rosser to repair Aux Bus Disconnect hot spot. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None.  **Import**: If RTCA indicates that the loss F3M, ST5 or ST6 will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 225 MW  MH\_ONT\_W (Import) SOL = 170 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.  a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.  b) Review RTCA to confirm there are no new contingencies.  c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.  d) Extend the outage in COLA  e) Update TLAP outage table  f) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2016 06 01 |

Copies to:

SOSS, System Control Centre NSSS, System Control Centre

GSSS, System Control Centre GSO, System Control Centre

Operating Order Ontario IESO

MISO – St. Paul MHEB OASIS

File 240801