| O.O. | 16-08273-OO | MISO No. | 1-11026790 | File No. |  |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | 230 kV Line G37C (Glenboro – Cornwallis) Raven Lake 230-115 kV Bank 3 |
| Effective Dates: | 2016-06-25 from 1500 to 2016-06-26 at 2000 CST (2016-06-25 from 1500 to 2016-06-26 at 2000 EST) |
| Standing Guide Reference: | MH-SPC Special Study |

| System Posturing | B10T will be operated within the range of "Scheduled / SOL" 95 / 110 MW South and "Scheduled / SOL" 0 / 15 MW North. “GRAPH” MAXIMUM of 900 MW was studied for this outage for west flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 200 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. “GRAPH” MAXIMUM of 900 MW was studied for this outage for east flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 200 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. Note: “GRAPH” = sum of Grand Rapids and Power to Ponton and Herblet Lake (This acronym replaces previous “GRPTPH” which had the same parameter value ) Note: “ARC” = sum of A3R and A4D “OUT” at Ashern plus MR11 “OUT” at Raven Lake plus C28R “IN” at Cornwallis. Note: “PH” - sum of Power to Ponton and Herblet Lake from lines P19W, J30P, W73H and W74H. (N.B: This acronym replaces previous “PTPH” which had the same parameter value). |
| --- | --- |
| Description of Work: | Structure replacement. Raven Lake 115 kV Bus upgrades |
|  | TRANSFER Limits: MH-SPC West (MH Export) SOL: 225 Schedule Limit 150 Location TTC RM Transfer OM Schedule Limit (SOL) Firm Non-Firm West 225 0 225 150 75 75 150 MH-SPC East (MH Import) SOL: 75 Schedule Limit 0 Location TTC RM Transfer OM Schedule Limit (SOL) Firm Non-Firm East 75 0 75 75 0 0 0 |

| MISO RC INFO | System Intact FIRM SCHED LIMIT DYNAMIC SCHED LIMIT SOL TLR1 TLR3 MH-SPC_West (MH Export) 175 175 250 233 238 MH-SPC_East (MH Import) 0 0 75 70 71 |
| --- | --- |
|  | MISO Webtool Manual Override is Required MISO Webtool Postings TTC Firm TRM Non-Firm TRM Coeff MH_SPC _West (Export) 225 75 75 1.000 MH_SPC_East (Import) 75 0 0 1.000 |
| Special Instructions: | Use RTCA to monitor contingencies on the 230kV lines between Dorsey and Cornwallis. If RTCA inticates overload or votage violations, Brandon CT may be used to mitigate the problem or the SPC transfers may be curtailed‎ (refer to Brandon area restriction NOP). When Loss of D12P or D54N shows overload on CN9, re-dispatch Grand Rapids (increase output) or start Brandon Generation as required (if not already on). TOI Extensions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities |

| Prepared By: | P.Belanger | Date: | 2016.06.25 |
| --- | --- | --- | --- |

Copies to:

SOSS, System Control Centre		NSSS, System Control Centre

GSSS, System Control Centre		GSO, System Control Centre

Operating Order		File 240802

MHEB OASIS		MISO – St. Paul

SPC – Yong Zheng		SPC - Colin Nicholson