|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| O.O. | ***16-01930*** | | | MISO No | ***1-10927193*** | File No. | 240801 |
| **Abnormal Operating Condition:** | | 230 kV Line M32R (Riel – Transcona East - Ridgeway) | | | | | |
| **Effective Dates:** | | | 2016-07-07 from 0830 to 2016-07-07 at 1800 CST  (2016-07-07 from 0830 to 2016-07-07 at 1800 EST) | | | | |
| **Standing Guide Reference:** | | | MH-IESO Standing Guide - Generation Pattern 1 (Summer 451- 591 MW's) | | | | |

|  |  |
| --- | --- |
| **Description of Work:** | M32R – Ridgeway Current injections from Breaker R1 CT's. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None.  **Import**: If RTCA indicates that the loss F3M will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 225 MW  MH\_ONT\_W (Import) SOL = 225 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.  a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.  b) Review RTCA to confirm there are no new contingencies.  c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.  d) Extend the outage in COLA  e) Update TLAP outage table  f) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2016 06 29 |

Copies to:

SOSS, System Control Centre NSSS, System Control Centre

GSSS, System Control Centre GSO, System Control Centre

Operating Order Ontario IESO

MISO – St. Paul MHEB OASIS

File 240801