|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| O.O. | **16-08819-OO** | | MISO No. | **1-11093559** | File No. |  |
| **Name of Outage:** | | 230 kV Line S53G (St. Leon – Glenboro) | | | | |
| **Effective Dates:** | | 2016-07-08 from 2126 to 2016-07-12 at 1600 CDT  (2016-07-08 from 2126 to 2016-07-12 at 1600 EST) | | | | |
| **Standing Guide Reference:** | | MHEX Summer Standing Guide | | | | |

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Description of Work:** | | Line Fault | | | | | | | | | |
| **TRANSFER LIMITS:** | | | | | | | | | | | |
| **MH-USA South (MH Export)** | | | | | | | | | | | |
|  | |  | |  | **SOL:** | **2175** |  | **Schedule Limit** | | **1950** |
| **Location** | |  | | **RM** |  | **CRSG** | **OM** |  |  | **Schedule Limit** |
| **TTC** | | **Transfer (SOL)** | **Firm** | **Non-Firm** |
| **USA** | | **2430** | | **255** | **2175** | **150** | **75** | **1950** | **0** | **1950** |
|  | | | | | | | | | | |
|
| **MH-USA North (MH Import)** | | | | | | | | | | |
| **IROL** | | **1100** | |  | **SOL:** | **770** |  | **Schedule Limit** | | **720** |
| **Location** | |  | | **RM** |  | **CRSG** | **OM** |  |  | **Schedule Limit** |
| **TTC** | | **Transfer (SOL)** | **Firm** | **Non-Firm** |
| **USA** | | **770** | | **0** | **770** | **0** | **770** | **0** | **720** | **720** |
|  | | | | | | | | | | |
| **TLR Triggers** | | **South TLR 1** | | **South TLR 3** | **North TLR 1** | **North TLR 3** |  | | | |
| **2005** | | **2025** | **716** | **732** |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **MISO Webtool Postings** | |  | | --- | |  | | **MISO Webtool Postings** | | **TTC** | **TRM** | **Coeff** | | **MHEX\_S (Export)** | | **2430** | **480** | **1.0** | | **MHEX\_N (Import)** | | **770** | **770** | **0.065** | |

|  |  |
| --- | --- |
| **Special Notes to MISO West RC** | A) During this prior outage condition TLR on MHEX\_N may be required when Manitoba to USA flows are north to prevent post contingent overloads on B10T following a trip of M602F. |

|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **A)** **TOI Extentions** - This TOI may be extended until 23:59, by performing the following steps:   1. Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. 2. Review RTCA to confirm there are no new contingencies. 3. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. 4. Extend the outage in COLA. 5. Update TLAP outage table. 6. Provide notice to affected balancing authorities |
|  |
|  | |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S.W. Saboraki | **Date:** | 2016 07 09 |

|  |
| --- |
|  |

Copies to:

SOSS, System Control Centre MISO

NSSS, System Control Centre GSO, System Control Centre

GSSS, System Control Centre