|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. | ***16-04139*** | MISO No | ***1-10308702*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 230 kV Line D55Y (Dorsey – LaVerendrye)  |
| **Effective Dates:** | 2016-08-09 from 0800 to 2016-08-09 at 1600 CST(2016-08-09 from 0800 to 2016-08-09 at 1600 EST) |
| **Standing Guide Reference:** | MH-IESO Standing Guide - Generation Pattern 1 (Summer 451- 591 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | D55Y – Commission new LaVerendrye 230 kV Breaker R21. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  None. **Import**: If RTCA indicates that the loss F3M will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) SOL = 225 MWMH\_ONT\_W (Import) SOL = 225 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2016 08 03 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801