|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. |  ***17-07700*** | MISO No |  ***1-14418414*** | File No. | 240801 |
| **Abnormal Operating Condition:** | 115 kV Line CR4 (Parkdale - Rosser) |
| **Effective Dates:** | 2017-07-28 from 0830 to 2017-07-28 at 1600 CDT(2017-07-28 from 0830 to 2017-07-28 at 1600 EST) |
| **Standing Guide Reference:** | MHEB - IESO Standing Guide - Generation Pattern 1 (Summer 451- 553 MW's) |

|  |  |
| --- | --- |
| **Description of Work:** | CR4 – AMD and insulationing testing 115 kV Breaker CR4 C.T.s. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **Export**:  If RTCA indicates that the loss of SR3 will cause an overload on SG12, transfer from IESO may need to be curtailed. **Import**: If RTCA indicates that the loss of ST5 or ST6 will cause overload on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **MISO North RC Notes:** | MH\_ONT\_E (Export) Transfer Limit = 225 MWMH\_ONT\_W (Import) Transfer Limit = 225 MWMH\_ONT\_E (Export) Transfer Limit During Offloads = 140 MWMH\_ONT\_W (Import) Transfer Limit During Offloads = 130 MW |
|  |  |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59, by performing the following steps.a) Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.b) Review RTCA to confirm there are no new contingencies.c) Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.d) Extend the outage in COLAe) Update TLAP outage tablef) Provide notice to affected balancing authorities |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | S. Brooks | **Date:** | 2017 07 27 |

Copies to:

 SOSS, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GSO, System Control Centre

 Operating Order Ontario IESO

 MISO – St. Paul MHEB OASIS

 File 240801