| O.O. | 17-08297-OO | MISO No. | 1-14574708 | File No. | 240802 |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | 230 kV Line P52E (Ralls Island – EB Campbell) |
| Effective Dates: | 2017-07-28 from 1100 to 2017-08-04 at 1900 CDT (2017-07-28 from 1100 to 2017-08-04 at 1900 EST) |
| Standing Guide Reference: | MH-SPC Special Study (as per W. Zhang 2017-07-28) |

| System Posturing | B10T will be operated within the range of "Scheduled / SOL" 100 / 115 MW South and "Scheduled / SOL" 50 / 65 MW North. West Flow “GRAPH” MAXIMUM of 710 MW was studied for this outage for west flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 450 MW. Use "ARC Constant" value of 550 MW, for "GRAPH LIMIT" monitoring. East Flow “GRAPH” MAXIMUM of 710 MW was studied for this outage for east flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 450 MW. Use "ARC Constant" value of 550 MW, for "GRAPH LIMIT" monitoring. Note: “GRAPH” = sum of Grand Rapids and Power to Ponton and Herblet Lake (This acronym replaces previous “GRPTPH” which had the same parameter value ) Note: “ARC” = sum of U91A and A4D “OUT” at Ashern plus MR11 “OUT” at Raven Lake plus C28R “IN” at Cornwallis. Note: “PH” - sum of Power to Ponton and Herblet Lake from lines P19W, J30P, W73H and W74H. (N.B: This acronym replaces previous “PTPH” which had the same parameter value). |
| --- | --- |
| Description of Work: | SPC reported vegetation growing in Line, Line sagging in vegetation. |
|  | TRANSFER Limits: MH-SPC West (MH Export) Transfer Limit: 175 Schedule Limit 150 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm West 175 0 175 60 115 35 150 MH-SPC East (MH Import) Transfer Limit: 75 Schedule Limit 50 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm East 75 0 75 25 50 0 50 |

| MISO RC INFO | System Intact FIRM SCHED LIMIT DYNAMIC SCHED LIMIT TRANSFER LIMIT TLR1 TLR3 MH-SPC_West (MH Export) 115 150 175 163 166 MH-SPC_East (MH Import) 50 50 75 70 71 |
| --- | --- |
|  | MISO Manual Override Not Required MISO Webtool Postings TTC TRM Coeff MH_SPC (West) Export 175 60 0.417 MH_SPC_East (Import) 75 25 1.000 |
| Special Instructions: | Operate the Northern AC as per NOP-1320-02 (Section 19). This TOI is still applicable when Brandon units are online producing MW's, or Brandon #5 is online as a synchronous condenser. TOI Extensions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities |

| Prepared By: | D. Williams | Date: | 2017.07.28 |
| --- | --- | --- | --- |
| Revised By: | D. Williams | Date: | 2017.07.28 |
| Revised By: | R. Dreger | Date: | 2017.07.28 |
| Revised By: | C. Yakiwchuk | Date: | 2017.08.01 |
| Revised By: | J. Thompson | Date: | 2017.08.01 |
| Revised By: | C. Yakiwchuk | Date: | 2017.08.02 |
| Revised By: | D. Williams | Date: | 2017.08.03 |

Copies to:

SOSS, System Control Centre		NSSS, System Control Centre

GSSS, System Control Centre		GSO, System Control Centre

Operating Order		File 240802

MHEB OASIS		MISO – St. Paul

SPC – Yong Zheng		SPC - Colin Nicholson