| O.O. | 17-08736-OO | MISO No. | 1-14719796 | File No. | 240802 |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | 230 kV Line G31V (Grand Rapids – Vermillion) |
| Effective Dates: | 2017-08-24 from 0800 to 1730 CDT (2017-08-24 from 0800 to 1730 EST) |
| Standing Guide Reference: | MH-SPC Special Study (as per R. Arruda 2017-08-16) |

| System Posturing | B10T will be operated within the range of "Scheduled / SOL" 125 / 140 MW South and "Scheduled / SOL" 50 / 65 MW North. West Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for west flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 525 MW. Use "ARC Constant" value of 540 MW, for "GRAPH LIMIT" monitoring. East Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for east flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 525 MW. Use "ARC Constant" value of 540 MW, for "GRAPH LIMIT" monitoring. Note: “GRAPH” = sum of Grand Rapids and Power to Ponton and Herblet Lake (This acronym replaces previous “GRPTPH” which had the same parameter value ) Note: “ARC” = sum of U91A and A4D “OUT” at Ashern plus MR11 “OUT” at Raven Lake plus C28R “IN” at Cornwallis. Note: “PH” - sum of Power to Ponton and Herblet Lake from lines P19W, J30P, W73H and W74H. (N.B: This acronym replaces previous “PTPH” which had the same parameter value). |
| --- | --- |
| Description of Work: | Relocation of two structures on G31V near Dauphin. |
|  | TRANSFER Limits: MH-SPC West (MH Export) Transfer Limit: 250 Schedule Limit 225 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm West 250 0 250 25 225 0 225 MH-SPC East (MH Import) Transfer Limit: 75 Schedule Limit 50 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm East 75 0 75 25 50 0 50 |

| MISO RC INFO | System Intact FIRM SCHED LIMIT DYNAMIC SCHED LIMIT TRANSFER LIMIT TLR1 TLR3 MH-SPC_West (MH Export) 225 225 250 233 238 MH-SPC_East (MH Import) 50 50 75 70 71 |
| --- | --- |
|  | MISO Webtool Manual Override is Required MISO Webtool Postings TTC TRM Coeff MH_SPC (West) Export 250 25 1.000 MH_SPC_East (Import) 75 25 1.000 |
| Special Instructions: | TOI Extensions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities |

| Prepared By: | D. Williams | Date: | 2017.08.16 |
| --- | --- | --- | --- |

Copies to:

SOSS, System Control Centre		NSSS, System Control Centre

GSSS, System Control Centre		GSO, System Control Centre

Operating Order		File 240802

MHEB OASIS		MISO – St. Paul

SPC – Yong Zheng		SPC - Colin Nicholson