| O.O. | 18-02660-OO 18-00549-OO | MISO No. | 1-16971447 1-16319318 | File No. | 240802 |
| --- | --- | --- | --- | --- | --- |
| Name of Outage: | 230 kV Line B10T (Boundary Dam – Tioga) and, 230 kV Line P52E (Ralls Island – EB Campbell) |
| Effective Dates: | 2018-02-24 from 0700 to 1630 CST (2018-02-24 from 0700 to 1630 EST) |
| Standing Guide Reference: | MH-SPC Special Study (as per R. Arruda 2018-02-13) |

| System Posturing | B10T will be operated within the range of "Scheduled / SOL" 150 / 165 MW South and "Scheduled / SOL" 75 / 90 MW North. West Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for west flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. East Flow “GRAPH” MAXIMUM of 900 MW was studied for this outage for east flow conditions. Monitor Graph by using the “GRAPH LIMIT” calculation. “GRAPH” MINIMUM of 0 MW. Maximum "PH" of 500 MW. Use "ARC Constant" value of 575 MW, for "GRAPH LIMIT" monitoring. Note: “GRAPH” = sum of Grand Rapids and Power to Ponton and Herblet Lake (This acronym replaces previous “GRPTPH” which had the same parameter value ) Note: “ARC” = sum of U91A and A4D “OUT” at Ashern plus MR11 “OUT” at Raven Lake plus C28R “IN” at Cornwallis. Note: “PH” - sum of Power to Ponton and Herblet Lake from lines P19W, J30P, W73H and W74H. (N.B: This acronym replaces previous “PTPH” which had the same parameter value). |
| --- | --- |
| Description of Work: | B10T – BD922T Tapchanger repairs. P52E – SPC/MHEB Line mtce. Insulation tests on Ralls P52E Line and Sync PTs. Teleprotection maintenance. |
|  | TRANSFER Limits: MH-SPC West (MH Export) Transfer Limit: 150 Schedule Limit 125 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm West 150 0 150 25 125 0 125 MH-SPC East (MH Import) Transfer Limit: 75 Schedule Limit 50 Location TTC RM Transfer OM Schedule Limit Limit (TL) Firm Non-Firm East 75 0 75 75 0 50 50 |

| MISO RC INFO | System Intact FIRM SCHED LIMIT DYNAMIC SCHED LIMIT TRANSFER LIMIT TLR1 TLR3 MH-SPC_West (MH Export) 125 125 150 140 143 MH-SPC_East (MH Import) 0 50 75 70 71 |
| --- | --- |
|  | MISO Webtool Manual Override is Required MISO Webtool Postings TTC TRM Coeff MH_SPC _West (Export) 150 25 1.000 MH_SPC_East (Import) 75 75 0.333 |
| Special Instructions: | Operate the Northern AC as per NOP-1320-02 Rev 7 (Section 3.5.3.15) Manitoba Hydro System Operators will notify SaskPower control room if Brandon Unit 5 is unable to operate as a synchronous condenser during the outage period. Additional restrictions to Saskpower generation pattern are required if Brandon Unit 5 is not online during the outage period. TOI Extensions - This TOI may be extended until 23:59 by performing the following steps: Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. Review RTCA to confirm there are no new contingencies. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. Extend the outage in COLA. Update TLAP outage table. Provide notice to affected balancing authorities |

| Prepared By: | D. Williams | Date: | 2018.02.13 |
| --- | --- | --- | --- |

Copies to:

SOSS, System Control Centre		NSSS, System Control Centre

GSSS, System Control Centre		GSO, System Control Centre

Operating Order		File 240802

MHEB OASIS		MISO – St. Paul

SPC – Yong Zheng		SPC - Colin Nicholson