|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| O.O. | **18-03270-OO** | | MISO No. | **1-18034930** | File No. | 240801 |
| **Name of Outage:** | | 230 kV Line D55Y (Dorsey – LaVerendrye) | | | | |
| **Effective Dates:** | | 2018-05-18 from 0700 to 2018-05-18 at 1700 CDT  (2018-05-18 from 0700 to 2018-05-18 at 1700 EST) ***and,***  2018-05-19 from 0700 to 2018-05-19 at 1700 CDT  (2018-05-19 from 0700 to 2018-05-19 at 1700 EST) | | | | |
| **Standing Guide Reference:** | | MH – IESO Standing Guide – Generation Pattern 1 - 5 (Summer 166 - 553 MWs) | | | | |

|  |  |
| --- | --- |
| **System**  **Posturing** | None required |
| **Description**  **of Work:** | Insulation checks on D55Y Line PT’s and trip testing associated with co-terminated Laverendrye 230-115 kV Bank 1. |





|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | Export: If RTCA indicates that the loss of K21W will cause overloads on Whiteshell Bank 8 or the loss of K22W will cause overloads on Whiteshell Bank 7, loss of SR3 will cause an overload on SG12, transfer to IESO may need to be curtailed.  Import: If RTCA indicates that the loss of K21W will cause overloads on Whiteshell Bank 8 or the loss of K22W will cause overloads on Whiteshell Bank 7, loss of ST5 or ST6 will cause overloads on WT34, transfer from IESO may need to be curtailed. |

|  |  |
| --- | --- |
| **Special Notes to MISO North RC** | MH\_ONT\_E (Export) Transfer Limit = 225 MW  MH\_ONT\_W (Import) Transfer Limit = 219 MW  MH\_ONT\_E (Export) Transfer Limit During Offloads = 140 MW  MH\_ONT\_W (Import) Transfer Limit During Offloads = 135 MW |

|  |  |
| --- | --- |
| **Special Instructions:** | **TOI Extensions** - This TOI may be extended until 23:59 by performing the following steps:   1. 1. Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages. 2. 2. Review RTCA to confirm there are no new contingencies. 3. 3. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI. 4. 4. Extend the outage in COLA. 5. 5. Update TLAP outage table.   6. Provide notice to affected balancing authorities. |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | J.Thompson | **Date:** | **05/09/2018** |
| **Revised By:** | D.Williams | **Date:** | **05/18/2018** |

Copies to:

SPSO, System Control Centre NSSS, System Control Centre

GSSS, System Control Centre GNSO, System Control Centre

Operating Order Ontario IESO

MHEB OASIS MISO – St. Paul

File 240801