|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| O.O. | **18-00307-OO****18-08423-OO** | MISO No. | **1-11819781** | File No. | 240803 |
| **Name of Outage:** | 230 kV Line Balta – McHenry ***and,***230 kV Line Pickert – Grand Forks |
| **Effective Dates:** |   2018-07-09 2000 to 2018-07-13 1600 CDT(2018-07-09 2000 to 2018-07-13 1600 EST)  |
| **Standing Guide Reference:** | Study as per K. Long |

|  |  |
| --- | --- |
| **System****Posturing** | N/A |
| **Description****of Work:** | * Balta – McHenry
	+ Line construction on Balta McHenry
* Pickert – Grand Forks forced OOS

Line repair, 5 structures down due to storm. |



|  |  |
| --- | --- |
| **Special Notes to MISO North RC** | A) During this prior outage condition generation curtailment of the St. Joseph and St. Leon wind farms concurrent with TLR on MHEX\_N may be required when Manitoba to USA flows are north to prevent post contingent overloads on G37C following a trip of B10T or M602F.B) The SOL for MHEX\_S remain the same if the MISO RTCA and MISO Flowgate Monitoring Tool is unavailable prior to or during this outage. The SOL for MHEX\_ N is 170 if the MISO RTCA and MISO Flowgate Monitoring Tool is unavailable prior to or during this outage.  |

|  |  |
| --- | --- |
| **Special Instructions to MHEB Operator:** | **A)** **TOI Extensions** – This TOI may be extended until 23:59 by performing the following steps:1. Verify system conditions to confirm there are no additional tie line facilities outages, or new internal MH outages.
2. Review RTCA to confirm there are no new contingencies.
3. Contact MISO to confirm there are no new outages, if there are no new outages provide notice to MISO that MH is extending the TOI.
4. Extend the outage in COLA.
5. Update TLAP outage table.
6. Provide notice to affected balancing authorities

**B)** **When called upon by MISO for the supply of CRSG:**If Real Time Contingency Analysis (RTCA) indicates a post contingent overload condition on Y51L for the contingent loss of D14S - redispatch MH generation to maintain CRSG delivery as per:* Start Brandon Gas Generation and run up to 60 MW.

Brandon generation must be re-dispatched from HVDC generation at Dorsey* After 60 MW re-dispatch is complete, should RTCA continue to indicate a post contingent overload condition on Y51L due to the contingent loss of D14S, continue to re-dispatch generation from Brandon gas in 10 MW increments until post contingent overload on Y51L has been mitigated.
* The mitigation must be completed within 30 minutes.
 |

|  |  |  |  |
| --- | --- | --- | --- |
| **Prepared By:** | Paul Grestoni | **Date:** | **2018-07-09** |
| **Revised By:** | Paul Grestoni | **Date:** | **2018-07-09** |

Copies to:

 SPSO, System Control Centre NSSS, System Control Centre

 GSSS, System Control Centre GNSO, System Control Centre

 Operating Order Ontario IESO

 MHEB OASIS MISO – St. Paul