Final Report

Aug 22, 2002

Montana-Southeast Path Study

Winter 2002-2003

Northwest Operating Capability Study

## Description of Path

The Montana – Southeast (MTSE) path consists of the following lines:

A.  Billings - Yellowtail 230 kV line (metered at Yellowtail, with phase shifter)

B.  Rimrock - Yellowtail 161 kV line (metered at Rimrock, with phase shifter)

C.  Hardin - Crossover 230 kV line (metered at Crossover)

D.  Huntley Tap - Crossover 230 kV line (metered at Crossover)

These lines provide a path from Montana to WAPA UM and PACE at the Southeast boundary of Montana's system.  This path has never been formally rated.  Montana is not proposing to enter the WECC path rating process to rate this path.  Our understanding is that NOPSG has requested that we study this path to establish an operating limit.  This study is our response to that request.

## Base Cases Descriptions (see Excel sheet “PF” )

### Light winter:

The light load case was modified to allow regulation by the TOT2 phase shifters.   Generation in Colorado and Wyoming was adjusted to encourage flows north when required. Schedules were adjusted to the Northwest.  The full Miles City DC (MCDC) model is used in the cases prepared by Montana.  The more accurate DC model replaces the negative load representation in the cases as provided by the WECC.

Yellowtail generation was varied from 20 to 288 MW, the full potential operating range of the plant.   On northbound flow cases,  MCDC was varied from 50 to 195 MW east to west. The 50 MW minimum is based on conversations with WAPA,  the operator of Miles City indicating that the minimum sustained operating level at Miles City is 50 MW. Colstrip was varied from full load to levels specified on the winter 2002-03 nomograms to capture the sensitivity of the MTSE OTC to Colstrip generation.

### Heavy winter:

For the heavy winter case, generation in Colorado and Wyoming was increased to create more import to Montana.   The Desert Southwest phase shifters were allowed to regulate.  The full MCDC model was included. Surplus power was generally scheduled to the Northwest. Yellowtail generation was varied from 20 to 288 MW, the full potential operating range of the plant. On northbound cases,  MCDC was varied from 50 to 195 MW east to west.  Comparing the winter 01-02 case and the winter 02-03 case shows the effects of newly-modeled load on the OREBASIN 230 bus.  This load accounts for a 10% reduction in the 374 MW NB (winter 01-02 OTC ) vs 337 MW NB (winter 02-03 OTC).

## Remedial Action Schemes

The Montana Power Acceleration Trend Relay (ATR) at Colstrip was modeled to simulate unit tripping.

A revision to the previous ATR to reduce over-tripping (ATR-OR) was completed in October, 2001. For these studies,   MPC is operating the ATR in the OR mode.

The BPA RAS scheme described in Standing Order 319 trips the Miles City DC  tie and two reactors at Garrison as necessary.   However, it should be noted MCDC does not trip for Broadview-Garrison outages.

## Disturbances

As with the winter 2001-2002,  spring 2002 and summer 2002 MTSE studies and the OTCPG approved winter 2002-03 study plan, MPC used the Broadview-Garrison double 500 kV outage as the limiting event for the winter 2002-03 MTSE OTC.

Transient Study Results (Excel sheet “Results” and “Graphs”)

North to South

This path has been studied in the north to south direction from the summer of 1999 through the summer of 2001.  Each season results in 600 MW OTC.  The path is no longer studied in the southbound direction as nothing affecting the OTC has changed on or around the path from the previous seasonal studies.

Every study to-date indicates that the North to South operating limit on the MTSE path is at least as great as the informal rating of 600 MW.  This OTC does not depend on whether the heavy or light case was used.    The North to South influence of Yellowtail generation is not tested because increasing Yellowtail can overload the paths south of Yellowtail.  MPC expects the transient performance to improve with increased Yellowtail generation.  Yellowtail generation on the 600 MW north to south studies is at 20 MW which is under the estimated limit for overloads of the paths south of Yellowtail.

### South to North

All buses in the winter 2002-03 OTC cases pass WECC criteria for all MTSE nomogram corner points for the Broadview-Garrison double 500 kV outage.

Previous study work indicated that the OTC of the MTSE path is sensitive to the amount of generation at the Yellowtail plant, to the generation at Colstrip, heavy or light loads and the  MCDC east to west level.  All of these quantities are tested and the nomograms and operating procedures reflect their influence on the OTC.  The additional load at OREBASIN 230 affects some nomogram corner points at YT=20.

# Yellowtail Generation

Two levels of Yellowtail generation were studied (20 MW and 288 MW) based on indications from WAPA that this was appropriate. However all appropriate MTSE values are easily derived from the winter 2002-03 nomograms for any level of Yellowtail generation.

###### Heavy Load

The resulting heavy load OTC nomogram with Colstrip fully loaded for MTSE was 337 MW (YT=20), 600 MW (YT=288). An additional 600 MW (YT=20 and 288) corner point is developed to allow adjusting the OTC for less-than-full Colstrip generation levels.  For this season, if  Colstrip is less than 1313 MW, MTSE is 600 regardless of Yellowtail generation.

###### Light Load

The light load nomogram has MTSE at 415 MW with Colstrip full, YT=20, and MCDC=195 E to W.  For the same conditions  except YT=288, MTSE is 448 MW.  With Colstrip at 1800 and YT=288,  the MTSE northbound OTC is 600 MW.  For Colstrip generation of 1628 MW or less,  MTSE is 600 MW regardless of YT generation.

Miles City DC flows vs. northbound MTSE
A reduction in the Miles City DC east to west flow of 1 MW results in a reduction in northbound MTSE by 1.41 MW (YT=20) to 1.46 MW (YT=288) in the heavy load case.

A 1 MW reduction in MCDC in the light load case results in about 1.5 MW (YT=20) to 0.81 MW (YT=288)  MW reduction in northbound MTSE.

Conclusions

- Slight reductions (374 - 337 = 10% reduction) in the winter 02-03 OTC vs winter 01-02 OTC at YT=20 are due to load changes in Wyoming on the OREBASIN 230 bus.

- The Montana - Southeast path can accommodate flows of 600 MW in the North to South direction in both heavy and light load cases.

- The South to North OTC varies for heavy and light load periods for this season and is affected by Yellowtail and Colstrip generation and MCDC flows with the following corner points:

| Heavy North-bound MTSE OTC |
| --- |
| Colstrip Generation | YT = 20 MW | YT = 288 MW |
| FULL | OTC = 337 MW | OTC = 600 MW |
| 1313 MW or less | OTC = 600 MW | OTC = 600 MW |
| -1 MW MCDC = - 1.41 MW MTSE (-1.46 as YT =288 MW) |

| Light North-bound MTSE OTC |
| --- |
| Colstrip Generation | YT = 20 MW | YT = 288 MW |
| FULL | OTC = 415 MW | OTC = 448 MW |
| 1800 MW or less | OTC = 501 MW | OTC = 600 MW |
| 1761 MW or less | OTC = 600 MW | OTC = 600 MW |
| -1 MW MCDC = -1.5 MW MTSE (-0.81 as YT = 288 MW) |

## Q-V Analysis Results (Excel sheet “QV-heavy & QV-Light”)

Montana no longer applies a QV criteria on this path  as it is a transient limited path. Past QV analysis has always  reflected that this  path has ample reactive margin in all load areas and performs well in the +5% cases.  The resulting reactive margins are from  the trauma of the loss of 3 Colstrip units for the double Broadview-Garrison outage. QV measures the ability to reliably serve load. The major load center in this area is Billings,  which is served by at least three other good 230 kV sources and has over 500 MW of local generation for an area with about 375 MW load during heavy load period.

The table below represents the summer of 2000 QV-analysis.

|  |  |  | Northbound |  |  |
| --- | --- | --- | --- | --- | --- |
| Bus | Quantity |  | Yellowtail = 20 MW, MCDC – 195 |  |
|  |  |  | Broadview - Garrison 1 | Broadview - Garrison 1&2 | Yellowtail-Crossover 230 |
| BUFFALO 230 | QV |  | -441.5 | -290.2 | -434.8 |
|  | Voltage |  | 0.6 | 0.6 | 0.6 |
| FRANNIE 230 | QV |  | -300.5 | -195.8 | -285.1 |
|  | Voltage |  | 0.5 | 0.6 | 0.6 |
| GARLAND 230 | QV |  | -280.7 | -189.4 | -268.9 |
|  | Voltage |  | 0.5 | 0.6 | 0.6 |
| GOOSE CK 230 | QV |  | -394.4 | -232.4 | -378.4 |
|  | Voltage |  | 0.6 | 0.6 | 0.6 |
| KAYCEE 230 | QV |  | -401.6 | -306.8 | -399.8 |
|  | Voltage |  | 0.5 | 0.6 | 0.5 |
| OREBASIN 230 | QV |  | -259.7 | -179.5 | -253.2 |
|  | Voltage |  | 0.5 | 0.6 | 0.6 |
| SHERIDAN 230 | QV |  | -393.8 | -234.4 | -378.8 |
|  | Voltage |  | 0.6 | 0.6 | 0.6 |
| WILSALL 230 | QV |  | -331.2 | -328.4 | -338.2 |
|  | Voltage |  | 0.6 | 0.7 | 0.6 |
| WYODAK 230 | QV |  | -347.6 | -270.0 | -347.7 |
|  | Voltage |  | 0.8 | 0.8 | 0.8 |
| * Printed next to MVAR output indicates Q-V Curve minimum not found |  |

## Answers to specific OTCPG questions

The OTCPG questions and answers for Montana Southeast include:

1. When was the last time the path was studied?
This path was studied for the summer 2002, spring 2002, winter 01-02, summer 2001, spring 2001, winter 2000-2001, summer 2000, spring of 2000, winter of 99-00, and the summer of 1999.

2. What is the critical season for this path?

All three seasons perform similarly.

3. Full studies or check cases?
	All studies to date have been full cases.

4. What are the impacts of this path on system reliability?  Are problems local only or is there potential for cascading outside the local area?

This path is located in Eastern Montana and internal disturbance (including doubles) cause minor voltage dips in the immediate area.  The double 500 kV outages cause three Colstrip units to trip and limits the OTC because of transient voltage dip performance which can either be in Montana or in Northern Wyoming.

The path is fully controlled with three (3) phase-shifting transformers and ample local generation (Yellowtail and Miles City DC) which solves most local problems which may arise.  No cascading is experienced in any of our study work at the transfer levels recommended.

5. What is the limiting factor: transient, reactive, thermal?

Transient voltage dip in Montana or northern Wyoming.

6. Have load and generation changes been accounted for?

Yes

7. Is it appropriate to study this path in the OTCPG arena?

Yes

## Additional Comments

### Thermal Rating (reflected in existing operating procedures)

It should be noted that any outage that called for a quick reduction in the flow on the MTSE path could be accommodated by adjusting the phase-shifting transformers, the Miles City DC tie flow, the generation at Yellowtail and Colstrip or Corette, or some combination of all three.  For this reason, traditional issues such as momentary overloading that may occur immediately after lines are opened are not significant.  Of course, the initial transient event must perform.

The most critical thermal situation is when Montana-Southeast is southbound and Pacificorp is operating Yellowtail-south per their nomogram . In this situation, the loss of the Yellowtail - Frannie 230 kV line  may overload the 115 kV line from Greybull to Lovell.  This overload can be relieved in the 5-10 minute time-frame by the methods described above.  WAPA owns the 115 line as well as the Yellowtail generation and is prepared to handle this local thermal problem, that has no potential to cascade.  For years, Montana’s operating procedures for Southbound MTSE have specifically stated how to coordinate with WAPA and Pacificorp to eliminate Yellowtail-south overloads.  Pacificorp and WAPA both participate in the Rocky Mountain OTC sub-regional study group, which reviews Wyoming transmission.