Montana-Idaho (Path 18) Study Report

Summer 2006 Operating Season

April 3, 2006

Submitted to:

Northwest Operational-Planning Study Group (NOPSG)

Submitted by:

Chuck Stigers

Planning Engineer

NorthWestern Energy

Montana – Idaho (Path 18) – 2006 Summer OTC Study Report

# INTRODUCTION

Evaluating the capacity (OTC) with improvements that were added in 2005 to compensate for the removal of the BPA shunt capacitor bank at their Anaconda (Mill Creek) substation.

# PATH DESCRIPTION

The Montana – Idaho path consists of two lines:

- The Mill Creek – Antelope 230 kV line (AMPS line) with load taps at Peterson Flats and AMPS and,

- The Dillon Salmon – Big Grassy 161 kV line.

These lines provide a path from southwest Montana to southeast Idaho (Idaho Falls area).  Before the summer of 2004 the path was rated (Existing Rating) at 337 MW in both directions.  The OTC limit on the path is lower than 337 MW for northbound flow with heavy summer conditions.  This OTC reduction is caused by the presence of heavy loads in the eastern Idaho area (south end of the path), that constrain the system south of this path limiting the ability of the Idaho system to deliver power to the path.

# ASSUMPTIONS/METHODOLOGY

The rating for this path is based on the post-contingency voltage performance for service to loads served by both lines.  Specifically, the Salmon, Idaho load that is served from the Peterson Flats tap, and the Dillon, Montana load that is served from the Dillon-Salmon 161 kV bus at the northern terminal of the Dillon-Salmon – Big Grassy tie line.  There is also some load in the Salmon, Idaho area that is served from the Dillon-Salmon station.  It is important to note that the path will not collapse at flows significantly higher than the rating.  Instead there is a steady decline in the voltage performance.  It is also important to note that the limit is based on performance that is deemed acceptable by the parties that serve loads connected to these lines rather than by thermal limits or stability considerations.

There three improvements were made in 2005 by NWE and IPC to increase the capacity of Path 18:

- NWE installed two new 6 MVAr banks of switched shunt capacitors on the 69 kV bus at Dillon, bringing the total to 24 MVAr.

- IPC is installed a switched shunt capacitor bank on the 230 kV bus at Peterson Flats with a 35 MVAr (based on 242 kV) rating.

- NWE installed a 37.7 MVAr switched shunt capacitor bank on the 230 kV bus at the Mill Creek (Anaconda) substation at the north terminal of the AMPS line.

In 2005 the rating of this path was increased to 356 MW north to south through the WECC three phase rating process.  The increase was based on the findings reported in the summer 2005 OTC study.  The OTC for this path was determined to be:

- 356 MW when the flow West of Bridger is such that only one Bridger unit would be tripped for the BKBG (see definition below) event.

- 351 MW when the flow West of Bridger is such that two Bridger units would be tripped for the BKBG (see definition below) event.

NWE further chose to apply a TRM for this path equal to the difference between the OTC and 337 MW.  Thus, when the flow West of Bridger is less than the threshold for two unit tripping at Bridger the TRM would be 19 MW, and when the flow West of Bridger is equal to or greater than the threshold for two unit tripping the TRM would be 14 MW.  When the actual flow is approaching 337 MW on this path NWE will begin to take measures including the reduction of schedules (outlined in the operating procedure) to limit the flow to 337 MW.  If the efforts to prevent the flow from exceeding 337 MW are unsuccessful, these actions would culminate in the opening of Path 18 to prevent extended operation at levels above 337 MW.

## BRIDGER TRIPPING SCHEME

The Bridger tripping algorithm calls for tripping based on the formula:

Trip amount (net MW) = 1.3 * (Bridger West Flow – 1250 MW)

For this to yield a trip amount greater than the nominal net capacity of a single machine (Pmax = 562 MW, auxiliary load = 30 MW) the Bridger West flow would have to exceed 1635 MW (based on 500 MW net).

## PLANNED OPERATING PRACTICE

Scheduling on this path (and actual flow) will be limited to 337 MW with the described improvements in place.  NWE and the other owners of the path have agreed to reserve the capacity above 337 MW as explicit margin (TRM).  This study shows that at the stated OTC flow levels (see discussion below) the post-transient voltage performance roughly matches the performance that the owners of the path have previously agreed to accept for the worst-case contingency.   The OTCs quoted are based on waiving the WECC criterion (10 percent voltage change for double contingency) for this unlikely contingency.

CRITERIA FOR EVALUATIONOF THE OTC OF THE PATH
The OTC is based on the post-transient voltage performance required at the relevant load buses.   The purpose of this study is to demonstrate that the OTC of the path for summer 2006 is 356/351 MW.  The basis for the original rating of 337 MW (see WECC path rating catalog) is somewhat less conservative than the present WECC criteria.  The three owners of the Path 18 lines (IPC, NWE, and PACE) have agreed to this criterion.  The criterion used for this study was to achieve the original performance documented in joint studies that were performed in 2004 (see benchmark results in SUMMARY page of results workbook).  At the proposed OTC a case representing the worst case contingency achieved a performance roughly equal to the benchmark at both Dillon and Peterson Flats.

## METHODOLGY

For the north to south (Montana to Idaho) loading on the Montana-Idaho Path (Path 18), the “06hs4ap” base case was used for this study.  The base case had a flow of 322 MW on this path.  Generation adjustments were made to the case to increase the flow creating a series of cases between 327 and 368 MW.  These cases were then used to evaluate the performance of the path for 12 different outage cases that demonstrate the system performance for the seven most critical outages and for five other important outages.  For each of the seven critical outages two cases were solved (one with and one without switching the new 12 MVAr switched shunt capacitor bank on at Dillon for the post-contingency case).  The other two system improvements (items 2 & 3) were modeled as in-service before and after the switching events.  For the five other outages of interest the new capacitors at Dillon were kept out-of-service post-contingency.  All results were tabulated in an Excel “workbook” along with documentation on how to interpret the table of results.

# DISTURBANCES

## MONTANA CONTINGENCIES

The critical outages that are internal to Path 18 are the loss of the Mill Creek – Antelope 230 kV line and the loss of the Dillon-Salmon – Big Grassy 161 kV line.

## OTHER CONTINGENCIES

There are outages that are external to the path (e.g. double-contingencies on the Bridger system that require two-unit tripping) that result in poorer performance than the internal contingencies.  For southbound flows the critical (external) outage is the simultaneous loss of the Bridger – Kinport and Bridger – Goshen 345 kV lines (BKBG).  When the flow on the Bridger West Path (Path 19) are great enough (see algorithm description above) to require the tripping of two Bridger units for this contingency.  For this event, the post-contingency flow on the path is greater than the pre-contingency flow.  This flow increase results in depressed voltage at the Peterson Flats 230 kV load tap.  This causes low voltage on the 69 kV system that serves Salmon, Idaho from Peterson Flats.  (The 69 kV system is not modeled in WECC base cases.)  Also, the AMPS 230 kV load-tap (along with the 69 kV system served from that tap) and the Dillon-Salmon 161 kV bus (along with the loads served from the Dillon-Salmon substation) are subjected to low voltages.

This study also examines the performance when Bridger generation is reduced (pre-contingency) to levels that result in tripping only one unit for the BKBG event.  The system performance under these conditions is significantly improved since the incremental flow for the BKBG contingency is reduced.

Results are presented that indicate acceptable (i.e. comparable) performance at pre-event flows up to 356 MW when the Bridger West flow is less than the threshold for tripping two Bridger units for the BKBG event.  Thus the OTC of the path is 356 MW for this condition.

## DESCRIPTION OF PETERSON FLATS SERVICE TO SALMON AREA

At the Peterson Flats tap there is a voltage-regulating transformer to regulate the 69 kV voltages downstream on the 69 kV system that serves the Salmon, ID area.  This regulator is capable of correcting the voltage up to 10 percent.  Also, there are regulating transformers at the major load serving terminals further down stream on the 69 kV system.  Thus, the steady-state voltage at the loads can be corrected even when the 230 kV bus is quite low.  Since this is the only load that depends on the Peterson Flats tap for its source, the absolute voltage at Peterson Flats is not critical as long as the 69/69 kV regulating transformer has not reached its limit tap.

## DESCRIPTION OF DILLON AREA SERVICE

The Dillon-Salmon substation is now equipped with four banks of switched shunt capacitors (6 MVAR each).  The first two banks are automatically switched into service when the voltage falls below 0.9826 PU (67.8 kV).  The first bank is presently set to switch in after a one second delay, and the second will switch after a 10 second delay.  The other two banks are automatically switched when the local voltage falls below 0.93 PU (intentionally set very low so that these are switched only for the worst case contingencies).  Presently, there is no tap-changing transformer to regulate the 69 kV buses in the Dillon area.  In this study two of these banks are on pre-event, and the other two are switched on post-contingency for the stated OTC result.  Results are tabulated for the critical contingencies both with and without switching the third and fourth bank.

# STUDY RESULTS

The study showed that the north-to-south operating limit on the path is 356 MW when the three new sets of capacitors (listed above) are utilized and the flow on the West of Bridger path is less than the threshold for tripping two Bridger units.  Also, the study showed that the OTC is 351 MW when the West of Bridger flow is greater than the threshold for tripping two Bridger units.

## BENCHMARK SYSTEM PERFORMANCE

With an initial flow of 337 MW on the path and the BPA capacitor bank on at Anaconda the initial bus at the regulated 69 kV bus at Peterson Flats was 1.0357 PU, and the post-transient voltage was 0.8625 PU (relative voltage of 0.8328).  For the Dillon S 69 kV bus the starting voltage was 0.9909 PU, the post-transient voltage was 0.8565 PU, and the relative voltage was 0.8644 PU.  (See SUMMARY page of <<results_2006hs_p18otc.xls>>.)

## NEW SYSTEM PERFORMANCE

With 355 MW flowing on Path 18, and 1603 MW flowing on the Bridger West Path, the initial voltage at Peterson Flats 69 kV regulated bus is 1.0356 PU, and the post-disturbance voltage is 0.9267 PU (0.8949 relative to the starting voltage); the pre-event voltage at the Dillon S 69 kV bus is 0.9340 PU, and the post-disturbance voltage is 0.8807 PU (relative voltage = 0.9429).  Thus, since the relative voltage meets the original benchmarked performance requirements at both locations, the OTC can be increased to 356 MW with West of Bridger less than the two unit-tripping threshold.

With 351 MW flowing on Path 18, and 1880 MW flowing on the Bridger West Path, the initial voltage at Peterson Flats 69 kV regulated bus is 1.0364 PU, and the post-disturbance voltage is 0.8681 PU (0.8376 relative to the starting voltage); the pre-event voltage at the Dillon S 69 kV bus is 0.9304 PU, and the post-disturbance voltage is 0.8293 PU (relative voltage = 0.8914).  Thus, since the relative voltage meets the original benchmarked performance requirements at both locations, the OTC is 351 MW with West of Bridger greater than the two unit-tripping threshold.

Study results are contained in the Excel workbook “results_2006hs_p18otc.xls” included with this report.  This workbook contains several worksheets:

- PV_PF_BR-OFF – shows a graph of the PV analysis at the Peterson Flats bus for the critical outage (Bridger – Goshen, and Bridger – Kinport)  (BKBG) with one Bridger unit off-line.

- PV_DS_BR-OFF – shows a graph of the PV analysis at the Dillon 69 kV bus for the critical outage (BKBG).

- PV_BR-OFF – shows the numeric PV analysis results for the BKBG outage with one Bridger unit off.

- PV_PF_BR-ON – shows a graph of the PV analysis results at the Peterson Flats bus for the critical BKBG outage with all four Bridger units on.

- PV_DS_BR-ON – shows a graph of the PV analysis results at the Dillon bus for the BKBG outage with all four Bridger units on.

- PV_BR-ON – shows the numeric PV analysis results for the BKBG outage with all four Bridger units fully loaded.

- ANNOTATION – provides a key to the column heading in the main data spreadsheet.

- CASE_NAMES – gives the naming convention used to name outage cases for a given pre-event case.

- SUMMARY – gives a brief summary of the most significant results.

- log_p18otc_pf – is the main table of results.

The reactive margin analysis showed that a total flow on the path of 361 MW can exist as a pre-event flow, and any one of the critical contingencies can be sustained without reaching the “nose” of the P-V curve for the path.  Since post-fault powerflow cases with Path 18 at 385 MW solve without a complete voltage collapse, the “nose” of the PV curve is clearly greater than 385 MW.  Thus, the path more than meets the WECC minimum standards of 2.5 percent overload capacity for Level C, and 5 percent overload capacity for Level B events.  Thus, the practical limit is based on acceptable load service as stated above.

# CONCLUSIONS

The Montana-Idaho path (Path 18) can accommodate flows of 356/351 MW (see bullets above) in the North to South direction with the new shunt capacitor additions at Dillon, Peterson Flats, and Anaconda as described above.  This will result in performance that is comparable to that achieved before 2004.  Setting the OTC at this level assumes that voltage performance criteria adopted in the past is still acceptable to all affected parties.

The Montana-Idaho path (Path 18) meets the PV-performance criteria of the WECC with flow limit of 356 MW with the West of Bridger flow below the two-unit tripping threshold, and 351 MW with the West of Bridger flow equal to or greater than the two-unit tripping threshold.