## Summary
Case | West of Bridger | Path 18 Flow | pfv | pregv | dsv | ds6v | NOTES:
amps_base.sav | 1923 | 337 | 0.9383 | 1.0357 | 0.9846 | 0.9909
amps_base_brgo_brkp.sav |  | 372 | 0.7948 | 0.8625 | 0.8585 | 0.8565 | Benchmark reference case. Sets performance standard agreed to in 2004.
relative voltages (PU) |  |  | 0.84706 | 0.83277 | 0.87193 | 0.86437 | BPA CAP in place (2004).
p18otc351.sav | 1879.6 | 351.3 | 0.92028 | 1.0364 | 0.94692 | 0.93035
p18otc351_brgo_brkp_s.sav |  | 389 | 0.79273 | 0.8681 | 0.83271 | 0.82933
relative voltages (PU) |  |  | 0.8614 | 0.83764 | 0.87939 | 0.89142 | Check case results. With Bridger West > 1650 MW (2 trips @ Bridger)
p18otc355b.sav | 1603.8 | 354.9 | 0.91963 | 1.0356 | 0.9503 | 0.934
p18otc355b_brgo_brkp_s.sav |  | 392.5 | 0.84305 | 0.92672 | 0.87838 | 0.88069
relative voltages (PU) |  |  | 0.91673 | 0.89485 | 0.92432 | 0.94292 | Check case results. With Bridger West < 1650 MW (1 trip @ Bridger)

## Outage Definitions
set | out_n | grp_n | case_name | Outage discription:
1 | 0 | 0 | *.sav | No outages.
1 | 1 | 1 | *_amps.sav | Remove Anaconda - Peterson Flats - AMPS - Antelope (and Salmon area served from PF).
1 | 2 | 2 | *_amps_s.sav | Remove Anaconda - Peterson Flats - AMPS - Antelope (and Salmon area served from PF) switch 12 MVA cap at DS.
1 | 3 | 3 | *_dsbg.sav | Remove Dillon S - Dell - Big Grassy.
1 | 4 | 3 | *_bloxhcb.sav | Remove Brownlee - Oxbow and Brownlee - Hells Canyon lines (with McCall sub-transmission).
1 | 5 | 4 | *_bloxhcb_s.sav | Remove Brownlee - Oxbow and Brownlee - Hells Canyon lines (with McCall sub-transmission) and switch 12 MVA caps at DS 69kv.
1 | 6 | 4 | *_blhcoxll.sav | Remove Brownlee - Hells Canyon and Oxbow - Imnaha - Lolo.
1 | 7 | 5 | *_blhcoxll_s.sav | Remove Brownlee - Hells Canyon and Oxbow - Imnaha - Lolo and switch 12 MVA caps at DS 69 kv.
1 | 8 | 5 | *_mpsl.sav | Remove Midpoint - Burns - Summerlake line.
1 | 9 | 6 | *_mpsl_s.sav | Remove Midpoint - Burns - Summerlake line and switch 12 MVA caps at DS 69kv.
1 | 10 | 6 | *_angr1.sav | Remove Mill Creek - Garrison line (AMPS).
1 | 11 | 7 | *_angr2.sav | Remove Anaconda BPA - Garrison line.
1 | 12 | 8 | *_angr12.sav | Remove both Anaconda - Garrison lines.
1 | 13 | 9 | *_grgr.sav | Remove Garrison 500/230 kV transformer.
1 | 14 | 10 | *_anpf.sav | Remove Anaconda - Peterson Flats (Open ended at Anaconda, with 35 MVA reactor on.
1 | 15 | 11 | *_antbdy.sav | Remove Antelope - Brady 230 kV line.
1 | 16 | 11 | *_brbo_brkp.sav | Remove Bridger - Borah and Bridger - Kinport lines with Bridger tripping (per RAS spec).
1 | 17 | 11 | *_brbo_brkp_s.sav | Remove Bridger - Borah and Bridger - Kinport lines with Bridger tripping (per RAS spec) and switch 12 MVA caps at DS 69 kv.
1 | 18 | 12 | *_brgo_brkp.sav | Remove Bridger - Goshen and Bridger - Kinport lines with Bridger tripping (per RAS spec).
1 | 19 | 12 | *_brgo_brkp_s.sav | Remove Bridger - Goshen and Bridger - Kinport lines with Bridger tripping (per RAS spec) and switch 12 MVA caps at DS 69 kv.

## Annotation
Column | Label | Description | UNITS
A | case name | Full name of powerflow case. | none
B | nojd | North of John Day Path flow | MW
C | coi | California - Oregon Intertie flow. | MW
D | celilo12 | PDCI 230 Kv terminal flow | MW
E | celilo34 | PDCI 500 Kv terminal flow | MW
F | bcnw | BCH - US (NW) | MW
G | woh | West of Hatwai | MW
H | nwhydro | Northwest MT Hydro (WMH) | MW
I | mtnw | Montana - NW (Path 8) | MW
J | mtut | Montana - UT Path 18 | MW
K | bvgr1p | Broadview - Garrison line 1 | MW
L | bvgr2p | Broadview - Garrison line 2 | MW
M | bvjgp | Broadview - Judith Gap | MW
N | srwsp | Shorey Road - Wilsall | MW
O | crbtp | Columbus-Rapelje - Big Timber | MW
P | bvbvp1 | Broadview 230/100 kV XFRMR1 | MW
Q | bvbvp2 | Broadview 230/100 kV XFRMR2 | MW
R | wobvp | West of Broadview total | MW
S | cs1g | Colstrip Unit 1 | MW
T | cs2g | Colstrip Unit 2 | MW
U | cs3g | Colstrip Unit 3 | MW
V | cs4g | Colstrip Unit 4 | MW
W | cstot | Colstrip total generation | MW
X | mcp | Miles City DC flow (westbound) | MW
Y | wocs | West of Colstrip | MW
Z | woxo | West of Crossover | MW
AA | idnw | Idaho - Northwest | MW
AB | mpsl | Midpoint - Summer Lake (westbound) | MW
AC | borahw | West of Borah | MW
AD | brdgrw | West of Bridger | MW
AE | pathc | Path C | MW
AF | path15 | Path 15 | MW
AG | tot2 | TOT2 | MW
AH | mtse | Montana - Southeast (MTSE) | MW
AI | ytno | Yellowtail North | MW
AJ | ytso | Yellowtail South | MW
AK | tot4a | TOT4A | MW
AL | tot4b | TOT4B | MW
AM | ytgen | Yellowtail generation total | MW
AN | libg | Libby generation | MW
AO | noxg | Noxon generation | MW
AP | hhg | Hungry Horse generation | MW
AQ | cgg | Cabinet Gorge generation | MW
AR | ckld | CFAC (Con Kelly) Load total | MW
AS | hhnet | Hungry Horse net = (hhg - ckld) | MW
AT | fhnld | Flathead Area Net Load (see report) | MW
AU | corg | Corette generation | MW
AV | mt1 | Montana I generation | MW
AW | bgi | Billings Generation Inc. | MW
AX | thrml | Montana thermal generation total | MW
AY | kerr | Kerr generation | MW
AZ | tfls | Thompson Falls total generation | MW
BA | krtf | Kerr + Thompson Falls generation | MW
BB | haus | Hauser generation | MW
BC | holt | Holter generation | MW
BD | canf | Canyon Ferry generation | MW
BE | rbow | Rainbow generation | MW
BF | beag | Black Eagle generation | MW
BG | ryan | Ryan generation | MW
BH | coch | Cochrane generation | MW
BI | morn | Morony generation | MW
BJ | madn | Madison generation | MW
BK | mogen | Missouri River total generation | MW
BL | mttld | Montana total load | MW
BM | mttlss | Montana total losses | MW
BN | mtti | Montana total interchange | MW
BO | mttg | Montana total genration | MW
BP | cfkapct | Columbia Falls - Kalispell percent of rating. | Percent
BQ | hsdxpct | Hot Springs - Dixon percent of rating. | Percent
BR | bkpct | Burke - BurkeAVAA percent of rating. | Percent
BS | pcpct | Pine Creek 230/100 kV loading-percent of rating. | Percent
BT | rrpsa | Rimrock PST angle setting. | degrees
BU | blpsa | Billings PST angle setting. | degrees
BV | xopsa | Crossover PST angle setting. | degrees
BW | hmltnv | Hamilton MT bus voltage. | PU
BX | anv | Anaconda 230 kv voltage. | PU
BY | an1v | Anaconda 161 kv voltage. | PU
BZ | pfv | Peterson Flats 230 kV voltage. | PU
CA | pf6rv | Peterson Flats 69 kV voltage (regulated). | PU
CB | amv | AMPS 230 kV voltage. | PU
CC | am6v | AMPS 69 kV voltage. | PU
CD | antv | Antelope 230 kV voltage. | PU
CE | dsv | Dillon S 161 kV voltage. | PU
CF | ds6v | Dillon 69 kV voltage. | PU
CG | bggv | Big Grassy 161 kV voltage. | PU
CH | bgg6v | Big Grassy 69 kV voltage. | PU
CI | jfrpv | Jefferson "P" 161 kV voltage. | PU
CJ | jfrsniv | Jefferson "I" 161 kV voltage. | PU
CK | an23q | Anaconda 230 kV switched shunt. | MVA
CL | an16q | Anaconda 161 kV switched shunt. | MVA
CM | ov23q | Ovando 230 kV switched shunt. | MVA
CN | ws23q | Wilsall 230 kV switched shunt. | MVA
CO | gr50q | Garrison 500 kV switched shunt. | MVA
CP | hs50q | Hot Springs 500 kV switched shunt. | MVA
CQ | tt50q | Taft 500 kV switched shunt. | MVA
CR | ds69q | Dillon S 161 kV switched shunt. | MVA
CS | pf23q | Peterson Flats 230 kV switched shunt. | MVA
CT | gran1 | Garrison - Anaconda ckt 1 (PCT loading) | PCT
CU | gran2 | Garrison - Anaconda ckt 2 (PCT loading) | PCT
CV | anpf | Anaconda - Petersonflats (PCT loading) | PCT
CW | ands | Anaconda - Dillon S (PCT loading) | PCT
CX | jfrsn | Jefferson PST (PCT loading) | PCT
CY | htwll | Hatwai - Lolo (PCT loading) | PCT
CZ | llimn | Lolo - Imnaha (PCT loading) | PCT
DA | bleehcn | Brownlee - Hellscnyn (PCT loading) | PCT
DB | lala | Ladd - LaGrange (PCT loading) | PCT
DC | bomo | Bonanaza - Mona (PCT loading) | PCT
DD | brdgr1 | Jim Bridger 1 | MW
DE | brdgr2 | Jim Bridger 2 | MW
DF | brdgr3 | Jim Bridger 3 | MW
DG | brdgr4 | Jim Bridger 4 | MW
DH | brdgrt | Jim Bridger Total | MW
DI | nwtld | Northwest Load | MW
DJ | nwtlss | Northwest Losses | MW
DK | nwti | Northwest Interchange (Export) | MW
DL | nwtg | Northwest Generation | MW
DM | idtld | Idaho Load | MW
DN | idtlss | Idaho Losses | MW
DO | idti | Idaho Interchnage (Export) | MW
DP | idtg | Idaho Generation | MW
DQ | pactld | PACE Load | MW
DR | pactlss | PACE Losses | MW
DS | pacti | PACE Interchange (Export) | MW
DT | pactg | PACE generation | MW
DU | cou2g | Coulee 230 kV connected generation total. | MW
DV | cou5g | Coulee 500 kV connected generation total. | MW
DW | bleeg | Brownlee Total generation | MW
DX | naug | Naughton Total generation | MW
DY | bonzg | Bonanza generation. | MW
DZ | ampsp | Post-event flow on AMPS line | MW
EA | dsbgp | Post-event flow on Big Grassy line | MW
EB | anatangl | Voltage Phase difference Anaconda - Antelope | degrees
EC | jfpsa | Jefferson PST angle (no load) | degrees
ED | jfp | Jefferson PST flow | MW
EE | bbv | Bell Bpa 500 kV voltage | PU
EF | dwv | Dworshak 500 kV voltage | PU
EG | hwv | Hatwai 500 kV voltage | PU
EH | bb1v | Bell 230 kV voltage | PU
EI | bb50q | Bell 500 kV shunt | MVA
EJ | bbs1q | Bell South1 shunt | MVA
EK | bbs2q | Bell South2 shunt | MVA
EL | bbs3q | Bell South3 shunt | MVA
EM | wohnew | West of Hatwai (new definition) | MW
EN | wohold | West of Hatwai (old definition) | MW
EO | mtut_b | Path 18 Pre-event flow | MW
EP | ampsp_b | Pre-event flow on AMPS line. | MW
EQ | dsbgp_b | Pre-event flow on Big Grassy line. | MW
ER | anv_r | post-event voltage/pre-event voltage | PU
ES | an1v_r | post-event voltage/pre-event voltage | PU
ET | pfv_r | post-event voltage/pre-event voltage | PU
EU | pf6rv_r | post-event voltage/pre-event voltage | PU
EV | amv_r | post-event voltage/pre-event voltage | PU
EW | am6v_r | post-event voltage/pre-event voltage | PU
EX | antv_r | post-event voltage/pre-event voltage | PU
EY | dsv_r | post-event voltage/pre-event voltage | PU
EZ | ds6v_r | post-event voltage/pre-event voltage | PU
FA | bggv_r | post-event voltage/pre-event voltage | PU
FB | bgg6v_r | post-event voltage/pre-event voltage | PU
FC | jfrpv_r | post-event voltage/pre-event voltage | PU
FD | jfrsniv_r | post-event voltage/pre-event voltage | PU
FE | ncase | Outage Case Number | NA
FF | nout | Outage Number | NA

## log_amps06hs_pf
root.sav_amps06hs | nojd | coi | celilo12 | celilo34 | bcnw | woh | nwhydro | mtnw | mtut | bvgr1p | bvgr2p | bvjgp | srwsp | crbtp | bvbvp1 | bvbvp2 | wobvp | cs1g | cs2g | cs3g | cs4g | cstot | mcp | wocs | woxo | idnw | mpsl | borahw | brdgrw | pathc | path15 | tot2 | mtse | ytno | ytso | tot4a | tot4b | ytgen | libg | noxg | hhg | cgg | ckld | hhnet | fhnld | corg | mt1 | bgi | thrml | kerr | tfls | krtf | haus | holt | canf | rbow | beag | ryan | coch | morn | madn | mogen | mttld | mttlss | mtti | mttg | cfkapct | hsdxpct | bkpct | pcpct | rrpsa | blpsa | xopsa | hmltv | anv | an1v | pfv | pf6rv | amv | am69v | antv | dsv | ds6v | bggv | bgg6v | jfrpv | jfrsniv | an23q | an16q | ov23q | ws23q | gr50q | hs50q | tt50q | ds69q | pf23q | gran1 | gran2 | anpf | ands | jfrsn | htwll | llimn | bleehcn | lala | bomo | brdgr1 | brdgr2 | brdgr3 | brdgr4 | brdgrt | nwtld | nwtlss | nwti | nwtg | idtld | idtlss | idti | idtg | pactld | pactlss | pacti | pactg | cou2g | cou5g | bleeg | naug | bonzg | ampsp | dsbgp | anatangl | jfpsa | jfp | bbv | dwv | hwv | bb1v | bb50q | bbs1q | bbs2q | bbs3q | wohnew | wohold | mtut_b | ampsp_b | dsbgp_b | anv_r | an1v_r | pfv_r | pf6rv_r | amv_r | am6v_r | antv_r | dsv_r | ds6v_r | bggv_r | bgg6v_r | jfrpv_r | jfrsniv_r | ncase | nout
06hs4apotc.sav | 7445.1 | 3848.7 | 1107.5 | 1896.8 | 2300 | 1405.1 | 1226.7 | 909.8 | 327.2 | 788.9 | 788.9 | 103.7 | 164.2 | 82.2 | 26.2 | 26.8 | 1980.9 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2151.4 | -590.9 | -80.8 | 626.7 | 1952.7 | -626.9 | 842.6 | 349.7 | 7.2 | -130.2 | 413.3 | 419.1 | 26.2 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 117.4 | 1295 | 3158 | 40.7 | 20 | 15.3 | 9 | 6.6 | 6.6 | 0 | 0.98238 | 1.0054 | 0.99885 | 0.9584 | 1.0361 | 0.96032 | 0.9971 | 0.98533 | 0.95167 | 0.93548 | 0.92834 | 0.93477 | 0.94923 | 0.9826 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55.6 | 67.7 | 57.8 | 54.2 | 65.3 | 60.4 | 82.7 | 83.5 | 38.9 | 34 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1126.7 | 4576.1 | 28533.9 | 3273.9 | 228 | 645.4 | 4147.3 | 7635.3 | 295.7 | -1174.4 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 243.4 | 83.8 | 44.518 | 14 | 41.8 | 1.0856 | 1.0755 | 1.074 | 1.0331 | 0 | 0 | 129 | 0 | 1405.1 | 1717.5 | 327.2 | 243.4 | 83.8 | 1.0054 | 0.99885 | 0.9584 | 1.0361 | 0.96032 | 0.9971 | 0.98533 | 0.95167 | 0.93548 | 0.92834 | 0.93477 | 0.94923 | 0.9826 | 0 | 0
06hs4apotc_amps.sav | 7594.7 | 3916.3 | 1107.5 | 1896.8 | 2298.9 | 1589.8 | 1226.7 | 1122.6 | 102.6 | 786.1 | 786.1 | 97.7 | 146.5 | 73.8 | 25.3 | 25.9 | 1941.3 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2140.3 | -704.3 | -154.1 | 519.5 | 1980.7 | -599 | 823 | 329 | 47.4 | -170.1 | 453.3 | 446.5 | -5.6 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 102 | 1323.3 | 3158 | 36.6 | 14.3 | 21.7 | 9.3 | 6.6 | 6.6 | 0 | 0.99288 | 1.0311 | 1.0225 | 0.9584 | 1.0361 | 0.96032 | 0.9971 | 1.0075 | 0.95113 | 0.9349 | 0.91079 | 0.91638 | 0.93557 | 0.97893 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 34.3 | 41.9 | 0 | 65 | 89.2 | 63.2 | 88 | 86.4 | 41.6 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1154.1 | 4548.8 | 28533.9 | 3273.9 | 235.3 | 638.1 | 4147.3 | 7581.2 | 296.5 | -1121.1 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 0 | 102.6 | 59.937 | 14 | 59.8 | 1.0853 | 1.0741 | 1.0726 | 1.0328 | 0 | 0 | 129 | 0 | 1589.8 | 1920.3 | 327.2 | 243.4 | 83.8 | 1.0255 | 1.0236 | 1 | 1 | 1 | 1 | 1.0225 | 0.99943 | 0.99938 | 0.9811 | 0.98033 | 0.98561 | 0.99626 | 1 | 1
06hs4apotc_amps_s.sav | 7593.7 | 3916.3 | 1107.5 | 1896.8 | 2298.9 | 1588.6 | 1226.7 | 1121 | 104.5 | 786 | 786 | 97.6 | 147 | 73.9 | 25.3 | 25.9 | 1941.8 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2140.4 | -703 | -153.1 | 520.8 | 1980.4 | -599.5 | 823.3 | 329.3 | 46.9 | -169.6 | 452.8 | 446.1 | -5.2 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 102 | 1323.3 | 3158 | 36.6 | 14.3 | 21.7 | 9.3 | 6.6 | 6.6 | 0 | 0.9942 | 1.0336 | 1.0257 | 0.9584 | 1.0361 | 0.96032 | 0.9971 | 1.0077 | 0.96705 | 0.97928 | 0.91777 | 0.92369 | 0.94025 | 0.98145 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 34.4 | 41.9 | 0 | 65.3 | 88.4 | 63.2 | 87.9 | 86.4 | 41.6 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1153.8 | 4549 | 28533.9 | 3273.9 | 235.2 | 638.2 | 4147.3 | 7581.2 | 296.4 | -1120.9 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 0 | 104.5 | 59.842 | 14 | 61.8 | 1.0855 | 1.0743 | 1.0727 | 1.0329 | 0 | 0 | 129 | 0 | 1588.6 | 1919 | 327.2 | 243.4 | 83.8 | 1.028 | 1.0268 | 1 | 1 | 1 | 1 | 1.0227 | 1.0162 | 1.0468 | 0.98861 | 0.98815 | 0.99054 | 0.99883 | 2 | 1
06hs4apotc_dsbg.sav | 7495 | 3862.9 | 1107.5 | 1896.8 | 2299.6 | 1467.1 | 1226.7 | 982 | 255.3 | 791.8 | 791.8 | 101.1 | 152.3 | 75.1 | 25.9 | 26.4 | 1964.4 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2147.1 | -638 | -112.5 | 581.2 | 1968.4 | -615.7 | 832 | 338.4 | 24.2 | -147.1 | 430.3 | 432 | 12.6 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.8 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 100 | 1312.3 | 3158 | 39.1 | 17.9 | 17.7 | 9 | 6.6 | 6.6 | 0 | 0.98523 | 1.0108 | 1.0055 | 0.94884 | 1.0492 | 0.94986 | 0.98526 | 0.98031 | 0.99316 | 0.98015 | 0.95517 | 0.96285 | 0.9732 | 0.98466 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 49.9 | 60.8 | 61 | 16.7 | 45.1 | 61.5 | 84.7 | 84.6 | 40 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1135.7 | 4567.1 | 28533.9 | 3273.9 | 230.8 | 642.6 | 4147.3 | 7635.3 | 299.1 | -1177.8 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 255.3 | 0 | 47.484 | 14 | -41.6 | 1.0853 | 1.0749 | 1.0735 | 1.0329 | 0 | 0 | 129 | 0 | 1467.1 | 1786.2 | 327.2 | 243.4 | 83.8 | 1.0053 | 1.0067 | 0.99003 | 1.0126 | 0.98911 | 0.98813 | 0.99491 | 1.0436 | 1.0478 | 1.0289 | 1.03 | 1.0253 | 1.0021 | 3 | 2
06hs4apotc_bloxhcb.sav | 7537.4 | 3860.9 | 1107.5 | 1896.8 | 2299.9 | 1276.6 | 1226.7 | 873.3 | 339.2 | 779.1 | 779.1 | 103.3 | 163.9 | 82.2 | 26.2 | 26.8 | 1960.7 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2145.1 | -497.1 | -234.6 | 683 | 1972.9 | -597.9 | 810.8 | 316.4 | 27.3 | -150.1 | 433.3 | 436.5 | 10.2 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 121.7 | 1290.7 | 3158 | 41.2 | 20.8 | 14.2 | 9.2 | 6.6 | 6.6 | 0 | 0.9796 | 0.9992 | 0.9926 | 0.94074 | 1.0398 | 0.94477 | 0.97949 | 0.97669 | 0.93987 | 0.92274 | 0.91665 | 0.92252 | 0.93996 | 0.97751 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.4 | 69.9 | 60.6 | 57.3 | 73.1 | 62.7 | 109.6 | 0 | 62 | 34.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1165.7 | 4537.2 | 28533.9 | 3273.9 | 212.6 | 660.8 | 4147.3 | 7635.3 | 298 | -1176.6 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 250.8 | 88.4 | 47.415 | 14 | 46.2 | 1.0852 | 1.0745 | 1.0725 | 1.0328 | 0 | 0 | 129 | 0 | 1276.6 | 1682.3 | 327.2 | 243.4 | 83.8 | 0.99378 | 0.99374 | 0.98157 | 1.0036 | 0.98381 | 0.98234 | 0.99123 | 0.9876 | 0.98638 | 0.98741 | 0.98689 | 0.99023 | 0.99482 | 4 | 3
06hs4apotc_bloxhcb_s.sav | 7536.3 | 3861 | 1107.5 | 1896.8 | 2299.9 | 1275.3 | 1226.7 | 871.6 | 341.5 | 779.1 | 779.1 | 103.3 | 164.4 | 82.4 | 26.2 | 26.8 | 1961.2 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2145.3 | -495.7 | -233.4 | 684.5 | 1972.5 | -598.4 | 811.2 | 316.8 | 26.8 | -149.6 | 432.8 | 436.1 | 10.7 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 121.7 | 1290.7 | 3158 | 41.2 | 20.7 | 14.3 | 9.2 | 6.6 | 6.6 | 0 | 0.98095 | 1.0017 | 0.99587 | 0.94296 | 1.0424 | 0.94621 | 0.98112 | 0.97751 | 0.95582 | 0.96685 | 0.92372 | 0.92993 | 0.94477 | 0.98013 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 57.4 | 69.9 | 60.5 | 57.8 | 71.9 | 62.7 | 109.5 | 0 | 61.9 | 34.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1165.4 | 4537.5 | 28533.9 | 3273.9 | 212.5 | 660.9 | 4147.3 | 7635.3 | 297.8 | -1176.4 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 251.3 | 90.1 | 47.312 | 14 | 47.9 | 1.0854 | 1.0747 | 1.0726 | 1.0329 | 0 | 0 | 129 | 0 | 1275.3 | 1680.7 | 327.2 | 243.4 | 83.8 | 0.9963 | 0.99702 | 0.98389 | 1.006 | 0.98531 | 0.98397 | 0.99206 | 1.0044 | 1.0335 | 0.99502 | 0.99482 | 0.9953 | 0.99749 | 5 | 3
06hs4apotc_blhcoxll.sav | 7802.9 | 3882.5 | 1107.5 | 1896.8 | 2299.1 | 1625.1 | 1226.7 | 816.2 | 355.7 | 763.5 | 763.5 | 102.6 | 162.8 | 81.9 | 26.1 | 26.7 | 1927.2 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2134.8 | -377.4 | -427.2 | 756.9 | 2000.4 | -560.1 | 771.7 | 275.7 | 60.7 | -183.2 | 466.4 | 462 | -15.8 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.1 | 1283.3 | 3158 | 41.7 | 21.9 | 12.5 | 8.7 | 6.6 | 6.6 | 0 | 0.97609 | 0.98995 | 0.98315 | 0.91122 | 1.0057 | 0.91821 | 0.94929 | 0.9617 | 0.91988 | 0.90109 | 0.89638 | 0.90127 | 0.92393 | 0.96853 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.3 | 73.4 | 64.8 | 62.2 | 85.6 | 22.5 | 0 | 0 | 88.7 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1198.8 | 4504.2 | 28533.9 | 3273.9 | 196 | 677.4 | 4147.3 | 7635.3 | 303.1 | -1181.8 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 260.6 | 95 | 52.13 | 14 | 52.4 | 1.0863 | 1.0794 | 1.0786 | 1.0341 | 0 | 0 | 129 | 0 | 1625.1 | 1625.1 | 327.2 | 243.4 | 83.8 | 0.98458 | 0.98428 | 0.95077 | 0.97068 | 0.95615 | 0.95205 | 0.97602 | 0.9666 | 0.96324 | 0.96557 | 0.96416 | 0.97335 | 0.98568 | 6 | 4
06hs4apotc_blhcoxll_s.sav | 7801.4 | 3882.7 | 1107.5 | 1896.8 | 2299.1 | 1623.4 | 1226.7 | 814.2 | 358.2 | 763.5 | 763.5 | 102.5 | 163.4 | 82.1 | 26.1 | 26.7 | 1927.8 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2135 | -375.8 | -425.8 | 758.6 | 2000 | -560.7 | 772.2 | 276.3 | 60.1 | -182.6 | 465.8 | 461.5 | -15.3 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.1 | 1283.3 | 3158 | 41.7 | 21.8 | 12.5 | 8.7 | 6.6 | 6.6 | 0 | 0.97753 | 0.99263 | 0.9866 | 0.91363 | 1.0085 | 0.91978 | 0.95107 | 0.96258 | 0.93599 | 0.94488 | 0.90351 | 0.90874 | 0.92875 | 0.97116 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.2 | 73.3 | 64.8 | 62.6 | 84.5 | 22.5 | 0 | 0 | 88.6 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1198.4 | 4504.6 | 28533.9 | 3273.9 | 195.9 | 677.5 | 4147.3 | 7635.3 | 302.9 | -1181.5 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 261.3 | 96.9 | 52.009 | 14 | 54.3 | 1.0865 | 1.0796 | 1.0787 | 1.0342 | 0 | 0 | 129 | 0 | 1623.4 | 1623.4 | 327.2 | 243.4 | 83.8 | 0.98725 | 0.98774 | 0.95329 | 0.97336 | 0.95778 | 0.95384 | 0.97691 | 0.98352 | 1.01 | 0.97325 | 0.97215 | 0.97842 | 0.98836 | 7 | 4
06hs4apotc_mpsl.sav | 7416.6 | 3878.3 | 1107.5 | 1896.8 | 2300 | 1379.9 | 1226.7 | 895.6 | 332.1 | 785.2 | 785.2 | 103.6 | 164.2 | 82.3 | 26.2 | 26.8 | 1973.4 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.1 | -543.8 | 0 | 660.7 | 1963.2 | -603.9 | 815.3 | 321.2 | 14.6 | -137.5 | 420.7 | 427.8 | 20.3 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119.3 | 1293.1 | 3158 | 40.9 | 20.3 | 14.9 | 9.1 | 6.6 | 6.6 | 0 | 0.98107 | 1.0025 | 0.99587 | 0.94927 | 1.0496 | 0.95104 | 0.9866 | 0.97861 | 0.94593 | 0.92929 | 0.92176 | 0.92788 | 0.94357 | 0.97864 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56.4 | 68.7 | 59 | 55.5 | 68.7 | 61.9 | 86.1 | 86 | 41.8 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1123.8 | 4579.1 | 28533.9 | 3273.9 | 236.1 | 637.3 | 4147.3 | 7635.3 | 296.6 | -1175.3 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 246.2 | 85.9 | 45.819 | 14 | 43.8 | 1.0855 | 1.0752 | 1.0737 | 1.033 | 0 | 0 | 129 | 0 | 1379.9 | 1704 | 327.2 | 243.4 | 83.8 | 0.99703 | 0.99702 | 0.99047 | 1.0131 | 0.99034 | 0.98947 | 0.99318 | 0.99397 | 0.99338 | 0.99291 | 0.99263 | 0.99404 | 0.99597 | 8 | 5
06hs4apotc_mpsl_s.sav | 7415.9 | 3878 | 1107.5 | 1896.8 | 2300 | 1378.9 | 1226.7 | 894.2 | 334.2 | 785.2 | 785.2 | 103.5 | 164.7 | 82.4 | 26.2 | 26.8 | 1974 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.3 | -543 | 0 | 661.7 | 1962.7 | -604.6 | 816.1 | 322 | 14 | -136.9 | 420.1 | 427.4 | 20.8 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119.3 | 1293.1 | 3158 | 40.9 | 20.3 | 14.9 | 9.1 | 6.6 | 6.6 | 0 | 0.98241 | 1.005 | 0.99909 | 0.95152 | 1.0522 | 0.95253 | 0.98828 | 0.97946 | 0.96184 | 0.97352 | 0.92886 | 0.93531 | 0.94841 | 0.98126 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56.4 | 68.6 | 58.9 | 56.1 | 67.4 | 61.8 | 86 | 86 | 41.7 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1123.5 | 4579.3 | 28533.9 | 3273.9 | 235.9 | 637.5 | 4147.3 | 7635.3 | 296.4 | -1175.1 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 246.7 | 87.5 | 45.706 | 14 | 45.4 | 1.0857 | 1.0754 | 1.0738 | 1.0331 | 0 | 0 | 129 | 0 | 1378.9 | 1702.8 | 327.2 | 243.4 | 83.8 | 0.99951 | 1.0002 | 0.99282 | 1.0156 | 0.99189 | 0.99115 | 0.99404 | 1.0107 | 1.0407 | 1.0006 | 1.0006 | 0.99914 | 0.99864 | 9 | 5
06hs4apotc_angr1.sav | 7457.5 | 3845.9 | 1107.5 | 1896.8 | 2299.8 | 1420.9 | 1226.7 | 934.6 | 299.1 | 772.3 | 772.3 | 107 | 182.3 | 90.8 | 26.8 | 27.4 | 1978.7 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.7 | -609.5 | -94 | 608.5 | 1956.1 | -622.3 | 836.9 | 343.6 | 8.4 | -131.3 | 414.5 | 421.1 | 25.3 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119.7 | 1292.9 | 3158 | 43.4 | 22.6 | 12.2 | 9.3 | 6.6 | 6.6 | 0 | 0.97209 | 0.97551 | 0.96959 | 0.95051 | 1.0272 | 0.96195 | 0.99895 | 0.98709 | 0.93208 | 0.91431 | 0.92583 | 0.93214 | 0.94853 | 0.98162 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 116.5 | 54.5 | 49.7 | 59.2 | 60.8 | 83.4 | 83.9 | 39.3 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1134.9 | 4567.9 | 28533.9 | 3273.9 | 228.6 | 644.8 | 4147.3 | 7635.3 | 294.8 | -1173.4 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 224.2 | 74.9 | 41.756 | 14 | 33.1 | 1.0852 | 1.075 | 1.0737 | 1.0329 | 0 | 0 | 129 | 0 | 1420.9 | 1735.5 | 327.2 | 243.4 | 83.8 | 0.97022 | 0.97071 | 0.99177 | 0.99142 | 1.0017 | 1.0019 | 1.0018 | 0.97942 | 0.97737 | 0.9973 | 0.99719 | 0.99926 | 0.999 | 10 | 6
06hs4apotc_angr2.sav | 7457 | 3848.7 | 1107.5 | 1896.8 | 2299.8 | 1420.2 | 1226.7 | 929.4 | 304.9 | 774.1 | 774.1 | 106.5 | 180.5 | 89.8 | 26.7 | 27.3 | 1979 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.9 | -605.7 | -91.2 | 612.3 | 1955.4 | -623.4 | 838.3 | 345.1 | 8.3 | -131.3 | 414.4 | 420.7 | 25.4 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119 | 1293.5 | 3158 | 43 | 22.2 | 12.7 | 9.3 | 6.6 | 6.6 | 0 | 0.97479 | 0.98465 | 0.97824 | 0.95526 | 1.0326 | 0.96376 | 1.001 | 0.98784 | 0.93875 | 0.92152 | 0.92785 | 0.93425 | 0.94977 | 0.98245 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 89.9 | 0 | 55 | 50.3 | 59.8 | 60.7 | 83.3 | 83.8 | 39.2 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1130.8 | 4572 | 28533.9 | 3273.9 | 228.5 | 644.9 | 4147.3 | 7635.3 | 294.9 | -1173.6 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 228.2 | 76.7 | 42.077 | 14 | 34.9 | 1.0851 | 1.075 | 1.0737 | 1.0329 | 0 | 0 | 129 | 0 | 1420.2 | 1734.4 | 327.2 | 243.4 | 83.8 | 0.97931 | 0.97937 | 0.99672 | 0.99658 | 1.0036 | 1.0039 | 1.0025 | 0.98642 | 0.98508 | 0.99947 | 0.99944 | 1.0006 | 0.99985 | 11 | 7
06hs4apotc_angr12.sav | 7520.9 | 3819.7 | 1107.5 | 1896.8 | 2299.5 | 1502.3 | 1226.7 | 1028.3 | 138.4 | 712.7 | 712.7 | 122.4 | 236.2 | 116.9 | 29.5 | 30.1 | 1960.5 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2142 | -717.5 | -171.8 | 502.4 | 1976.6 | -593.5 | 802.8 | 308 | 19.9 | -142.3 | 425.4 | 434.2 | 17.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114.3 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 175.9 | 1237.6 | 3158 | 55.3 | 36.4 | 3.9 | 12.8 | 6.6 | 6.6 | 0 | 0.88384 | 0.78018 | 0.76916 | 0.86565 | 0.93132 | 0.93428 | 0.96757 | 0.97506 | 0.76806 | 0.73387 | 0.87658 | 0.88048 | 0.9179 | 0.96008 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 39.6 | 28.9 | 62.7 | 62.6 | 87 | 86.1 | 41.6 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1142.8 | 4560.1 | 28533.9 | 3273.9 | 233.7 | 639.7 | 4147.3 | 7635.3 | 295 | -1173.7 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 114.5 | 23.9 | 26.719 | 14 | -18 | 1.0826 | 1.0721 | 1.0718 | 1.0314 | 0 | 0 | 129 | 0 | 1502.3 | 1829.2 | 327.2 | 243.4 | 83.8 | 0.77595 | 0.77005 | 0.90322 | 0.89887 | 0.97288 | 0.97038 | 0.98958 | 0.80707 | 0.78448 | 0.94425 | 0.94192 | 0.96699 | 0.97708 | 12 | 8
06hs4apotc_grgr.sav | 7485.6 | 3835.1 | 1107.5 | 1896.8 | 2300 | 1458.5 | 1226.7 | 975.5 | 226.9 | 690.6 | 690.6 | 166.4 | 233.9 | 114.3 | 35.5 | 36.2 | 1967.3 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2142.6 | -655.6 | -127.2 | 563.2 | 1966.6 | -610 | 822.8 | 328.9 | 16.2 | -138.8 | 421.9 | 428.3 | 19.7 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 115.2 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 143.4 | 1269.5 | 3158 | 62.4 | 56.4 | 13.9 | 17 | 6.6 | 6.6 | 0 | 0.91662 | 0.92623 | 0.91709 | 0.94936 | 1.0259 | 0.97493 | 1.0136 | 0.99518 | 0.89604 | 0.87518 | 0.9249 | 0.93116 | 0.95043 | 0.98083 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 28.7 | 35 | 45.3 | 35.9 | 44.8 | 61.5 | 84.9 | 84.8 | 40.3 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1139.5 | 4563.7 | 28533.9 | 3273.9 | 230.4 | 643 | 4147.3 | 7635.3 | 293.6 | -1172.2 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 175.8 | 51 | 33.133 | 14 | 9.5 | 1.0837 | 1.0732 | 1.0726 | 1.0325 | 0 | 0 | 129 | 0 | 1458.5 | 1778.3 | 327.2 | 243.4 | 83.8 | 0.92121 | 0.91815 | 0.99057 | 0.99016 | 1.0152 | 1.0166 | 1.01 | 0.94154 | 0.93554 | 0.99629 | 0.99614 | 1.0013 | 0.9982 | 13 | 9
06hs4apotc_anpf.sav | 7585.4 | 3868.2 | 1107.5 | 1896.8 | 2299 | 1580.8 | 1226.7 | 1116.1 | 91 | 784.3 | 784.3 | 97.6 | 146.4 | 73.8 | 25.3 | 25.9 | 1937.6 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2139.1 | -745.9 | -187.2 | 477.2 | 1990.4 | -585.4 | 805.8 | 311 | 51.1 | -173.7 | 457 | 452.4 | -8.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 103.2 | 1309 | 3158 | 36.7 | 14.4 | 21.5 | 9.3 | 6.6 | 6.6 | 0 | 0.99271 | 1.0307 | 1.022 | 1.1165 | 1.0162 | 1.0821 | 1.134 | 1.0424 | 0.94901 | 0.93261 | 0.91031 | 0.91588 | 0.93635 | 0.98166 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 34.6 | 42.1 | 0 | 66.1 | 92.3 | 63.6 | 88.8 | 87 | 42.4 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1152.5 | 4550.4 | 28533.9 | 3273.9 | 237.6 | 635.8 | 4147.3 | 7635.3 | 297.9 | -1176.6 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | -13.3 | 104.3 | 63.198 | 14 | 61.4 | 1.0853 | 1.0741 | 1.0725 | 1.0328 | 0 | 0 | 129 | 0 | 1580.8 | 1914.3 | 327.2 | 243.4 | 83.8 | 1.0251 | 1.0232 | 1.165 | 0.98074 | 1.1268 | 1.1373 | 1.0579 | 0.99721 | 0.99693 | 0.98058 | 0.97979 | 0.98643 | 0.99904 | 14 | 10
06hs4apotc_antbdy.sav | 7462.8 | 3850.4 | 1107.5 | 1896.8 | 2299.8 | 1427.3 | 1226.7 | 935.7 | 301.6 | 788.8 | 788.8 | 102.9 | 162 | 81.1 | 26.1 | 26.7 | 1976.5 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2150.2 | -611.4 | -94.9 | 607.2 | 1953.2 | -619.5 | 838.6 | 345.4 | 11.7 | -134.6 | 417.8 | 421.7 | 22.6 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2531 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 112.6 | 1299.8 | 3158 | 40.2 | 19.2 | 16.1 | 9 | 6.6 | 6.6 | 0 | 0.98483 | 1.0112 | 1.0042 | 0.97064 | 1.0499 | 0.95474 | 0.99078 | 0.96057 | 0.95405 | 0.93804 | 0.92489 | 0.93115 | 0.94491 | 0.97766 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 52.9 | 64.4 | 50.8 | 54.7 | 65.6 | 60.9 | 83.5 | 84 | 39.3 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1129.6 | 4573.2 | 28533.9 | 3273.9 | 229 | 644.4 | 4147.3 | 7635.3 | 299.5 | -1178.2 | 6760.7 | 900 | 3069.2 | 647.9 | 609.5 | 484 | 216.6 | 85 | 38.764 | 14 | 42.9 | 1.0857 | 1.0755 | 1.074 | 1.0332 | 0 | 0 | 129 | 0 | 1427.3 | 1742.4 | 327.2 | 243.4 | 83.8 | 1.0058 | 1.0054 | 1.0128 | 1.0133 | 0.99419 | 0.99366 | 0.97487 | 1.0025 | 1.0027 | 0.99628 | 0.99613 | 0.99545 | 0.99497 | 15 | 11
06hs4apotc_brbo_brkp.sav | 7641.2 | 3536.1 | 1107.5 | 1896.8 | 2476.6 | 1344.6 | 1247.2 | 839.8 | 369.2 | 779.4 | 779.4 | 104.9 | 167.7 | 85.2 | 26.3 | 26.9 | 1969.8 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2148.8 | -1262.7 | -592.9 | -89.2 | 772.1 | -288.2 | 993.9 | 148.9 | 19.4 | -142.3 | 425.4 | 459.5 | 16.1 | 288 | 590.5 | 268.4 | 193.4 | 194.9 | 78 | 115.4 | 111.1 | 151 | 39 | 59 | 2531 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 145.2 | 1278.6 | 3169.3 | 43.4 | 22.8 | 13 | 10 | 6.6 | 6.6 | 0 | 0.95804 | 0.9626 | 0.95534 | 0.85662 | 0.94248 | 0.87588 | 0.90088 | 0.94231 | 0.87771 | 0.85519 | 0.87063 | 0.87423 | 0.90896 | 0.96826 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 63.7 | 77.5 | 71 | 69.3 | 106.3 | 68.3 | 100.4 | 97.8 | 53.2 | 38.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1206.9 | 4846.4 | 28883.9 | 3292.5 | 202.2 | -439.1 | 3055.5 | 7635.3 | 320.4 | -1173.8 | 6786 | 916.2 | 3125 | 659.6 | 611.4 | 490 | 267.6 | 101.6 | 59.567 | 14 | 58.1 | 1.077 | 1.0658 | 1.0643 | 1.0248 | 0 | 0 | 129 | 0 | 1344.6 | 1714.8 | 327.2 | 243.4 | 83.8 | 0.95738 | 0.95644 | 0.8938 | 0.90964 | 0.91207 | 0.9035 | 0.95634 | 0.92228 | 0.91417 | 0.93783 | 0.93524 | 0.95758 | 0.98541 | 16 | 12
06hs4apotc_brbo_brkp_s.sav | 7633.7 | 3536.9 | 1107.5 | 1896.8 | 2476.4 | 1336.4 | 1247.2 | 829.5 | 382.8 | 779.9 | 779.9 | 104.7 | 169.3 | 85.7 | 26.3 | 26.9 | 1972.7 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.6 | -1253.2 | -586.2 | -80.1 | 770.9 | -291.9 | 996 | 151.5 | 16.5 | -139.4 | 422.6 | 457.6 | 18.4 | 288 | 590.5 | 268.4 | 193.4 | 194.9 | 78 | 115.4 | 111.1 | 151 | 39 | 59 | 2531 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 144.7 | 1279.1 | 3169.3 | 43.4 | 22.7 | 12.9 | 10 | 6.6 | 6.6 | 0 | 0.96312 | 0.97223 | 0.96539 | 0.89139 | 0.98278 | 0.89718 | 0.92529 | 0.95314 | 0.9007 | 0.90563 | 0.88246 | 0.88665 | 0.91754 | 0.97376 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 63.8 | 77.7 | 71.3 | 69.2 | 104.5 | 68.1 | 100 | 97.5 | 52.9 | 38.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1204.1 | 4848 | 28882.6 | 3292.5 | 201.1 | -438.1 | 3055.5 | 7635.3 | 319.2 | -1172.5 | 6786 | 916.2 | 3124.9 | 659.6 | 611.4 | 490 | 278.4 | 104.4 | 58.722 | 14 | 61.1 | 1.0782 | 1.067 | 1.0653 | 1.0257 | 0 | 0 | 129 | 0 | 1336.4 | 1705.7 | 327.2 | 243.4 | 83.8 | 0.96696 | 0.9665 | 0.93008 | 0.94854 | 0.93425 | 0.92798 | 0.96733 | 0.94644 | 0.96809 | 0.95058 | 0.94852 | 0.96662 | 0.991 | 17 | 12
06hs4apotc_brgo_brkp.sav | 7638.7 | 3526.3 | 1107.5 | 1896.8 | 2482.5 | 1330 | 1248.3 | 823.8 | 373.4 | 778.5 | 778.5 | 106.3 | 168.6 | 86.3 | 26.5 | 27.1 | 1971.8 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.6 | 2149.4 | -1270.8 | -599.7 | -85.5 | 759 | -277.5 | 1001.2 | 145.6 | 17.2 | -140 | 423.2 | 457.5 | 18 | 288 | 591 | 268.6 | 193.6 | 195.1 | 78 | 115.6 | 110.9 | 151 | 39 | 59 | 2531 | 142.7 | 67.2 | 209.9 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 159.8 | 1264.6 | 3169.8 | 44 | 23.8 | 12.1 | 10.2 | 6.6 | 6.6 | 0 | 0.94815 | 0.94502 | 0.93609 | 0.82344 | 0.90391 | 0.84832 | 0.86913 | 0.9266 | 0.82853 | 0.80119 | 0.82209 | 0.82312 | 0.87255 | 0.94868 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 66.6 | 81.1 | 73.5 | 78.5 | 130.4 | 68.4 | 100.5 | 98 | 53.5 | 38.7 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1209.7 | 4855 | 28895.2 | 3292.5 | 212.2 | -448.3 | 3056.4 | 7635.3 | 328.7 | -1181.5 | 6786.5 | 917.1 | 3126.6 | 660.2 | 611.5 | 490 | 266 | 107.4 | 63.408 | 14 | 62.8 | 1.0752 | 1.0641 | 1.0631 | 1.0234 | 0 | 0 | 129 | 0 | 1330 | 1700.3 | 327.2 | 243.4 | 83.8 | 0.9399 | 0.93717 | 0.85918 | 0.87242 | 0.88337 | 0.87166 | 0.9404 | 0.87061 | 0.85645 | 0.88555 | 0.88056 | 0.91922 | 0.96548 | 18 | 13
06hs4apotc_brgo_brkp_s.sav | 7629.9 | 3525.7 | 1107.5 | 1896.8 | 2480.6 | 1320.9 | 1248.1 | 812.7 | 388.1 | 778.9 | 778.9 | 106.1 | 170.5 | 87 | 26.5 | 27.1 | 1974.8 | 330 | 330 | 807 | 815 | 2282 | 141 | 2120.5 | 2150.3 | -1260.5 | -592.4 | -75.5 | 758.3 | -282 | 1001.4 | 148.6 | 14.2 | -137.1 | 420.2 | 455.6 | 20.3 | 288 | 591 | 268.4 | 193.6 | 195.1 | 78 | 115.6 | 110.9 | 151 | 39 | 59 | 2531 | 142.6 | 67.2 | 209.8 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 159 | 1265.2 | 3169.7 | 44.1 | 23.7 | 12 | 10.1 | 6.6 | 6.6 | 0 | 0.95341 | 0.95488 | 0.94641 | 0.85827 | 0.9444 | 0.87003 | 0.89416 | 0.93785 | 0.8521 | 0.85119 | 0.83462 | 0.83633 | 0.88165 | 0.95473 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 66.7 | 81.2 | 73.8 | 78 | 128.7 | 68.1 | 100.1 | 97.7 | 53.2 | 38.7 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1206.2 | 4856.8 | 28893.5 | 3292.5 | 210.9 | -447.1 | 3056.1 | 7635.3 | 327.2 | -1179.9 | 6786.5 | 917.1 | 3126.1 | 660.1 | 611.5 | 490 | 277.2 | 110.9 | 62.447 | 14 | 66.4 | 1.0764 | 1.0655 | 1.0642 | 1.0244 | 0 | 0 | 129 | 0 | 1320.9 | 1690 | 327.2 | 243.4 | 83.8 | 0.9497 | 0.9475 | 0.89552 | 0.9115 | 0.90598 | 0.89676 | 0.95181 | 0.89537 | 0.9099 | 0.89905 | 0.89469 | 0.9288 | 0.97164 | 19 | 13
p18otc330.sav | 7444.9 | 3846 | 1107.5 | 1896.8 | 2300 | 1403.8 | 1226.7 | 908.1 | 329.6 | 789.4 | 789.4 | 103.9 | 164.7 | 82.5 | 26.3 | 26.8 | 1983 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2153.3 | -589 | -79.7 | 628.1 | 1952.2 | -627.2 | 843.1 | 350.1 | 6.8 | -129.7 | 412.9 | 418.8 | 26.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 118.9 | 1295.2 | 3159.8 | 40.8 | 20.1 | 15.2 | 9.1 | 6.6 | 6.6 | 0 | 0.98196 | 1.0047 | 0.99789 | 0.95823 | 1.0359 | 0.96031 | 0.9971 | 0.98523 | 0.94737 | 0.93084 | 0.92337 | 0.92956 | 0.9454 | 0.98094 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55.9 | 68.1 | 57.7 | 55.9 | 69.7 | 60.4 | 82.7 | 83.4 | 38.8 | 34 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1127.4 | 4576.3 | 28534.7 | 3273.9 | 228 | 646 | 4147.9 | 7635.3 | 295.8 | -1174.3 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 242.8 | 86.8 | 44.423 | 12.2 | 44.6 | 1.0855 | 1.0755 | 1.074 | 1.0331 | 0 | 0 | 129 | 0 | 1403.8 | 1715.8 | 329.6 | 242.8 | 86.8 | 1.0047 | 0.99789 | 0.95823 | 1.0359 | 0.96031 | 0.9971 | 0.98523 | 0.94737 | 0.93084 | 0.92337 | 0.92956 | 0.9454 | 0.98094 | 0 | 0
p18otc330_amps.sav | 7594.3 | 3913.3 | 1107.5 | 1896.8 | 2298.9 | 1588.2 | 1226.7 | 1120.6 | 105 | 786.6 | 786.6 | 97.9 | 147 | 74.1 | 25.4 | 25.9 | 1943.5 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2142.1 | -702.4 | -153 | 520.8 | 1980.3 | -599.3 | 823.4 | 329.4 | 47 | -169.6 | 452.9 | 446.2 | -5.3 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.8 | 1323.3 | 3159.8 | 36.7 | 14.4 | 21.5 | 9.3 | 6.6 | 6.6 | 0 | 0.99234 | 1.03 | 1.0212 | 0.95823 | 1.0359 | 0.96031 | 0.9971 | 1.0072 | 0.94582 | 0.92916 | 0.90461 | 0.9099 | 0.93085 | 0.97673 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 34.6 | 42.2 | 0 | 66.6 | 93.6 | 63.2 | 87.9 | 86.3 | 41.6 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1154.7 | 4549.1 | 28534.7 | 3273.9 | 235.2 | 638.8 | 4147.9 | 7581.2 | 296.8 | -1121.2 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 0 | 105 | 59.822 | 12.2 | 62 | 1.0852 | 1.0741 | 1.0726 | 1.0328 | 0 | 0 | 129 | 0 | 1588.2 | 1918.4 | 329.6 | 242.8 | 86.8 | 1.0252 | 1.0233 | 1 | 1 | 1 | 1 | 1.0223 | 0.99836 | 0.9982 | 0.97968 | 0.97885 | 0.98461 | 0.99571 | 1 | 1
p18otc330_amps_s.sav | 7593.2 | 3913.4 | 1107.5 | 1896.8 | 2298.9 | 1586.9 | 1226.7 | 1119 | 107 | 786.6 | 786.6 | 97.8 | 147.5 | 74.3 | 25.4 | 25.9 | 1944 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2142.3 | -701 | -152.1 | 522.2 | 1979.9 | -599.7 | 823.7 | 329.7 | 46.4 | -169.1 | 452.4 | 445.8 | -4.9 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.8 | 1323.2 | 3159.8 | 36.7 | 14.4 | 21.6 | 9.3 | 6.6 | 6.6 | 0 | 0.99366 | 1.0325 | 1.0244 | 0.95823 | 1.0359 | 0.96031 | 0.9971 | 1.0074 | 0.96168 | 0.97334 | 0.91155 | 0.91718 | 0.93551 | 0.97924 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 34.7 | 42.3 | 0 | 66.9 | 92.8 | 63.1 | 87.8 | 86.3 | 41.5 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1154.4 | 4549.3 | 28534.7 | 3273.9 | 235.1 | 638.9 | 4147.9 | 7581.2 | 296.6 | -1121 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 0 | 107 | 59.725 | 12.2 | 64.1 | 1.0854 | 1.0742 | 1.0727 | 1.0329 | 0 | 0 | 129 | 0 | 1586.9 | 1916.9 | 329.6 | 242.8 | 86.8 | 1.0277 | 1.0265 | 1 | 1 | 1 | 1 | 1.0225 | 1.0151 | 1.0457 | 0.9872 | 0.98668 | 0.98954 | 0.99827 | 2 | 1
p18otc330_dsbg.sav | 7496.9 | 3861.5 | 1107.5 | 1896.8 | 2299.5 | 1468.4 | 1226.7 | 983.5 | 255.3 | 792.5 | 792.5 | 101.2 | 152.3 | 75.1 | 25.9 | 26.4 | 1965.9 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2148.8 | -637.5 | -112.3 | 581.2 | 1968.5 | -615.7 | 832.2 | 338.7 | 24.4 | -147.3 | 430.5 | 432.1 | 12.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.8 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 100.1 | 1314 | 3159.8 | 39 | 17.9 | 17.7 | 9 | 6.6 | 6.6 | 0 | 0.98519 | 1.0107 | 1.0055 | 0.94874 | 1.0491 | 0.94978 | 0.98517 | 0.98027 | 0.99309 | 0.98007 | 0.95517 | 0.96285 | 0.9732 | 0.98466 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 49.9 | 60.8 | 61 | 16.7 | 45.1 | 61.5 | 84.7 | 84.6 | 39.9 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1136.8 | 4566.9 | 28534.7 | 3273.9 | 230.8 | 643.2 | 4147.9 | 7635.3 | 299.2 | -1177.7 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 255.3 | 0 | 47.496 | 12.2 | -41.6 | 1.0853 | 1.0748 | 1.0734 | 1.0329 | 0 | 0 | 129 | 0 | 1468.4 | 1787.5 | 329.6 | 242.8 | 86.8 | 1.006 | 1.0076 | 0.9901 | 1.0127 | 0.98903 | 0.98803 | 0.99497 | 1.0483 | 1.0529 | 1.0344 | 1.0358 | 1.0294 | 1.0038 | 3 | 2
p18otc330_bloxhcb.sav | 7537.2 | 3858.1 | 1107.5 | 1896.8 | 2299.9 | 1275.5 | 1226.7 | 871.8 | 341.3 | 779.7 | 779.7 | 103.5 | 164.3 | 82.5 | 26.2 | 26.8 | 1962.8 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2147 | -495.5 | -233.5 | 684.2 | 1972.5 | -598.2 | 811.2 | 316.8 | 26.9 | -149.7 | 432.9 | 436.1 | 10.6 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.3 | 1290.9 | 3159.8 | 41.3 | 20.8 | 14.2 | 9.2 | 6.6 | 6.6 | 0 | 0.9791 | 0.99828 | 0.99146 | 0.94048 | 1.0395 | 0.94472 | 0.97943 | 0.97656 | 0.93506 | 0.91753 | 0.91123 | 0.91685 | 0.93581 | 0.97566 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.7 | 70.3 | 60.5 | 58.9 | 77.5 | 62.7 | 109.4 | 0 | 61.9 | 34.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1166.4 | 4537.4 | 28534.7 | 3273.9 | 212.6 | 661.4 | 4147.9 | 7635.3 | 298.2 | -1176.6 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 250.1 | 91.2 | 47.324 | 12.2 | 48.8 | 1.0851 | 1.0745 | 1.0725 | 1.0327 | 0 | 0 | 129 | 0 | 1275.5 | 1680.7 | 329.6 | 242.8 | 86.8 | 0.99364 | 0.99356 | 0.98148 | 1.0035 | 0.98377 | 0.98228 | 0.9912 | 0.98701 | 0.9857 | 0.98685 | 0.98633 | 0.98986 | 0.99462 | 4 | 3
p18otc330_bloxhcb_s.sav | 7536 | 3858.3 | 1107.5 | 1896.8 | 2299.9 | 1274.1 | 1226.7 | 870 | 343.7 | 779.6 | 779.6 | 103.5 | 164.9 | 82.7 | 26.2 | 26.8 | 1963.3 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2147.1 | -494 | -232.3 | 685.7 | 1972.1 | -598.7 | 811.6 | 317.3 | 26.4 | -149.2 | 432.4 | 435.7 | 11 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.3 | 1290.8 | 3159.8 | 41.3 | 20.8 | 14.2 | 9.2 | 6.6 | 6.6 | 0 | 0.98049 | 1.0009 | 0.99482 | 0.94276 | 1.0421 | 0.9462 | 0.98111 | 0.97741 | 0.95114 | 0.96167 | 0.91836 | 0.92431 | 0.94065 | 0.97829 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 57.7 | 70.2 | 60.4 | 59.4 | 76.4 | 62.7 | 109.4 | 0 | 61.8 | 34.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1166.1 | 4537.7 | 28534.7 | 3273.9 | 212.5 | 661.5 | 4147.9 | 7635.3 | 297.9 | -1176.4 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 250.7 | 92.9 | 47.218 | 12.2 | 50.6 | 1.0853 | 1.0747 | 1.0726 | 1.0329 | 0 | 0 | 129 | 0 | 1274.1 | 1679.1 | 329.6 | 242.8 | 86.8 | 0.99623 | 0.99692 | 0.98386 | 1.006 | 0.98531 | 0.98396 | 0.99206 | 1.004 | 1.0331 | 0.99457 | 0.99435 | 0.99498 | 0.9973 | 5 | 3
p18otc330_blhcoxll.sav | 7802.6 | 3879.7 | 1107.5 | 1896.8 | 2299.1 | 1623.9 | 1226.7 | 814.9 | 357.3 | 764.1 | 764.1 | 102.8 | 163.2 | 82.2 | 26.2 | 26.7 | 1929.3 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2136.7 | -376.1 | -426.2 | 757.7 | 2000 | -560.3 | 772.1 | 276.1 | 60.3 | -182.8 | 466 | 461.7 | -15.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.8 | 1283.4 | 3159.8 | 41.8 | 22 | 12.4 | 8.8 | 6.6 | 6.6 | 0 | 0.97548 | 0.98883 | 0.98178 | 0.91084 | 1.0053 | 0.91811 | 0.94918 | 0.96155 | 0.91442 | 0.89516 | 0.89034 | 0.89493 | 0.91936 | 0.96641 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.5 | 73.7 | 64.7 | 63.8 | 89.9 | 22.5 | 0 | 0 | 88.6 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.5 | 4504.4 | 28534.7 | 3273.9 | 196 | 678.1 | 4147.9 | 7635.3 | 303.4 | -1181.8 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 260 | 97.3 | 52.045 | 12.2 | 54.5 | 1.0862 | 1.0793 | 1.0785 | 1.034 | 0 | 0 | 129 | 0 | 1623.9 | 1623.9 | 329.6 | 242.8 | 86.8 | 0.98423 | 0.98386 | 0.95054 | 0.97044 | 0.95606 | 0.95194 | 0.97596 | 0.96522 | 0.96167 | 0.96423 | 0.96275 | 0.97246 | 0.98519 | 6 | 4
p18otc330_blhcoxll_s.sav | 7801.1 | 3879.8 | 1107.5 | 1896.8 | 2299.1 | 1622.1 | 1226.7 | 812.9 | 360 | 764 | 764 | 102.7 | 163.8 | 82.4 | 26.1 | 26.7 | 1929.9 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2136.8 | -374.5 | -424.8 | 759.4 | 1999.6 | -560.9 | 772.6 | 276.7 | 59.7 | -182.2 | 465.4 | 461.2 | -15 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.8 | 1283.4 | 3159.8 | 41.8 | 21.9 | 12.4 | 8.8 | 6.6 | 6.6 | 0 | 0.97696 | 0.9916 | 0.98531 | 0.91332 | 1.0081 | 0.91971 | 0.951 | 0.96244 | 0.93057 | 0.93888 | 0.89748 | 0.90242 | 0.92417 | 0.96905 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.5 | 73.7 | 64.7 | 64.2 | 88.9 | 22.5 | 0 | 0 | 88.5 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199 | 4504.8 | 28534.7 | 3273.9 | 195.9 | 678.1 | 4147.9 | 7635.3 | 303.1 | -1181.6 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 260.7 | 99.3 | 51.921 | 12.2 | 56.6 | 1.0865 | 1.0795 | 1.0786 | 1.0342 | 0 | 0 | 129 | 0 | 1622.1 | 1622.1 | 329.6 | 242.8 | 86.8 | 0.98699 | 0.98739 | 0.95313 | 0.9732 | 0.95772 | 0.95377 | 0.97687 | 0.98227 | 1.0086 | 0.97196 | 0.9708 | 0.97754 | 0.98788 | 7 | 4
p18otc330_mpsl.sav | 7416.8 | 3875.2 | 1107.5 | 1896.8 | 2300 | 1378.9 | 1226.7 | 894.2 | 334.3 | 785.8 | 785.8 | 103.8 | 164.6 | 82.6 | 26.3 | 26.8 | 1975.6 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2151 | -542.6 | 0 | 661.5 | 1962.6 | -604.4 | 816.1 | 322 | 14.1 | -137 | 420.2 | 427.4 | 20.7 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 120.8 | 1293.3 | 3159.8 | 41 | 20.4 | 14.8 | 9.1 | 6.6 | 6.6 | 0 | 0.98065 | 1.0017 | 0.9949 | 0.94918 | 1.0495 | 0.95111 | 0.98667 | 0.97855 | 0.94154 | 0.92454 | 0.91668 | 0.92256 | 0.93966 | 0.97692 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56.6 | 69 | 58.8 | 57.2 | 73 | 61.8 | 85.9 | 85.9 | 41.7 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1124.5 | 4579.2 | 28534.7 | 3273.9 | 236 | 638 | 4147.9 | 7635.3 | 296.8 | -1175.2 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 245.6 | 88.7 | 45.709 | 12.2 | 46.5 | 1.0854 | 1.0752 | 1.0737 | 1.033 | 0 | 0 | 129 | 0 | 1378.9 | 1702.6 | 329.6 | 242.8 | 86.8 | 0.99702 | 0.997 | 0.99056 | 1.0132 | 0.99042 | 0.98954 | 0.99322 | 0.99385 | 0.99323 | 0.99276 | 0.99247 | 0.99393 | 0.9959 | 8 | 5
p18otc330_mpsl_s.sav | 7416.1 | 3874.9 | 1107.5 | 1896.8 | 2300 | 1377.9 | 1226.7 | 892.7 | 336.4 | 785.8 | 785.8 | 103.7 | 165.2 | 82.7 | 26.2 | 26.8 | 1976.3 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2151.2 | -541.7 | 0 | 662.5 | 1962 | -605.2 | 816.8 | 322.8 | 13.5 | -136.4 | 419.6 | 426.9 | 21.2 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 120.8 | 1293.3 | 3159.8 | 41 | 20.4 | 14.8 | 9.1 | 6.6 | 6.6 | 0 | 0.98198 | 1.0042 | 0.99812 | 0.95143 | 1.0521 | 0.9526 | 0.98837 | 0.9794 | 0.95742 | 0.96862 | 0.92376 | 0.92997 | 0.94449 | 0.97954 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56.6 | 69 | 58.8 | 57.7 | 71.8 | 61.8 | 85.8 | 85.9 | 41.6 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1124.3 | 4579.5 | 28534.7 | 3273.9 | 235.8 | 638.2 | 4147.9 | 7635.3 | 296.6 | -1175 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 246 | 90.4 | 45.594 | 12.2 | 48.2 | 1.0856 | 1.0754 | 1.0738 | 1.0331 | 0 | 0 | 129 | 0 | 1377.9 | 1701.3 | 329.6 | 242.8 | 86.8 | 0.99951 | 1.0002 | 0.9929 | 1.0157 | 0.99197 | 0.99125 | 0.99408 | 1.0106 | 1.0406 | 1.0004 | 1.0004 | 0.99904 | 0.99857 | 9 | 5
p18otc330_angr1.sav | 7457.3 | 3843.2 | 1107.5 | 1896.8 | 2299.8 | 1419.7 | 1226.7 | 933.1 | 301.2 | 772.8 | 772.8 | 107.2 | 182.8 | 91.1 | 26.8 | 27.4 | 1980.8 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2151.6 | -607.7 | -93 | 609.7 | 1955.7 | -622.6 | 837.2 | 344 | 8 | -131 | 414.1 | 420.8 | 25.6 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 121.2 | 1293.1 | 3159.8 | 43.5 | 22.7 | 12.1 | 9.3 | 6.6 | 6.6 | 0 | 0.97147 | 0.9742 | 0.96812 | 0.95 | 1.0266 | 0.96177 | 0.99875 | 0.98692 | 0.92748 | 0.90932 | 0.92107 | 0.92715 | 0.94488 | 0.98006 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 117.1 | 54.3 | 51.3 | 63.4 | 60.7 | 83.3 | 83.8 | 39.2 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1135.7 | 4568 | 28534.7 | 3273.9 | 228.6 | 645.4 | 4147.9 | 7635.3 | 294.9 | -1173.4 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 223.3 | 77.8 | 41.65 | 12.2 | 35.9 | 1.0851 | 1.0749 | 1.0737 | 1.0329 | 0 | 0 | 129 | 0 | 1419.7 | 1733.9 | 329.6 | 242.8 | 86.8 | 0.96967 | 0.97017 | 0.99141 | 0.99106 | 1.0015 | 1.0017 | 1.0017 | 0.97901 | 0.97688 | 0.99751 | 0.99741 | 0.99945 | 0.9991 | 10 | 6
p18otc330_angr2.sav | 7456.9 | 3846.1 | 1107.5 | 1896.8 | 2299.8 | 1418.9 | 1226.7 | 927.9 | 307.1 | 774.6 | 774.6 | 106.7 | 181 | 90.1 | 26.7 | 27.3 | 1981 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2151.8 | -604 | -90.2 | 613.5 | 1955 | -623.7 | 838.7 | 345.5 | 7.9 | -130.9 | 414 | 420.4 | 25.7 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 120.5 | 1293.7 | 3159.8 | 43.1 | 22.3 | 12.6 | 9.3 | 6.6 | 6.6 | 0 | 0.97419 | 0.98342 | 0.97684 | 0.95481 | 1.032 | 0.96362 | 1.0008 | 0.98768 | 0.93418 | 0.91658 | 0.92303 | 0.92921 | 0.94608 | 0.98087 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 90.4 | 0 | 54.8 | 51.9 | 64.1 | 60.7 | 83.2 | 83.8 | 39.1 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1131.5 | 4572.1 | 28534.7 | 3273.9 | 228.5 | 645.5 | 4147.9 | 7635.3 | 295 | -1173.5 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 227.4 | 79.7 | 41.973 | 12.2 | 37.7 | 1.0851 | 1.0749 | 1.0737 | 1.0328 | 0 | 0 | 129 | 0 | 1418.9 | 1732.8 | 329.6 | 242.8 | 86.8 | 0.97885 | 0.97891 | 0.99643 | 0.99628 | 1.0034 | 1.0038 | 1.0025 | 0.98608 | 0.98468 | 0.99963 | 0.99962 | 1.0007 | 0.99993 | 11 | 7
p18otc330_angr12.sav | 7521.5 | 3816.1 | 1107.5 | 1896.8 | 2299.4 | 1502 | 1226.7 | 1028.2 | 137.4 | 713.5 | 713.5 | 122.8 | 235.7 | 116.8 | 29.6 | 30.2 | 1962 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2143.7 | -717.7 | -172.3 | 501.6 | 1976.7 | -593.1 | 802.5 | 307.7 | 20 | -142.4 | 425.4 | 434.3 | 17.5 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 114.3 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 178.9 | 1236.4 | 3159.8 | 55.4 | 36.7 | 4.1 | 12.9 | 6.6 | 6.6 | 0 | 0.88011 | 0.77283 | 0.76164 | 0.86111 | 0.92617 | 0.93183 | 0.96479 | 0.97376 | 0.75902 | 0.7237 | 0.87163 | 0.87527 | 0.91432 | 0.9584 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 39.4 | 30.3 | 64.9 | 62.5 | 86.9 | 86.1 | 41.6 | 34.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1143.7 | 4560 | 28534.7 | 3273.9 | 233.8 | 640.2 | 4147.9 | 7635.3 | 295.2 | -1173.7 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 111.8 | 25.6 | 26.432 | 12.2 | -16.4 | 1.0824 | 1.0719 | 1.0717 | 1.0312 | 0 | 0 | 129 | 0 | 1502 | 1828.9 | 329.6 | 242.8 | 86.8 | 0.76924 | 0.76325 | 0.89865 | 0.89407 | 0.97034 | 0.9676 | 0.98836 | 0.80119 | 0.77747 | 0.94397 | 0.9416 | 0.96713 | 0.97702 | 12 | 8
p18otc330_grgr.sav | 7485.7 | 3832.4 | 1107.5 | 1896.8 | 2300 | 1457.5 | 1226.7 | 974.4 | 228.5 | 690.9 | 690.9 | 166.8 | 234.3 | 114.6 | 35.5 | 36.3 | 1969.3 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2144.5 | -654 | -126.4 | 564.2 | 1966.3 | -610.2 | 823.2 | 329.3 | 15.9 | -138.5 | 421.6 | 428.1 | 20 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 115.2 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 145 | 1269.7 | 3159.8 | 62.5 | 56.7 | 14.2 | 17.1 | 6.6 | 6.6 | 0 | 0.91491 | 0.92409 | 0.9148 | 0.94834 | 1.0248 | 0.97449 | 1.0131 | 0.99491 | 0.8915 | 0.87024 | 0.92104 | 0.92713 | 0.9475 | 0.97966 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 28.9 | 35.2 | 45.1 | 37.5 | 48 | 61.5 | 84.8 | 84.8 | 40.2 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1140.3 | 4563.7 | 28534.7 | 3273.9 | 230.4 | 643.6 | 4147.9 | 7635.3 | 293.6 | -1172.1 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 174.6 | 53.9 | 32.977 | 12.2 | 12.3 | 1.0837 | 1.0731 | 1.0726 | 1.0324 | 0 | 0 | 129 | 0 | 1457.5 | 1777.1 | 329.6 | 242.8 | 86.8 | 0.9198 | 0.91673 | 0.98968 | 0.98925 | 1.0148 | 1.0161 | 1.0098 | 0.94103 | 0.9349 | 0.99748 | 0.99739 | 1.0022 | 0.99869 | 13 | 9
p18otc330_anpf.sav | 7585 | 3865.3 | 1107.5 | 1896.8 | 2299 | 1579.2 | 1226.7 | 1114.1 | 93.4 | 784.8 | 784.8 | 97.8 | 146.9 | 74.1 | 25.4 | 25.9 | 1939.7 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2141 | -744.1 | -186.2 | 478.5 | 1989.9 | -585.6 | 806.2 | 311.4 | 50.7 | -173.3 | 456.5 | 452.1 | -8.2 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.6 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.1 | 1308.9 | 3159.8 | 36.8 | 14.5 | 21.4 | 9.3 | 6.6 | 6.6 | 0 | 0.99216 | 1.0296 | 1.0207 | 1.1162 | 1.0158 | 1.0817 | 1.1336 | 1.042 | 0.94357 | 0.92674 | 0.904 | 0.90926 | 0.93154 | 0.97941 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 34.9 | 42.5 | 0 | 67.8 | 96.7 | 63.5 | 88.7 | 87 | 42.3 | 34.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1153.1 | 4550.6 | 28534.7 | 3273.9 | 237.6 | 636.4 | 4147.9 | 7635.3 | 298.2 | -1176.7 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | -13.3 | 106.6 | 63.087 | 12.2 | 63.6 | 1.0852 | 1.0741 | 1.0725 | 1.0328 | 0 | 0 | 129 | 0 | 1579.2 | 1912.4 | 329.6 | 242.8 | 86.8 | 1.0248 | 1.0228 | 1.1648 | 0.9806 | 1.1264 | 1.1369 | 1.0577 | 0.99599 | 0.9956 | 0.97902 | 0.97816 | 0.98534 | 0.99844 | 14 | 10
p18otc330_antbdy.sav | 7462.5 | 3847.7 | 1107.5 | 1896.8 | 2299.8 | 1426 | 1226.7 | 934.1 | 303.9 | 789.4 | 789.4 | 103.1 | 162.5 | 81.4 | 26.1 | 26.7 | 1978.6 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2152.1 | -609.5 | -93.8 | 608.5 | 1952.7 | -619.7 | 839 | 345.9 | 11.3 | -134.2 | 417.4 | 421.4 | 22.9 | 288 | 580 | 265.2 | 190 | 191.5 | 78 | 112 | 113.9 | 151 | 39 | 59 | 2532.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 114.2 | 1300 | 3159.8 | 40.2 | 19.3 | 16 | 9 | 6.6 | 6.6 | 0 | 0.98439 | 1.0104 | 1.0032 | 0.97023 | 1.0494 | 0.95443 | 0.99043 | 0.96019 | 0.94968 | 0.93333 | 0.91982 | 0.92584 | 0.941 | 0.97594 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 53.2 | 64.8 | 50.7 | 56.4 | 70.1 | 60.8 | 83.4 | 83.9 | 39.3 | 34.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1130.3 | 4573.4 | 28534.7 | 3273.9 | 229 | 645 | 4147.9 | 7635.3 | 299.6 | -1178.1 | 6760.9 | 900 | 3070.1 | 648.6 | 609.7 | 484 | 215.9 | 87.9 | 38.684 | 12.2 | 45.8 | 1.0857 | 1.0755 | 1.0739 | 1.0331 | 0 | 0 | 129 | 0 | 1426 | 1740.7 | 329.6 | 242.8 | 86.8 | 1.0057 | 1.0053 | 1.0125 | 1.013 | 0.99388 | 0.99331 | 0.97459 | 1.0024 | 1.0027 | 0.99616 | 0.996 | 0.99535 | 0.9949 | 15 | 11
p18otc330_brbo_brkp.sav | 7641.4 | 3533.1 | 1107.5 | 1896.8 | 2476.6 | 1343.8 | 1247.2 | 838.9 | 370.2 | 780 | 780 | 105.1 | 167.9 | 85.4 | 26.4 | 27 | 1971.7 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2150.7 | -1261.8 | -592.6 | -88.8 | 771.7 | -288.1 | 994 | 149.1 | 19.2 | -142.1 | 425.2 | 459.3 | 16.3 | 288 | 590.5 | 268.4 | 193.4 | 194.9 | 78 | 115.4 | 111.1 | 151 | 39 | 59 | 2532.8 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 147.2 | 1278.5 | 3171.1 | 43.5 | 22.9 | 12.9 | 10 | 6.6 | 6.6 | 0 | 0.9572 | 0.96116 | 0.95358 | 0.8559 | 0.94164 | 0.87553 | 0.90047 | 0.942 | 0.87112 | 0.84798 | 0.8636 | 0.86684 | 0.90372 | 0.96571 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 64 | 77.9 | 70.9 | 70.9 | 110.6 | 68.3 | 100.3 | 97.7 | 53.2 | 38.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1207.8 | 4846.5 | 28884.8 | 3292.5 | 202.2 | -438.4 | 3056.2 | 7635.3 | 320.8 | -1173.9 | 6786.2 | 916.2 | 3125.9 | 660.3 | 611.6 | 490 | 266.9 | 103.2 | 59.516 | 12.2 | 59.6 | 1.0769 | 1.0657 | 1.0642 | 1.0247 | 0 | 0 | 129 | 0 | 1343.8 | 1713.8 | 329.6 | 242.8 | 86.8 | 0.95669 | 0.9556 | 0.89321 | 0.90901 | 0.91172 | 0.90309 | 0.95612 | 0.91951 | 0.91098 | 0.93527 | 0.93253 | 0.95591 | 0.98447 | 16 | 12
p18otc330_brbo_brkp_s.sav | 7634 | 3533.9 | 1107.5 | 1896.8 | 2476.4 | 1335.6 | 1247.2 | 828.5 | 383.9 | 780.4 | 780.4 | 104.9 | 169.7 | 86 | 26.4 | 26.9 | 1974.7 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.4 | 2151.5 | -1252.2 | -585.9 | -79.8 | 770.5 | -291.9 | 996.3 | 151.7 | 16.3 | -139.2 | 422.4 | 457.4 | 18.6 | 288 | 590.5 | 268.4 | 193.4 | 194.9 | 78 | 115.4 | 111.1 | 151 | 39 | 59 | 2532.8 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 146.6 | 1279 | 3171.1 | 43.5 | 22.8 | 12.8 | 10 | 6.6 | 6.6 | 0 | 0.96231 | 0.97085 | 0.96368 | 0.89068 | 0.98196 | 0.89684 | 0.92489 | 0.95282 | 0.89414 | 0.89831 | 0.87541 | 0.87925 | 0.91226 | 0.97121 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 64.1 | 78 | 71.2 | 70.7 | 108.8 | 68.1 | 99.9 | 97.5 | 52.9 | 38.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1204.9 | 4848.1 | 28883.6 | 3292.5 | 201.1 | -437.4 | 3056.2 | 7635.3 | 319.6 | -1172.7 | 6786.2 | 916.2 | 3125.8 | 660.3 | 611.6 | 490 | 277.7 | 106.2 | 58.67 | 12.2 | 62.6 | 1.078 | 1.0669 | 1.0652 | 1.0256 | 0 | 0 | 129 | 0 | 1335.6 | 1704.6 | 329.6 | 242.8 | 86.8 | 0.96634 | 0.96572 | 0.92951 | 0.94793 | 0.93391 | 0.92758 | 0.9671 | 0.94381 | 0.96505 | 0.94806 | 0.94588 | 0.96495 | 0.99008 | 17 | 12
p18otc330_brgo_brkp.sav | 7639.3 | 3523.2 | 1107.5 | 1896.8 | 2482.6 | 1329.6 | 1248.3 | 823.4 | 373.3 | 779 | 779 | 106.5 | 168.7 | 86.5 | 26.5 | 27.1 | 1973.4 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.3 | 2151.2 | -1270.5 | -599.8 | -85.7 | 759 | -277.4 | 1001.2 | 145.6 | 17.2 | -140.1 | 423.2 | 457.5 | 18 | 288 | 591 | 268.6 | 193.6 | 195.1 | 78 | 115.6 | 110.9 | 151 | 39 | 59 | 2532.8 | 142.7 | 67.2 | 209.9 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 161.9 | 1264.2 | 3171.6 | 44.1 | 23.9 | 12 | 10.2 | 6.6 | 6.6 | 0 | 0.94714 | 0.9433 | 0.93398 | 0.82234 | 0.90264 | 0.84767 | 0.86838 | 0.92607 | 0.8207 | 0.79254 | 0.81383 | 0.81441 | 0.86649 | 0.94557 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 66.9 | 81.5 | 73.5 | 80.1 | 134.5 | 68.3 | 100.5 | 98 | 53.4 | 38.7 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1210.7 | 4855 | 28896.1 | 3292.5 | 212.3 | -447.7 | 3057 | 7635.3 | 329.2 | -1181.6 | 6786.7 | 917.1 | 3127.5 | 660.8 | 611.7 | 490 | 265.2 | 108.1 | 63.39 | 12.2 | 63.3 | 1.075 | 1.0639 | 1.063 | 1.0233 | 0 | 0 | 129 | 0 | 1329.6 | 1699.7 | 329.6 | 242.8 | 86.8 | 0.93892 | 0.93595 | 0.85819 | 0.87136 | 0.8827 | 0.87091 | 0.93995 | 0.86629 | 0.85142 | 0.88137 | 0.87612 | 0.91653 | 0.96394 | 18 | 13
p18otc330_brgo_brkp_s.sav | 7630.7 | 3522.9 | 1107.5 | 1896.8 | 2481 | 1320.6 | 1248.1 | 812.3 | 388.1 | 779.4 | 779.4 | 106.3 | 170.6 | 87.1 | 26.5 | 27.1 | 1976.5 | 330 | 330 | 808.8 | 815 | 2283.8 | 141 | 2122.3 | 2152 | -1260.1 | -592.4 | -75.7 | 758.3 | -281.9 | 1001.7 | 148.6 | 14.2 | -137.1 | 420.3 | 455.6 | 20.3 | 288 | 591 | 268.4 | 193.6 | 195.1 | 78 | 115.6 | 110.9 | 151 | 39 | 59 | 2532.8 | 142.6 | 67.2 | 209.8 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 161.1 | 1264.9 | 3171.5 | 44.2 | 23.8 | 11.9 | 10.2 | 6.6 | 6.6 | 0 | 0.95237 | 0.95312 | 0.94426 | 0.8571 | 0.94304 | 0.86933 | 0.89335 | 0.93729 | 0.84418 | 0.84228 | 0.82627 | 0.82753 | 0.8755 | 0.95158 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 66.9 | 81.5 | 73.7 | 79.6 | 132.8 | 68.1 | 100.1 | 97.7 | 53.1 | 38.7 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1207.3 | 4856.9 | 28894.6 | 3292.5 | 210.9 | -446.5 | 3056.8 | 7635.3 | 327.6 | -1180.1 | 6786.7 | 917.1 | 3127 | 660.8 | 611.7 | 490 | 276.4 | 111.7 | 62.432 | 12.2 | 67 | 1.0762 | 1.0653 | 1.064 | 1.0242 | 0 | 0 | 129 | 0 | 1320.6 | 1689.5 | 329.6 | 242.8 | 86.8 | 0.94869 | 0.94626 | 0.89446 | 0.91036 | 0.90526 | 0.89595 | 0.95134 | 0.89108 | 0.90486 | 0.89484 | 0.89024 | 0.92606 | 0.97007 | 19 | 13
p18otc340.sav | 7577 | 3895.5 | 1107.5 | 1896.8 | 2300 | 1517.3 | 1416.7 | 872.2 | 340.2 | 780.6 | 780.6 | 101.9 | 163 | 81.9 | 26 | 26.6 | 1960.5 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2130.5 | -703.6 | -157.3 | 528.5 | 1916 | -702.6 | 793.9 | 302.4 | 32.4 | -154.7 | 437.9 | 439.8 | 6.5 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 122.2 | 1295 | 3162.8 | 68 | 21.7 | 17.8 | 9.2 | 9.1 | 9.1 | 0 | 0.9773 | 0.99938 | 0.9925 | 0.93723 | 1.0387 | 0.94149 | 0.97576 | 0.97519 | 0.94199 | 0.92503 | 0.91976 | 0.92578 | 0.94252 | 0.97894 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57 | 69.4 | 61.4 | 56.4 | 70.7 | 62.8 | 87.2 | 86.2 | 41.6 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1167.6 | 4776.4 | 28774.9 | 3273.9 | 229.7 | 646 | 4149.6 | 7635.3 | 304 | -1374.1 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 253.4 | 86.8 | 48.227 | 16.1 | 44.6 | 1.0824 | 1.072 | 1.0715 | 1.0303 | 0 | 0 | 129 | 0 | 1517.3 | 1844.8 | 340.2 | 253.4 | 86.8 | 0.99938 | 0.9925 | 0.93723 | 1.0387 | 0.94149 | 0.97576 | 0.97519 | 0.94199 | 0.92503 | 0.91976 | 0.92578 | 0.94252 | 0.97894 | 0 | 0
p18otc340_amps.sav | 7732.8 | 3963.6 | 1107.5 | 1896.8 | 2298.8 | 1710.3 | 1416.7 | 1094.6 | 106.3 | 777.8 | 777.8 | 95.5 | 144.4 | 72.9 | 25 | 25.6 | 1919.2 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2119 | -823.1 | -234.6 | 416 | 1945.3 | -673.5 | 772.7 | 280.2 | 74.5 | -196.4 | 479.6 | 468.1 | -26.4 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72.3 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.6 | 1325.4 | 3162.8 | 63.6 | 15.7 | 24.6 | 9.9 | 9.1 | 9.1 | 0 | 0.99034 | 1.0307 | 1.0213 | 0.93723 | 1.0387 | 0.94149 | 0.97576 | 1.007 | 0.94357 | 0.92673 | 0.90162 | 0.90677 | 0.92863 | 0.97586 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 34.4 | 41.9 | 0 | 67.8 | 96 | 65.7 | 92.8 | 89.3 | 44.5 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1197.7 | 4746.3 | 28774.9 | 3273.9 | 237.8 | 637.9 | 4149.6 | 7581.2 | 304.5 | -1320.5 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 0 | 106.3 | 64.577 | 16.1 | 63.3 | 1.0822 | 1.0706 | 1.0699 | 1.03 | 0 | 0 | 129 | 0 | 1710.3 | 2056.9 | 340.2 | 253.4 | 86.8 | 1.0313 | 1.029 | 1 | 1 | 1 | 1 | 1.0327 | 1.0017 | 1.0018 | 0.98028 | 0.97947 | 0.98526 | 0.99685 | 1 | 1
p18otc340_amps_s.sav | 7731.7 | 3963.7 | 1107.5 | 1896.8 | 2298.9 | 1709 | 1416.7 | 1092.9 | 108.4 | 777.8 | 777.8 | 95.4 | 145 | 73.1 | 25 | 25.6 | 1919.7 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2119.1 | -821.7 | -233.6 | 417.4 | 1945 | -674 | 773.1 | 280.6 | 73.9 | -195.8 | 479.1 | 467.7 | -26 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72.3 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.7 | 1325.4 | 3162.8 | 63.6 | 15.7 | 24.6 | 9.9 | 9.1 | 9.1 | 0 | 0.99169 | 1.0332 | 1.0245 | 0.93723 | 1.0387 | 0.94149 | 0.97576 | 1.0073 | 0.95944 | 0.97086 | 0.90856 | 0.91404 | 0.93327 | 0.97836 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 34.4 | 42 | 0 | 68.1 | 95.3 | 65.7 | 92.7 | 89.2 | 44.5 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1197.4 | 4746.6 | 28774.9 | 3273.9 | 237.7 | 638 | 4149.6 | 7581.2 | 304.3 | -1320.3 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 0 | 108.4 | 64.477 | 16.1 | 65.4 | 1.0824 | 1.0708 | 1.07 | 1.0301 | 0 | 0 | 129 | 0 | 1709 | 2055.5 | 340.2 | 253.4 | 86.8 | 1.0338 | 1.0322 | 1 | 1 | 1 | 1 | 1.0329 | 1.0185 | 1.0495 | 0.98782 | 0.98732 | 0.99019 | 0.99941 | 2 | 1
p18otc340_dsbg.sav | 7629.7 | 3910.3 | 1107.5 | 1896.8 | 2299.5 | 1582.9 | 1416.7 | 948.7 | 264.9 | 783.7 | 783.7 | 99.2 | 150.4 | 74.4 | 25.6 | 26.2 | 1943.2 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2125.9 | -753.1 | -190.6 | 480.8 | 1932.4 | -690.9 | 782.6 | 290.6 | 50.3 | -172.5 | 455.7 | 453.2 | -7.6 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72.1 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 103.1 | 1314 | 3162.8 | 66.3 | 19.4 | 20.4 | 9.4 | 9.1 | 9.1 | 0 | 0.98055 | 1.0053 | 1 | 0.92619 | 1.023 | 0.92944 | 0.96207 | 0.96943 | 0.98779 | 0.97439 | 0.9538 | 0.96142 | 0.97187 | 0.98335 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 50.9 | 62 | 64.7 | 17 | 45.2 | 63.9 | 89.3 | 87.4 | 42.7 | 34.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1177.7 | 4766.3 | 28774.9 | 3273.9 | 232.9 | 642.8 | 4149.6 | 7635.3 | 307.6 | -1377.7 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 264.9 | 0 | 51.4 | 16.1 | -41.6 | 1.082 | 1.0713 | 1.0708 | 1.03 | 0 | 0 | 129 | 0 | 1582.9 | 1917.6 | 340.2 | 253.4 | 86.8 | 1.0059 | 1.0076 | 0.98822 | 0.9849 | 0.9872 | 0.98597 | 0.99409 | 1.0486 | 1.0534 | 1.037 | 1.0385 | 1.0311 | 1.0045 | 3 | 2
p18otc340_bloxhcb.sav | 7674.2 | 3907.8 | 1107.5 | 1896.8 | 2299.9 | 1386.6 | 1416.7 | 835.3 | 351 | 770.4 | 770.4 | 101.6 | 162.4 | 81.8 | 26 | 26.5 | 1939.1 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2123.9 | -605.7 | -317.2 | 585.8 | 1937.2 | -672.2 | 760.2 | 267.3 | 53.8 | -175.9 | 459.1 | 457.9 | -10.2 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127.1 | 1290.1 | 3162.8 | 68.6 | 22.4 | 16.7 | 9.4 | 9.1 | 9.1 | 0 | 0.9739 | 0.99203 | 0.98509 | 0.91687 | 1.0122 | 0.92363 | 0.95546 | 0.96532 | 0.9281 | 0.90999 | 0.90642 | 0.9118 | 0.93202 | 0.97313 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.9 | 71.7 | 64.2 | 59.7 | 79 | 65.2 | 115 | 0 | 65.6 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1210 | 4734.1 | 28774.9 | 3273.9 | 212.1 | 663.6 | 4149.6 | 7635.3 | 306.7 | -1376.8 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 259.7 | 91.3 | 51.374 | 16.1 | 48.8 | 1.0819 | 1.0709 | 1.0697 | 1.0298 | 0 | 0 | 129 | 0 | 1386.6 | 1809 | 340.2 | 253.4 | 86.8 | 0.99264 | 0.99253 | 0.97828 | 0.97454 | 0.98103 | 0.9792 | 0.98988 | 0.98525 | 0.98374 | 0.9855 | 0.9849 | 0.98886 | 0.99406 | 4 | 3
p18otc340_bloxhcb_s.sav | 7672.9 | 3908 | 1107.5 | 1896.8 | 2299.9 | 1385.1 | 1416.7 | 833.4 | 353.5 | 770.3 | 770.3 | 101.5 | 163 | 82 | 25.9 | 26.5 | 1939.6 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2124.1 | -604.1 | -316 | 587.4 | 1936.8 | -672.8 | 760.6 | 267.8 | 53.2 | -175.3 | 458.5 | 457.5 | -9.8 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127 | 1290.1 | 3162.8 | 68.6 | 22.4 | 16.7 | 9.4 | 9.1 | 9.1 | 0 | 0.97536 | 0.99473 | 0.98855 | 0.91925 | 1.015 | 0.92517 | 0.95722 | 0.96619 | 0.94427 | 0.95406 | 0.91358 | 0.91931 | 0.93688 | 0.97578 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 58.9 | 71.7 | 64.2 | 60.1 | 77.9 | 65.1 | 115 | 0 | 65.6 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1209.6 | 4734.5 | 28774.9 | 3273.9 | 212 | 663.7 | 4149.6 | 7635.3 | 306.5 | -1376.6 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 260.4 | 93.1 | 51.259 | 16.1 | 50.7 | 1.0821 | 1.0711 | 1.0699 | 1.03 | 0 | 0 | 129 | 0 | 1385.1 | 1807.4 | 340.2 | 253.4 | 86.8 | 0.99535 | 0.99602 | 0.98082 | 0.97719 | 0.98267 | 0.981 | 0.99077 | 1.0024 | 1.0314 | 0.99328 | 0.99301 | 0.99402 | 0.99677 | 5 | 3
p18otc340_blhcoxll.sav | 7951.2 | 3929.1 | 1107.5 | 1896.8 | 2299 | 1751.6 | 1416.7 | 777.4 | 364.9 | 754.2 | 754.2 | 100.7 | 160.8 | 81.2 | 25.9 | 26.4 | 1903.4 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2113.2 | -480.8 | -519 | 661.2 | 1966.4 | -631.9 | 717.8 | 223.5 | 89.2 | -210.9 | 494.1 | 484.6 | -37.4 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.4 | 1281.7 | 3162.8 | 69 | 23.6 | 15 | 8.5 | 9.1 | 9.1 | 0 | 0.96975 | 0.98104 | 0.97379 | 0.88255 | 0.97255 | 0.89291 | 0.9204 | 0.94813 | 0.90462 | 0.88452 | 0.88323 | 0.88747 | 0.91382 | 0.96284 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 61.9 | 75.4 | 68.7 | 65 | 92.3 | 22.9 | 0 | 0 | 93.5 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1247.6 | 4696.6 | 28774.9 | 3273.9 | 193.3 | 682.4 | 4149.6 | 7635.3 | 312.7 | -1382.7 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 267.5 | 97.5 | 56.556 | 16.1 | 54.6 | 1.0831 | 1.0762 | 1.0763 | 1.0313 | 0 | 0 | 129 | 0 | 1751.6 | 1751.6 | 340.2 | 253.4 | 86.8 | 0.98165 | 0.98115 | 0.94166 | 0.93632 | 0.9484 | 0.94327 | 0.97225 | 0.96033 | 0.95621 | 0.96028 | 0.95862 | 0.96955 | 0.98355 | 6 | 4
p18otc340_blhcoxll_s.sav | 7949.7 | 3929.3 | 1107.5 | 1896.8 | 2299 | 1749.8 | 1416.7 | 775.3 | 367.8 | 754.1 | 754.1 | 100.7 | 161.5 | 81.5 | 25.9 | 26.4 | 1904.1 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2113.4 | -479 | -517.4 | 663 | 1965.9 | -632.6 | 718.4 | 224.1 | 88.6 | -210.3 | 493.5 | 484.2 | -37 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.4 | 1281.8 | 3162.8 | 69 | 23.6 | 15 | 8.4 | 9.1 | 9.1 | 0 | 0.9713 | 0.98388 | 0.9774 | 0.88513 | 0.97553 | 0.89456 | 0.92229 | 0.94905 | 0.92078 | 0.92799 | 0.89036 | 0.89495 | 0.91862 | 0.96548 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 61.9 | 75.3 | 68.6 | 65.3 | 91.2 | 22.9 | 0 | 0 | 93.4 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1247.1 | 4697.1 | 28774.9 | 3273.9 | 193.2 | 682.5 | 4149.6 | 7635.3 | 312.4 | -1382.4 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 268.3 | 99.5 | 56.423 | 16.1 | 56.7 | 1.0834 | 1.0764 | 1.0765 | 1.0315 | 0 | 0 | 129 | 0 | 1749.8 | 1749.8 | 340.2 | 253.4 | 86.8 | 0.98449 | 0.98479 | 0.94441 | 0.93919 | 0.95015 | 0.9452 | 0.9732 | 0.97748 | 1.0032 | 0.96803 | 0.9667 | 0.97464 | 0.98625 | 7 | 4
p18otc340_mpsl.sav | 7520.8 | 3952 | 1107.5 | 1896.8 | 2300.1 | 1467.5 | 1416.7 | 843.8 | 348.9 | 773 | 773 | 101.7 | 162.7 | 81.9 | 26 | 26.6 | 1945 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2125.7 | -611.7 | 0 | 598.8 | 1939.6 | -658.3 | 739.7 | 246.3 | 47.9 | -170 | 453.2 | 458 | -5.6 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 126.4 | 1290.7 | 3162.8 | 68.6 | 22.3 | 17.1 | 9.3 | 9.1 | 9.1 | 0 | 0.97432 | 0.99282 | 0.98588 | 0.91836 | 1.014 | 0.92373 | 0.95558 | 0.96387 | 0.92941 | 0.91142 | 0.9068 | 0.9122 | 0.93187 | 0.9722 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.6 | 71.3 | 63.8 | 59.2 | 77.8 | 65.6 | 93.8 | 91.1 | 47.3 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1163.3 | 4780.6 | 28774.9 | 3273.9 | 244.7 | 631.1 | 4149.6 | 7635.3 | 305.8 | -1375.8 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 258.3 | 90.6 | 50.966 | 16.1 | 48.2 | 1.0821 | 1.0714 | 1.0707 | 1.03 | 0 | 0 | 129 | 0 | 1467.5 | 1817.9 | 340.2 | 253.4 | 86.8 | 0.99344 | 0.99333 | 0.97987 | 0.9762 | 0.98114 | 0.97932 | 0.98839 | 0.98664 | 0.98529 | 0.98591 | 0.98533 | 0.9887 | 0.99311 | 8 | 5
p18otc340_mpsl_s.sav | 7520.1 | 3951.7 | 1107.5 | 1896.8 | 2300.1 | 1466.4 | 1416.7 | 842.2 | 351.3 | 773 | 773 | 101.7 | 163.3 | 82.1 | 26 | 26.5 | 1945.7 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2125.9 | -610.8 | 0 | 599.9 | 1939 | -659.2 | 740.6 | 247.2 | 47.2 | -169.3 | 452.5 | 457.4 | -5.1 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 126.3 | 1290.8 | 3162.8 | 68.5 | 22.3 | 17.1 | 9.3 | 9.1 | 9.1 | 0 | 0.9758 | 0.99555 | 0.98937 | 0.92086 | 1.0169 | 0.92537 | 0.95745 | 0.96479 | 0.94565 | 0.95561 | 0.91404 | 0.91979 | 0.9368 | 0.97488 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 58.5 | 71.3 | 63.7 | 59.7 | 76.6 | 65.6 | 93.7 | 91.1 | 47.2 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1163 | 4781 | 28774.9 | 3273.9 | 244.5 | 631.3 | 4149.6 | 7635.3 | 305.6 | -1375.6 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 258.9 | 92.4 | 50.834 | 16.1 | 50.1 | 1.0823 | 1.0716 | 1.0709 | 1.0301 | 0 | 0 | 129 | 0 | 1466.4 | 1816.5 | 340.2 | 253.4 | 86.8 | 0.99617 | 0.99685 | 0.98253 | 0.97897 | 0.98288 | 0.98123 | 0.98933 | 1.0039 | 1.0331 | 0.99378 | 0.99353 | 0.99393 | 0.99585 | 9 | 5
p18otc340_angr1.sav | 7589.7 | 3892.1 | 1107.5 | 1896.8 | 2299.8 | 1533.5 | 1416.7 | 898.2 | 310.7 | 764 | 764 | 105.3 | 180.8 | 90.4 | 26.6 | 27.2 | 1958.2 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2128.9 | -723.1 | -171.3 | 509.4 | 1919.5 | -697.8 | 787.8 | 296 | 33.7 | -155.9 | 439.1 | 441.8 | 5.7 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 124.7 | 1292.7 | 3162.8 | 70.9 | 24.3 | 14.6 | 9.4 | 9.1 | 9.1 | 0 | 0.96536 | 0.96505 | 0.95896 | 0.92774 | 1.0277 | 0.94314 | 0.97764 | 0.97712 | 0.91882 | 0.89993 | 0.91639 | 0.92225 | 0.94133 | 0.97769 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 119.7 | 57.9 | 51.8 | 64.4 | 63.1 | 87.9 | 86.6 | 42 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1176.6 | 4767.4 | 28774.9 | 3273.9 | 230.4 | 645.3 | 4149.6 | 7635.3 | 303 | -1373.1 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 233.5 | 77.2 | 45.418 | 16.1 | 35.2 | 1.0818 | 1.0714 | 1.071 | 1.0299 | 0 | 0 | 129 | 0 | 1533.5 | 1863.3 | 340.2 | 253.4 | 86.8 | 0.96565 | 0.96621 | 0.98987 | 0.98943 | 1.0018 | 1.0019 | 1.002 | 0.9754 | 0.97287 | 0.99634 | 0.99619 | 0.99874 | 0.99872 | 10 | 6
p18otc340_angr2.sav | 7589.3 | 3895.2 | 1107.5 | 1896.8 | 2299.8 | 1532.8 | 1416.7 | 892.8 | 316.8 | 765.8 | 765.8 | 104.8 | 179.1 | 89.4 | 26.5 | 27.1 | 1958.5 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2129 | -719.2 | -168.3 | 513.3 | 1918.8 | -698.9 | 789.3 | 297.6 | 33.6 | -155.8 | 439 | 441.4 | 5.7 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.9 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 124 | 1293.3 | 3162.8 | 70.5 | 23.9 | 15.1 | 9.3 | 9.1 | 9.1 | 0 | 0.96826 | 0.97481 | 0.96819 | 0.93274 | 1.0335 | 0.94496 | 0.9797 | 0.97784 | 0.92594 | 0.90765 | 0.9185 | 0.92446 | 0.94263 | 0.97855 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 92.4 | 0 | 58.4 | 52.4 | 65.1 | 63.1 | 87.8 | 86.5 | 41.9 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1172.2 | 4771.8 | 28774.9 | 3273.9 | 230.3 | 645.5 | 4149.6 | 7635.3 | 303.1 | -1373.2 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 237.6 | 79.1 | 45.736 | 16.1 | 37.1 | 1.0818 | 1.0714 | 1.071 | 1.0299 | 0 | 0 | 129 | 0 | 1532.8 | 1862.3 | 340.2 | 253.4 | 86.8 | 0.97542 | 0.97551 | 0.99521 | 0.995 | 1.0037 | 1.004 | 1.0027 | 0.98296 | 0.98121 | 0.99863 | 0.99857 | 1.0001 | 0.9996 | 11 | 7
p18otc340_angr12.sav | 7661.8 | 3855.6 | 1107.5 | 1896.8 | 2299.3 | 1626 | 1416.7 | 1008 | 119.3 | 708.6 | 708.6 | 121.4 | 223.6 | 111.8 | 29.6 | 30.3 | 1933.9 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2121.4 | -851.9 | -264.4 | 383.2 | 1944.4 | -662.5 | 746.3 | 252.9 | 49.3 | -170.8 | 453.8 | 457.9 | -4.7 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -71.7 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1737.5 | 199.2 | 1227 | 3162.8 | 81.1 | 40.1 | 3.3 | 12.6 | 9.1 | 9.1 | 0 | 0.83727 | 0.69763 | 0.68572 | 0.80246 | 0.88195 | 0.89685 | 0.92491 | 0.95611 | 0.68876 | 0.64466 | 0.84209 | 0.8442 | 0.89374 | 0.94569 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 41.8 | 29.7 | 79 | 65.3 | 92.1 | 89.3 | 44.8 | 34.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1189.2 | 4754.8 | 28774.9 | 3273.9 | 237.5 | 638.2 | 4149.6 | 7635.3 | 304.9 | -1375 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 103.8 | 15.6 | 28.781 | 16.1 | -26.9 | 1.0775 | 1.0667 | 1.0681 | 1.0271 | 0 | 0 | 129 | 0 | 1626 | 1970.1 | 340.2 | 253.4 | 86.8 | 0.69806 | 0.6909 | 0.8562 | 0.8491 | 0.95259 | 0.94789 | 0.98043 | 0.73118 | 0.69691 | 0.91555 | 0.91188 | 0.94825 | 0.96603 | 12 | 8
p18otc340_grgr.sav | 7618.9 | 3879.6 | 1107.5 | 1896.8 | 2300 | 1572.6 | 1416.7 | 942 | 234.2 | 684.8 | 684.8 | 164.1 | 229 | 112.7 | 35.3 | 36.1 | 1946.7 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2122.4 | -772.1 | -206.6 | 461.4 | 1930.4 | -684.7 | 772.5 | 280.1 | 41.5 | -163.4 | 446.4 | 449.1 | 0.2 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -70.7 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149.8 | 1268 | 3162.8 | 88.3 | 58.6 | 11.4 | 16.1 | 9.1 | 9.1 | 0 | 0.88868 | 0.8974 | 0.88812 | 0.91695 | 1.0152 | 0.95248 | 0.98823 | 0.98372 | 0.86827 | 0.84487 | 0.91056 | 0.91615 | 0.94002 | 0.97503 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.7 | 37.5 | 48.6 | 38.1 | 51.3 | 63.9 | 89.5 | 87.6 | 43.1 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1182.7 | 4761.6 | 28774.9 | 3273.9 | 232.5 | 643.2 | 4149.6 | 7635.3 | 301.7 | -1371.8 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 182.8 | 51.5 | 36.823 | 16.1 | 9.8 | 1.0805 | 1.0696 | 1.0699 | 1.0295 | 0 | 0 | 129 | 0 | 1572.6 | 1908 | 340.2 | 253.4 | 86.8 | 0.89796 | 0.89483 | 0.97836 | 0.9774 | 1.0117 | 1.0128 | 1.0087 | 0.92174 | 0.91334 | 0.99 | 0.9896 | 0.99735 | 0.99601 | 13 | 9
p18otc340_anpf.sav | 7723.6 | 3915.2 | 1107.5 | 1896.8 | 2298.9 | 1701.4 | 1416.7 | 1088.2 | 94.7 | 776 | 776 | 95.4 | 144.4 | 73 | 25 | 25.6 | 1915.5 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2117.9 | -865 | -267.9 | 373.7 | 1955 | -659.9 | 755.4 | 262.1 | 78.1 | -200 | 483.2 | 473.9 | -29.1 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72.3 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.9 | 1311.1 | 3162.8 | 63.7 | 15.8 | 24.4 | 9.9 | 9.1 | 9.1 | 0 | 0.99015 | 1.0303 | 1.0208 | 1.1159 | 1.0156 | 1.0815 | 1.1333 | 1.0418 | 0.94125 | 0.92423 | 0.90093 | 0.90604 | 0.92926 | 0.9785 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 34.6 | 42.2 | 0 | 68.9 | 99.2 | 66.1 | 93.6 | 89.9 | 45.3 | 35.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1196.3 | 4747.7 | 28774.9 | 3273.9 | 240.4 | 635.3 | 4149.6 | 7635.3 | 305.8 | -1375.9 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | -13.2 | 108 | 67.845 | 16.1 | 64.8 | 1.0822 | 1.0706 | 1.0698 | 1.03 | 0 | 0 | 129 | 0 | 1701.4 | 2051 | 340.2 | 253.4 | 86.8 | 1.0309 | 1.0285 | 1.1907 | 0.97777 | 1.1487 | 1.1615 | 1.0683 | 0.99921 | 0.99913 | 0.97953 | 0.97868 | 0.98593 | 0.99955 | 14 | 10
p18otc340_antbdy.sav | 7596.4 | 3897 | 1107.5 | 1896.8 | 2299.8 | 1541.7 | 1416.7 | 900.8 | 312.2 | 780.6 | 780.6 | 101 | 160.6 | 80.6 | 25.9 | 26.4 | 1955.6 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2129.1 | -726.4 | -173.1 | 506.8 | 1916.6 | -694.4 | 789.3 | 297.6 | 37.4 | -159.7 | 442.8 | 442.7 | 2.5 | 288 | 580 | 265.2 | 380 | 191.5 | 78 | 302 | -72 | 151 | 39 | 59 | 2535.8 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 116.6 | 1300.6 | 3162.8 | 67.4 | 20.9 | 18.7 | 9.2 | 9.1 | 9.1 | 0 | 0.98004 | 1.0057 | 0.99836 | 0.94904 | 1.0524 | 0.92997 | 0.96267 | 0.94004 | 0.94425 | 0.92746 | 0.91489 | 0.92067 | 0.93663 | 0.97234 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 53.9 | 65.7 | 53.5 | 57 | 71.1 | 63.3 | 88.1 | 86.7 | 42.1 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1170.9 | 4773 | 28774.9 | 3273.9 | 230.8 | 644.9 | 4149.6 | 7635.3 | 308.9 | -1379 | 6569.2 | 900 | 3120.3 | 650.3 | 418 | 484 | 224.1 | 88.1 | 41.868 | 16.1 | 45.9 | 1.0826 | 1.072 | 1.0713 | 1.0303 | 0 | 0 | 129 | 0 | 1541.7 | 1872.3 | 340.2 | 253.4 | 86.8 | 1.0063 | 1.0059 | 1.0126 | 1.0132 | 0.98776 | 0.98659 | 0.96396 | 1.0024 | 1.0026 | 0.9947 | 0.99448 | 0.99375 | 0.99326 | 15 | 11
p18otc340_brbo_brkp.sav | 7780.6 | 3585.3 | 1107.5 | 1896.8 | 2478.9 | 1460.8 | 1440.8 | 804.9 | 371.8 | 769.2 | 769.2 | 103 | 165 | 84.3 | 26.1 | 26.6 | 1943.3 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2126.4 | -1376.8 | -669.4 | -184.8 | 752.3 | -368.5 | 943.2 | 95.3 | 50.7 | -172.8 | 456 | 487 | -8 | 288 | 590.5 | 268.4 | 386.8 | 195.1 | 78 | 308.8 | -77.9 | 151 | 39 | 59 | 2535.8 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 151.8 | 1276.9 | 3174.3 | 71.6 | 24.3 | 15.7 | 10.4 | 9.1 | 9.1 | 0 | 0.94912 | 0.95128 | 0.94347 | 0.82361 | 0.90411 | 0.84676 | 0.86733 | 0.92616 | 0.85908 | 0.83481 | 0.85551 | 0.85833 | 0.89754 | 0.96167 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 65.2 | 79.4 | 74.4 | 72 | 112.8 | 70.9 | 105.4 | 100.9 | 56.3 | 39.2 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1259 | 5045.5 | 29134.8 | 3292.5 | 210 | -444.4 | 3058 | 7635.3 | 328.7 | -1373.3 | 6594.6 | 916.2 | 3177.6 | 662.1 | 419.6 | 490 | 269.3 | 102.5 | 64.114 | 16.1 | 58.8 | 1.0721 | 1.0606 | 1.06 | 1.0203 | 0 | 0 | 129 | 0 | 1460.8 | 1846.1 | 340.2 | 253.4 | 86.8 | 0.95187 | 0.9506 | 0.87877 | 0.87043 | 0.89938 | 0.88888 | 0.94972 | 0.91198 | 0.90247 | 0.93014 | 0.92714 | 0.95228 | 0.98236 | 16 | 12
p18otc340_brbo_brkp_s.sav | 7770.6 | 3582.5 | 1107.5 | 1896.8 | 2476.9 | 1451.9 | 1440.6 | 794.2 | 386.1 | 769.6 | 769.6 | 102.8 | 166.8 | 84.8 | 26.1 | 26.6 | 1946.5 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2127.3 | -1367.4 | -663.1 | -176 | 751 | -372.4 | 942.6 | 97.9 | 47.7 | -169.8 | 453 | 485 | -5.7 | 288 | 590.5 | 268.4 | 386.8 | 194.9 | 78 | 308.8 | -77.9 | 151 | 39 | 59 | 2535.8 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 151.2 | 1277.6 | 3174.2 | 71.6 | 24.4 | 15.6 | 10.3 | 9.1 | 9.1 | 0 | 0.95432 | 0.96101 | 0.95364 | 0.85801 | 0.94409 | 0.8679 | 0.8917 | 0.93688 | 0.88225 | 0.88502 | 0.86747 | 0.8709 | 0.90619 | 0.96723 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 65.3 | 79.5 | 74.6 | 71.8 | 110.8 | 70.7 | 104.9 | 100.6 | 56 | 39.1 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1255.1 | 5045.8 | 29131.3 | 3292.5 | 208.7 | -443.3 | 3057.9 | 7635.3 | 327.3 | -1372.4 | 6594.2 | 916.2 | 3177.4 | 662 | 419.6 | 490 | 280.6 | 105.5 | 63.19 | 16.1 | 61.8 | 1.0735 | 1.062 | 1.0611 | 1.0213 | 0 | 0 | 129 | 0 | 1451.9 | 1836.1 | 340.2 | 253.4 | 86.8 | 0.96161 | 0.96085 | 0.91547 | 0.90892 | 0.92184 | 0.91385 | 0.96071 | 0.93658 | 0.95675 | 0.94315 | 0.94072 | 0.96145 | 0.98804 | 17 | 12
p18otc340_brgo_brkp.sav | 7779.8 | 3575.6 | 1107.5 | 1896.8 | 2484.4 | 1449.6 | 1442 | 793 | 371.4 | 768.4 | 768.4 | 104.4 | 165.6 | 85.2 | 26.2 | 26.8 | 1944.9 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.4 | 2127 | -1387.5 | -678 | -184.6 | 737.9 | -354.8 | 949.1 | 91.4 | 48.8 | -170.9 | 454 | 484.7 | -6.4 | 288 | 591 | 268.6 | 387.2 | 195.2 | 78 | 309.2 | -78.2 | 151 | 39 | 59 | 2535.8 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.2 | 1745.2 | 166.7 | 1262.6 | 3174.7 | 72.2 | 25.2 | 14.9 | 10.5 | 9.1 | 9.1 | 0 | 0.93847 | 0.93257 | 0.92295 | 0.78717 | 0.86161 | 0.81603 | 0.83167 | 0.90827 | 0.80672 | 0.77704 | 0.80303 | 0.803 | 0.8577 | 0.93879 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 68.2 | 83 | 76.9 | 81 | 136.2 | 71 | 105.6 | 101.2 | 56.7 | 39.4 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1263 | 5053.2 | 29146.5 | 3292.5 | 219.8 | -452.7 | 3059.5 | 7635.3 | 337.5 | -1381.9 | 6594.8 | 917.1 | 3179.6 | 662.6 | 419.6 | 490 | 265 | 106.4 | 68.216 | 16.1 | 61.5 | 1.0701 | 1.0587 | 1.0586 | 1.0187 | 0 | 0 | 129 | 0 | 1449.6 | 1835.3 | 340.2 | 253.4 | 86.8 | 0.93315 | 0.92992 | 0.83989 | 0.82952 | 0.86674 | 0.85233 | 0.93138 | 0.8564 | 0.84002 | 0.87309 | 0.86738 | 0.91001 | 0.95899 | 18 | 13
p18otc340_brgo_brkp_s.sav | 7769.7 | 3574 | 1107.5 | 1896.8 | 2483.1 | 1440.5 | 1441.9 | 781.7 | 386.7 | 768.9 | 768.9 | 104.2 | 167.4 | 85.8 | 26.2 | 26.8 | 1948.2 | 330 | 330 | 811.8 | 815 | 2286.8 | 141 | 2125.3 | 2127.8 | -1376.4 | -670.4 | -174.3 | 737.1 | -359.6 | 950.2 | 94.5 | 45.6 | -167.7 | 450.8 | 482.7 | -3.9 | 288 | 591 | 268.6 | 387.2 | 195.1 | 78 | 309.2 | -78.2 | 151 | 39 | 59 | 2535.8 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.2 | 1745.2 | 165.7 | 1263.4 | 3174.7 | 72.2 | 25.2 | 14.8 | 10.5 | 9.1 | 9.1 | 0 | 0.94375 | 0.94237 | 0.93324 | 0.82157 | 0.90175 | 0.83761 | 0.85675 | 0.91944 | 0.83037 | 0.82669 | 0.81572 | 0.8164 | 0.8669 | 0.94492 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 68.1 | 82.9 | 77 | 80.5 | 134.4 | 70.8 | 105.1 | 100.9 | 56.3 | 39.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1258.7 | 5052.8 | 29141.8 | 3292.5 | 218.2 | -451.1 | 3059.5 | 7635.3 | 335.8 | -1380 | 6594.8 | 917.1 | 3179 | 662.6 | 419.6 | 490 | 276.7 | 110 | 67.161 | 16.1 | 65.2 | 1.0714 | 1.0601 | 1.0598 | 1.0197 | 0 | 0 | 129 | 0 | 1440.5 | 1824.9 | 340.2 | 253.4 | 86.8 | 0.94295 | 0.94029 | 0.87659 | 0.86816 | 0.88966 | 0.87803 | 0.94283 | 0.88151 | 0.89369 | 0.88688 | 0.88185 | 0.91977 | 0.96525 | 19 | 13
p18otc349.sav | 7706.9 | 3943.3 | 1107.5 | 1896.8 | 2300 | 1639.3 | 1617.1 | 833.2 | 349.1 | 769.5 | 769.5 | 100.1 | 160.8 | 80.8 | 25.7 | 26.3 | 1932.9 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2117.5 | -816.5 | -233.9 | 429.9 | 1881.5 | -776 | 745.8 | 255.8 | 62.9 | -184.7 | 467.8 | 463 | -17.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.3 | 1294.7 | 3165.6 | 70.6 | 23.6 | 13.6 | 8.8 | 10 | 10 | 0 | 0.97502 | 0.99448 | 0.98761 | 0.91616 | 1.0315 | 0.92239 | 0.95405 | 0.96493 | 0.93638 | 0.91895 | 0.91565 | 0.92148 | 0.93921 | 0.97669 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.3 | 71 | 64.8 | 57.2 | 72.1 | 65.2 | 91.8 | 88.9 | 44.3 | 35.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1205.3 | 4976.1 | 29012.3 | 3273.9 | 232.4 | 646 | 4152.3 | 7635.3 | 316 | -1574.5 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 262 | 87.1 | 51.878 | 19.6 | 44.9 | 1.0786 | 1.0682 | 1.0686 | 1.0265 | 0 | 0 | 129 | 0 | 1639.3 | 1982.1 | 349.1 | 262 | 87.1 | 0.99448 | 0.98761 | 0.91616 | 1.0315 | 0.92239 | 0.95405 | 0.96493 | 0.93638 | 0.91895 | 0.91565 | 0.92148 | 0.93921 | 0.97669 | 0 | 0
p18otc349_amps.sav | 7867.8 | 4011.8 | 1107.5 | 1896.8 | 2298.8 | 1839.6 | 1617.1 | 1063.9 | 107.9 | 766.9 | 766.9 | 93.3 | 141.7 | 71.5 | 24.7 | 25.3 | 1890.2 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2105.9 | -940.9 | -314.2 | 313.5 | 1911.7 | -746.1 | 723.2 | 232.2 | 106.2 | -227.5 | 510.7 | 491.6 | -50.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.3 | 1327.5 | 3165.6 | 65.9 | 17.3 | 20.6 | 9 | 10 | 10 | 0 | 0.99085 | 1.032 | 1.0221 | 0.91616 | 1.0315 | 0.92239 | 0.95405 | 1.0067 | 0.9415 | 0.9245 | 0.89832 | 0.90331 | 0.92611 | 0.97479 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 34.5 | 42 | 0 | 69.1 | 98.7 | 68.3 | 97.7 | 92.1 | 47.5 | 35.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1238.3 | 4943.2 | 29012.3 | 3273.9 | 241.4 | 637 | 4152.3 | 7581.2 | 316 | -1520.3 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 0 | 107.9 | 69.052 | 19.6 | 64.8 | 1.0786 | 1.0669 | 1.0671 | 1.0263 | 0 | 0 | 129 | 0 | 1839.6 | 2202.1 | 349.1 | 262 | 87.1 | 1.0377 | 1.035 | 1 | 1 | 1 | 1 | 1.0433 | 1.0055 | 1.006 | 0.98107 | 0.98028 | 0.98605 | 0.99806 | 1 | 1
p18otc349_amps_s.sav | 7866.7 | 4011.9 | 1107.5 | 1896.8 | 2298.8 | 1838.3 | 1617.1 | 1062.2 | 110 | 766.9 | 766.9 | 93.2 | 142.2 | 71.7 | 24.7 | 25.2 | 1890.7 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2106.1 | -939.5 | -313.2 | 314.9 | 1911.4 | -746.6 | 723.6 | 232.6 | 105.6 | -227 | 510.2 | 491.3 | -50 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.4 | 1327.5 | 3165.6 | 65.8 | 17.4 | 20.6 | 8.9 | 10 | 10 | 0 | 0.9922 | 1.0345 | 1.0253 | 0.91616 | 1.0315 | 0.92239 | 0.95405 | 1.007 | 0.95735 | 0.96855 | 0.90525 | 0.91057 | 0.93074 | 0.97729 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 34.5 | 42.1 | 0 | 69.3 | 98 | 68.3 | 97.6 | 92.1 | 47.4 | 35.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1238 | 4943.5 | 29012.3 | 3273.9 | 241.3 | 637.1 | 4152.3 | 7581.2 | 315.8 | -1520.1 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 0 | 110 | 68.95 | 19.6 | 66.9 | 1.0788 | 1.0671 | 1.0672 | 1.0264 | 0 | 0 | 129 | 0 | 1838.3 | 2200.7 | 349.1 | 262 | 87.1 | 1.0402 | 1.0382 | 1 | 1 | 1 | 1 | 1.0436 | 1.0224 | 1.054 | 0.98864 | 0.98816 | 0.99098 | 1.0006 | 2 | 1
p18otc349_dsbg.sav | 7760.3 | 3957.5 | 1107.5 | 1896.8 | 2299.5 | 1706 | 1617.1 | 911.1 | 272.4 | 772.7 | 772.7 | 97.3 | 148.1 | 73.2 | 25.3 | 25.9 | 1915.3 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2113 | -867.1 | -267.9 | 381.4 | 1898.1 | -764 | 734 | 243.5 | 81.1 | -202.7 | 485.9 | 476.4 | -31.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.8 | 1314.1 | 3165.6 | 68.8 | 21.3 | 16.2 | 8.8 | 10 | 10 | 0 | 0.97849 | 1.0005 | 0.99542 | 0.90373 | 0.99705 | 0.90887 | 0.93863 | 0.95841 | 0.98326 | 0.96952 | 0.95231 | 0.95986 | 0.97041 | 0.98193 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 52.1 | 63.4 | 68.1 | 17.3 | 45.2 | 66.3 | 94 | 90.1 | 45.5 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1216.2 | 4965.2 | 29012.3 | 3273.9 | 235.9 | 642.4 | 4152.3 | 7635.3 | 319.7 | -1578.2 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 272.4 | 0 | 55.171 | 19.6 | -41.6 | 1.0782 | 1.0674 | 1.0679 | 1.0262 | 0 | 0 | 129 | 0 | 1706 | 2056.1 | 349.1 | 262 | 87.1 | 1.0061 | 1.0079 | 0.98643 | 0.96659 | 0.98534 | 0.98384 | 0.99324 | 1.0501 | 1.055 | 1.04 | 1.0416 | 1.0332 | 1.0054 | 3 | 2
p18otc349_bloxhcb.sav | 7809 | 3955.6 | 1107.5 | 1896.8 | 2299.8 | 1506.6 | 1617.1 | 795.7 | 358.6 | 759 | 759 | 99.7 | 159.9 | 80.6 | 25.7 | 26.3 | 1910.2 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2110.8 | -714.2 | -400 | 488.4 | 1903.7 | -744.2 | 710 | 218.7 | 85.3 | -206.9 | 490.1 | 481.7 | -34.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.8 | 1289.3 | 3165.6 | 71.2 | 24.4 | 12.5 | 9.1 | 10 | 10 | 0 | 0.971 | 0.98591 | 0.97895 | 0.89282 | 0.98443 | 0.90201 | 0.93081 | 0.95376 | 0.92058 | 0.90184 | 0.9009 | 0.90601 | 0.92765 | 0.97026 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.3 | 73.5 | 67.7 | 60.7 | 81 | 67.6 | 120.7 | 0 | 69.4 | 35.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251.3 | 4930.2 | 29012.3 | 3273.9 | 212.5 | 665.9 | 4152.3 | 7635.3 | 319.1 | -1577.6 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 267 | 91.6 | 55.304 | 19.6 | 49.1 | 1.0779 | 1.0669 | 1.0667 | 1.026 | 0 | 0 | 129 | 0 | 1506.6 | 1945.7 | 349.1 | 262 | 87.1 | 0.99138 | 0.99123 | 0.97452 | 0.95436 | 0.97791 | 0.97564 | 0.98842 | 0.98313 | 0.98138 | 0.98389 | 0.98321 | 0.98769 | 0.99342 | 4 | 3
p18otc349_bloxhcb_s.sav | 7807.7 | 3955.8 | 1107.5 | 1896.8 | 2299.9 | 1505.1 | 1617.1 | 793.7 | 361.2 | 758.9 | 758.9 | 99.6 | 160.6 | 80.8 | 25.7 | 26.2 | 1910.8 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2110.9 | -712.5 | -398.7 | 490.1 | 1903.2 | -744.8 | 710.5 | 219.2 | 84.8 | -206.3 | 489.5 | 481.3 | -33.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.7 | 1289.3 | 3165.6 | 71.1 | 24.4 | 12.5 | 9.1 | 10 | 10 | 0 | 0.97252 | 0.98871 | 0.98251 | 0.89531 | 0.98732 | 0.90361 | 0.93263 | 0.95465 | 0.9368 | 0.94579 | 0.90808 | 0.91354 | 0.93252 | 0.97292 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.3 | 73.4 | 67.7 | 61.1 | 79.8 | 67.5 | 120.6 | 0 | 69.3 | 35.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1250.9 | 4930.7 | 29012.3 | 3273.9 | 212.4 | 666 | 4152.3 | 7635.3 | 318.9 | -1577.4 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 267.7 | 93.5 | 55.181 | 19.6 | 51 | 1.0782 | 1.0671 | 1.0669 | 1.0261 | 0 | 0 | 129 | 0 | 1505.1 | 1944 | 349.1 | 262 | 87.1 | 0.9942 | 0.99484 | 0.97724 | 0.95716 | 0.97964 | 0.97755 | 0.98935 | 1.0004 | 1.0292 | 0.99173 | 0.99138 | 0.99288 | 0.99614 | 5 | 3
p18otc349_blhcoxll.sav | 8093.4 | 3973.1 | 1107.5 | 1896.8 | 2298.9 | 1886.2 | 1617.1 | 735.4 | 370.5 | 741.4 | 741.4 | 98.8 | 157.9 | 79.9 | 25.6 | 26.2 | 1871.3 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2099.3 | -583.7 | -610.3 | 565.7 | 1934.6 | -701.3 | 664.3 | 171.7 | 124 | -245 | 528.2 | 509.9 | -63.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 140.4 | 1279.6 | 3165.6 | 71.6 | 25.6 | 11.1 | 8.3 | 10 | 10 | 0 | 0.96605 | 0.97314 | 0.96587 | 0.85239 | 0.93757 | 0.8658 | 0.8893 | 0.93366 | 0.89363 | 0.87255 | 0.8745 | 0.8783 | 0.90699 | 0.95853 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 63.6 | 77.5 | 72.5 | 66.5 | 95.6 | 23.4 | 0 | 0 | 98.7 | 36.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1296.4 | 4885.3 | 29012.3 | 3273.9 | 191.7 | 686.7 | 4152.3 | 7635.3 | 326.4 | -1584.8 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 272.5 | 98 | 61.166 | 19.6 | 55 | 1.0792 | 1.0726 | 1.0738 | 1.0275 | 0 | 0 | 129 | 0 | 1886.2 | 1886.2 | 349.1 | 262 | 87.1 | 0.97854 | 0.97799 | 0.93039 | 0.90893 | 0.93865 | 0.93213 | 0.96759 | 0.95434 | 0.94951 | 0.95506 | 0.95314 | 0.96569 | 0.98141 | 6 | 4
p18otc349_blhcoxll_s.sav | 8091.8 | 3973.4 | 1107.5 | 1896.8 | 2298.9 | 1884.3 | 1617.1 | 733.3 | 373.5 | 741.4 | 741.4 | 98.7 | 158.6 | 80.1 | 25.6 | 26.1 | 1871.9 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2099.5 | -581.9 | -608.7 | 567.6 | 1934.1 | -702 | 664.9 | 172.3 | 123.3 | -244.4 | 527.6 | 509.4 | -62.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 140.3 | 1279.7 | 3165.6 | 71.6 | 25.5 | 11.1 | 8.3 | 10 | 10 | 0 | 0.9676 | 0.976 | 0.96949 | 0.85503 | 0.94064 | 0.8675 | 0.89125 | 0.93459 | 0.9097 | 0.91566 | 0.8816 | 0.88575 | 0.91176 | 0.96115 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 63.5 | 77.3 | 72.5 | 66.8 | 94.6 | 23.4 | 0 | 0 | 98.7 | 36.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1295.8 | 4886 | 29012.3 | 3273.9 | 191.6 | 686.8 | 4152.3 | 7635.3 | 326.1 | -1584.5 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 273.4 | 100.1 | 61.02 | 19.6 | 57.1 | 1.0794 | 1.0728 | 1.074 | 1.0277 | 0 | 0 | 129 | 0 | 1884.3 | 1884.3 | 349.1 | 262 | 87.1 | 0.98142 | 0.98165 | 0.93328 | 0.91191 | 0.94049 | 0.93417 | 0.96856 | 0.97151 | 0.99642 | 0.96281 | 0.96122 | 0.97077 | 0.98409 | 7 | 4
p18otc349_mpsl.sav | 7623.7 | 4026.9 | 1107.5 | 1896.8 | 2300.2 | 1565.9 | 1617.1 | 791.9 | 359.8 | 758.3 | 758.3 | 99.8 | 160 | 80.7 | 25.7 | 26.3 | 1909.1 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2110.4 | -680.9 | 0 | 536.1 | 1918.4 | -709.4 | 662.8 | 170.3 | 86.5 | -208 | 491.2 | 490.5 | -35.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 132.2 | 1287.8 | 3165.6 | 71.4 | 24.5 | 12.5 | 9.1 | 10 | 10 | 0 | 0.96989 | 0.98339 | 0.9764 | 0.88512 | 0.97552 | 0.8939 | 0.92154 | 0.94763 | 0.91558 | 0.89642 | 0.89507 | 0.89989 | 0.92252 | 0.96632 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.8 | 74 | 68.4 | 61.5 | 83.1 | 69.5 | 101.8 | 96.4 | 53 | 35.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.7 | 4981.8 | 29012.3 | 3273.9 | 255.2 | 623.2 | 4152.3 | 7635.3 | 319.2 | -1577.6 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 267.2 | 92.6 | 56.228 | 19.6 | 50 | 1.078 | 1.0671 | 1.0674 | 1.026 | 0 | 0 | 129 | 0 | 1565.9 | 1942.8 | 349.1 | 262 | 87.1 | 0.98885 | 0.98865 | 0.96612 | 0.94572 | 0.96911 | 0.96592 | 0.98207 | 0.97779 | 0.97548 | 0.97752 | 0.97657 | 0.98223 | 0.98938 | 8 | 5
p18otc349_mpsl_s.sav | 7622.9 | 4026.7 | 1107.5 | 1896.8 | 2300.2 | 1564.7 | 1617.1 | 790 | 362.5 | 758.3 | 758.3 | 99.7 | 160.6 | 80.9 | 25.7 | 26.3 | 1909.8 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2110.6 | -679.8 | 0 | 537.3 | 1917.8 | -710.5 | 663.8 | 171.3 | 85.8 | -207.3 | 490.5 | 490 | -34.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 132.2 | 1287.8 | 3165.6 | 71.3 | 24.5 | 12.5 | 9.1 | 10 | 10 | 0 | 0.97144 | 0.98626 | 0.98003 | 0.88787 | 0.97871 | 0.89579 | 0.9237 | 0.94877 | 0.93192 | 0.94037 | 0.90248 | 0.90767 | 0.92762 | 0.9692 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.7 | 73.9 | 68.3 | 61.9 | 81.9 | 69.4 | 101.6 | 96.3 | 52.9 | 35.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.3 | 4982.2 | 29012.3 | 3273.9 | 254.9 | 623.5 | 4152.3 | 7635.3 | 318.9 | -1577.3 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 268 | 94.4 | 56.078 | 19.6 | 51.9 | 1.0782 | 1.0673 | 1.0676 | 1.0261 | 0 | 0 | 129 | 0 | 1564.7 | 1941.2 | 349.1 | 262 | 87.1 | 0.99173 | 0.99233 | 0.96912 | 0.94881 | 0.97116 | 0.96819 | 0.98325 | 0.99524 | 1.0233 | 0.98562 | 0.98501 | 0.98766 | 0.99233 | 9 | 5
p18otc349_angr1.sav | 7719.8 | 3939.5 | 1107.5 | 1896.8 | 2299.8 | 1655.9 | 1617.1 | 859.9 | 318.6 | 753 | 753 | 103.6 | 178.6 | 89.4 | 26.3 | 26.9 | 1930.7 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2116.1 | -836.6 | -248.3 | 410.3 | 1885.1 | -771.1 | 739.3 | 249 | 64 | -185.7 | 468.9 | 464.9 | -17.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128 | 1292.2 | 3165.6 | 73.5 | 26.3 | 10.4 | 9.2 | 10 | 10 | 0 | 0.96198 | 0.95681 | 0.95093 | 0.90582 | 1.0193 | 0.92452 | 0.95647 | 0.96725 | 0.91069 | 0.89111 | 0.91157 | 0.9172 | 0.93762 | 0.97522 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 122.8 | 61.1 | 52.5 | 65.8 | 65.5 | 92.5 | 89.3 | 44.8 | 35.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1214.9 | 4966.6 | 29012.3 | 3273.9 | 233.2 | 645.2 | 4152.3 | 7635.3 | 314.8 | -1573.3 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 241.6 | 77 | 49.021 | 19.6 | 35 | 1.078 | 1.0675 | 1.0682 | 1.0261 | 0 | 0 | 129 | 0 | 1655.9 | 2001 | 349.1 | 262 | 87.1 | 0.96212 | 0.96286 | 0.98871 | 0.98819 | 1.0023 | 1.0025 | 1.0024 | 0.97257 | 0.96971 | 0.99554 | 0.99535 | 0.99831 | 0.9985 | 10 | 6
p18otc349_angr2.sav | 7719.5 | 3942.8 | 1107.5 | 1896.8 | 2299.8 | 1655.2 | 1617.1 | 854.4 | 324.9 | 754.8 | 754.8 | 103.1 | 176.8 | 88.4 | 26.2 | 26.8 | 1930.9 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2116.2 | -832.6 | -245.2 | 414.4 | 1884.4 | -772.3 | 740.9 | 250.7 | 64 | -185.7 | 468.8 | 464.6 | -17.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127.3 | 1292.9 | 3165.6 | 73.1 | 25.9 | 10.9 | 9.2 | 10 | 10 | 0 | 0.96504 | 0.96712 | 0.96067 | 0.91101 | 1.0254 | 0.92629 | 0.95849 | 0.96792 | 0.91823 | 0.89929 | 0.91382 | 0.91956 | 0.939 | 0.97613 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 94.7 | 0 | 61.7 | 53.1 | 66.5 | 65.5 | 92.4 | 89.3 | 44.7 | 35.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1210.2 | 4971.2 | 29012.3 | 3273.9 | 233 | 645.4 | 4152.3 | 7635.3 | 315 | -1573.5 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 245.9 | 79 | 49.335 | 19.6 | 36.9 | 1.078 | 1.0675 | 1.0682 | 1.0261 | 0 | 0 | 129 | 0 | 1655.2 | 2000 | 349.1 | 262 | 87.1 | 0.97249 | 0.97272 | 0.99438 | 0.99413 | 1.0042 | 1.0047 | 1.0031 | 0.98062 | 0.97861 | 0.998 | 0.99792 | 0.99978 | 0.99943 | 11 | 7
p18otc349_angr12.sav | 7804.8 | 3905.9 | 1107.5 | 1896.8 | 2299.2 | 1765 | 1617.1 | 989.8 | 113.3 | 702.1 | 702.1 | 119.1 | 213.8 | 107.4 | 29.5 | 30.1 | 1904.1 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2110 | -977 | -349.1 | 273.8 | 1910.9 | -733.3 | 694.3 | 202.4 | 80.7 | -201.6 | 484.6 | 481 | -27.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.7 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1720.5 | 212.4 | 1233.8 | 3165.6 | 82.8 | 42.8 | 7.1 | 13.3 | 10 | 10 | 0 | 0.81415 | 0.65155 | 0.63974 | 0.76292 | 0.84977 | 0.87246 | 0.89694 | 0.94376 | 0.64733 | 0.59917 | 0.82388 | 0.82501 | 0.88089 | 0.93784 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 44.2 | 29.5 | 87.6 | 68 | 97.3 | 92.3 | 47.9 | 35.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1232.6 | 4948.9 | 29012.3 | 3273.9 | 241.9 | 636.4 | 4152.3 | 7635.3 | 317.9 | -1576.3 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 102.2 | 11.1 | 31.674 | 19.6 | -31.7 | 1.0728 | 1.0618 | 1.0644 | 1.0228 | 0 | 0 | 129 | 0 | 1765 | 2125.9 | 349.1 | 262 | 87.1 | 0.65517 | 0.64777 | 0.83274 | 0.82381 | 0.94587 | 0.94014 | 0.97806 | 0.69131 | 0.65202 | 0.89978 | 0.89531 | 0.9379 | 0.96022 | 12 | 8
p18otc349_grgr.sav | 7749.6 | 3925.7 | 1107.5 | 1896.8 | 2299.9 | 1696 | 1617.1 | 905.1 | 239.6 | 675.4 | 675.4 | 161.8 | 224.8 | 111 | 35.1 | 35.9 | 1919.3 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2109.9 | -887.6 | -285 | 360.6 | 1896 | -757.6 | 723.2 | 232.3 | 71.6 | -192.9 | 476 | 472 | -22.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -69.6 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 154.6 | 1266.1 | 3165.6 | 90.1 | 61 | 16 | 17.2 | 10 | 10 | 0 | 0.87232 | 0.8772 | 0.86809 | 0.89005 | 1.0007 | 0.93296 | 0.96607 | 0.97369 | 0.85017 | 0.82502 | 0.90207 | 0.90724 | 0.93387 | 0.97119 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 32.5 | 39.6 | 51.7 | 38.8 | 54.2 | 66.4 | 94.2 | 90.4 | 45.9 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1221.6 | 4960.2 | 29012.3 | 3273.9 | 235.6 | 642.8 | 4152.3 | 7635.3 | 313.4 | -1571.9 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 189.8 | 49.8 | 40.407 | 19.6 | 8.1 | 1.0768 | 1.0659 | 1.0672 | 1.0259 | 0 | 0 | 129 | 0 | 1696 | 2046.9 | 349.1 | 262 | 87.1 | 0.88207 | 0.87898 | 0.9715 | 0.97015 | 1.0115 | 1.0126 | 1.0091 | 0.90793 | 0.89779 | 0.98517 | 0.98455 | 0.99431 | 0.99437 | 13 | 9
p18otc349_anpf.sav | 7858.6 | 3963.1 | 1107.5 | 1896.8 | 2298.8 | 1830.8 | 1617.1 | 1057.5 | 96.2 | 765.2 | 765.2 | 93.2 | 141.7 | 71.5 | 24.7 | 25.2 | 1886.6 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2104.9 | -982.9 | -347.6 | 271.2 | 1921.4 | -732.5 | 705.7 | 214 | 109.7 | -231.1 | 514.3 | 497.4 | -53 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 106.7 | 1313.1 | 3165.6 | 65.9 | 17.5 | 20.5 | 9 | 10 | 10 | 0 | 0.99065 | 1.0316 | 1.0216 | 1.1155 | 1.0151 | 1.0811 | 1.1328 | 1.0414 | 0.93908 | 0.92188 | 0.89752 | 0.90246 | 0.92666 | 0.97738 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 34.7 | 42.3 | 0 | 70.2 | 101.9 | 68.6 | 98.5 | 92.8 | 48.2 | 35.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1237.1 | 4944.4 | 29012.3 | 3273.9 | 244.2 | 634.2 | 4152.3 | 7635.3 | 317.3 | -1575.7 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | -13.3 | 109.5 | 72.329 | 19.6 | 66.3 | 1.0786 | 1.0669 | 1.067 | 1.0263 | 0 | 0 | 129 | 0 | 1830.8 | 2196.3 | 349.1 | 262 | 87.1 | 1.0373 | 1.0344 | 1.2175 | 0.98414 | 1.172 | 1.1874 | 1.0793 | 1.0029 | 1.0032 | 0.9802 | 0.97936 | 0.98664 | 1.0007 | 14 | 10
p18otc349_antbdy.sav | 7727.8 | 3944.4 | 1107.5 | 1896.8 | 2299.7 | 1665.7 | 1617.1 | 864.1 | 319.2 | 769.5 | 769.5 | 99.1 | 158.3 | 79.5 | 25.6 | 26.1 | 1927.6 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2116.1 | -841.4 | -251.2 | 406.4 | 1882.4 | -767.2 | 740.7 | 250.4 | 68.3 | -190.1 | 473.3 | 466.2 | -21.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2538.6 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 118.9 | 1301.2 | 3165.6 | 69.9 | 22.7 | 14.6 | 8.7 | 10 | 10 | 0 | 0.97806 | 1.0014 | 0.99406 | 0.92755 | 1.0449 | 0.90463 | 0.93379 | 0.91901 | 0.93869 | 0.92145 | 0.90942 | 0.91495 | 0.9318 | 0.96846 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55 | 66.9 | 56.1 | 57.8 | 72.6 | 65.7 | 92.8 | 89.5 | 44.9 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1209.1 | 4972.3 | 29012.3 | 3273.9 | 233.6 | 644.7 | 4152.3 | 7635.3 | 322 | -1580.6 | 6380.9 | 900 | 3157.3 | 652.9 | 229.7 | 484 | 230.6 | 88.6 | 44.974 | 19.6 | 46.3 | 1.0788 | 1.0681 | 1.0685 | 1.0266 | 0 | 0 | 129 | 0 | 1665.7 | 2011.9 | 349.1 | 262 | 87.1 | 1.007 | 1.0065 | 1.0124 | 1.013 | 0.98075 | 0.97876 | 0.95241 | 1.0025 | 1.0027 | 0.9932 | 0.99291 | 0.99211 | 0.99157 | 15 | 11
p18otc349_brbo_brkp.sav | 7914.3 | 3633.2 | 1107.5 | 1896.8 | 2480.9 | 1585.9 | 1642.1 | 768.4 | 371.6 | 756.3 | 756.3 | 101 | 161.8 | 82.8 | 25.7 | 26.3 | 1910.2 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2112.1 | -1488.8 | -743.8 | -278.9 | 734.3 | -444.8 | 892.6 | 42.9 | 86.4 | -207.9 | 491.1 | 515.9 | -35.2 | 288 | 591 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.2 | 151 | 39 | 59 | 2538.6 | 142.7 | 67.2 | 209.9 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 156.5 | 1275.4 | 3177.4 | 74.1 | 26.2 | 11.4 | 10.1 | 10 | 10 | 0 | 0.94462 | 0.94266 | 0.93482 | 0.79125 | 0.86637 | 0.81733 | 0.83317 | 0.90982 | 0.84726 | 0.82182 | 0.84644 | 0.84878 | 0.89048 | 0.95699 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 66.7 | 81.2 | 77.7 | 73.3 | 115.5 | 73.6 | 110.5 | 104.1 | 59.5 | 39.8 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1308 | 5239.6 | 29377.8 | 3292.5 | 219.1 | -450.3 | 3061.2 | 7635.3 | 340.8 | -1571.1 | 6408.9 | 917.1 | 3216.1 | 665.2 | 233.9 | 490 | 269.4 | 102.2 | 68.668 | 19.6 | 58.3 | 1.0674 | 1.0554 | 1.0556 | 1.0159 | 0 | 0 | 129 | 0 | 1585.9 | 1986.4 | 349.1 | 262 | 87.1 | 0.94789 | 0.94655 | 0.86366 | 0.83991 | 0.8861 | 0.8733 | 0.94289 | 0.90482 | 0.8943 | 0.92441 | 0.9211 | 0.94812 | 0.97983 | 16 | 12
p18otc349_brbo_brkp_s.sav | 7904.4 | 3631.4 | 1107.5 | 1896.8 | 2479.7 | 1577 | 1641.6 | 757.5 | 386.4 | 756.9 | 756.9 | 100.8 | 163.6 | 83.4 | 25.7 | 26.3 | 1913.6 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2113 | -1479 | -737.2 | -269.6 | 732.8 | -449 | 892.8 | 45.9 | 83.2 | -204.7 | 487.9 | 513.8 | -32.8 | 288 | 590.5 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.2 | 151 | 39 | 59 | 2538.6 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 155.7 | 1276.1 | 3177.2 | 74.2 | 26.3 | 11.2 | 10.1 | 10 | 10 | 0 | 0.94983 | 0.95233 | 0.94495 | 0.82526 | 0.90603 | 0.83833 | 0.85757 | 0.92045 | 0.87052 | 0.87187 | 0.85857 | 0.86155 | 0.89926 | 0.96263 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 66.6 | 81.1 | 77.8 | 73 | 113.5 | 73.3 | 110.1 | 103.7 | 59.2 | 39.8 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1303.6 | 5239.9 | 29373.7 | 3292.5 | 217.7 | -449.2 | 3060.9 | 7635.3 | 339.3 | -1569.8 | 6408.9 | 916.2 | 3215.6 | 664.9 | 233.9 | 490 | 281.3 | 105.2 | 67.662 | 19.6 | 61.4 | 1.0688 | 1.0568 | 1.0568 | 1.017 | 0 | 0 | 129 | 0 | 1577 | 1976.4 | 349.1 | 262 | 87.1 | 0.95762 | 0.95681 | 0.90078 | 0.87835 | 0.90887 | 0.89887 | 0.9539 | 0.92966 | 0.94877 | 0.93766 | 0.93496 | 0.95746 | 0.9856 | 17 | 12
p18otc349_brgo_brkp.sav | 7912.1 | 3619.9 | 1107.5 | 1896.8 | 2485.9 | 1576.5 | 1642.4 | 759.8 | 367.6 | 755.7 | 755.7 | 102.5 | 162.1 | 83.6 | 25.9 | 26.5 | 1911.9 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.2 | 2112.7 | -1501.9 | -754.1 | -281.2 | 717.7 | -428 | 897.4 | 37.8 | 84.4 | -205.9 | 489.1 | 512.9 | -33.5 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2538.6 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 171.3 | 1260.8 | 3177.6 | 74.6 | 27 | 10.6 | 10.3 | 10 | 10 | 0 | 0.93365 | 0.92335 | 0.91365 | 0.75233 | 0.8208 | 0.78407 | 0.79423 | 0.89026 | 0.7932 | 0.762 | 0.79143 | 0.79073 | 0.84824 | 0.9316 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 69.5 | 84.7 | 80 | 82.3 | 138.5 | 73.7 | 110.9 | 104.5 | 59.9 | 40 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1312.3 | 5243.2 | 29385.6 | 3292.5 | 228.6 | -458.7 | 3062.3 | 7635.3 | 350 | -1579.7 | 6409.4 | 917.1 | 3217.8 | 665.4 | 234.1 | 490 | 262.5 | 105 | 72.976 | 19.6 | 60 | 1.0652 | 1.0532 | 1.0539 | 1.0141 | 0 | 0 | 129 | 0 | 1576.5 | 1977.4 | 349.1 | 262 | 87.1 | 0.92848 | 0.92511 | 0.82118 | 0.79573 | 0.85004 | 0.83248 | 0.92262 | 0.84709 | 0.82921 | 0.86434 | 0.85811 | 0.90314 | 0.95383 | 18 | 13
p18otc349_brgo_brkp_s.sav | 7903.7 | 3620.7 | 1107.5 | 1896.8 | 2484.4 | 1567.2 | 1642.4 | 748 | 383.4 | 756.1 | 756.1 | 102.3 | 163.9 | 84.2 | 25.9 | 26.5 | 1915.1 | 330 | 330 | 814.6 | 815 | 2289.6 | 141 | 2128.1 | 2113.5 | -1491.2 | -746.6 | -271 | 716.8 | -433.3 | 897.5 | 41.5 | 81.3 | -202.9 | 486 | 511 | -31.2 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2538.6 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.2 | 1745.2 | 170.2 | 1261.7 | 3177.5 | 74.7 | 27.1 | 10.5 | 10.2 | 10 | 10 | 0 | 0.93885 | 0.93296 | 0.92376 | 0.786 | 0.86024 | 0.80524 | 0.81907 | 0.90116 | 0.8167 | 0.81121 | 0.80408 | 0.80411 | 0.85739 | 0.9377 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 69.5 | 84.6 | 80 | 81.6 | 136.6 | 73.5 | 110.4 | 104.1 | 59.6 | 40 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1308 | 5246.5 | 29384.6 | 3292.5 | 226.9 | -457.1 | 3062.2 | 7635.3 | 348.1 | -1577.9 | 6409.3 | 917.1 | 3217.3 | 665.3 | 234.1 | 490 | 274.7 | 108.6 | 71.87 | 19.6 | 63.7 | 1.0666 | 1.0548 | 1.0553 | 1.0152 | 0 | 0 | 129 | 0 | 1567.2 | 1967 | 349.1 | 262 | 87.1 | 0.93814 | 0.93535 | 0.85793 | 0.83396 | 0.87299 | 0.85852 | 0.93391 | 0.87219 | 0.88276 | 0.87815 | 0.87263 | 0.91288 | 0.96008 | 19 | 13
p18otc351.sav | 7712.3 | 3949.3 | 1107.5 | 1896.8 | 2300 | 1644.4 | 1617.1 | 838.4 | 351.3 | 768.8 | 768.8 | 99.3 | 160 | 80.1 | 25.6 | 26.2 | 1928.8 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2115.2 | -817.1 | -233.8 | 430.3 | 1879.6 | -776.2 | 741 | 251.9 | 65.3 | -187.1 | 470.3 | 460.8 | -19.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.7 | 1304.6 | 3173.9 | 70.3 | 23.2 | 14 | 8.7 | 10 | 10 | 0 | 0.979 | 1.0016 | 0.99686 | 0.92028 | 1.0364 | 0.92415 | 0.95605 | 0.96577 | 0.94692 | 0.93035 | 0.92199 | 0.92812 | 0.94379 | 0.97901 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.3 | 69.7 | 65.1 | 56.1 | 69.2 | 65.3 | 91.9 | 89 | 44.3 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1205.9 | 4977.1 | 29013.9 | 3273.9 | 232.3 | 646.2 | 4152.4 | 7635.3 | 314.1 | -1584 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 264.8 | 86.5 | 51.987 | 21 | 44.4 | 1.0791 | 1.0686 | 1.0688 | 1.0268 | 0 | 0 | 129 | 0 | 1644.4 | 1987.6 | 351.3 | 264.8 | 86.5 | 1.0016 | 0.99686 | 0.92028 | 1.0364 | 0.92415 | 0.95605 | 0.96577 | 0.94692 | 0.93035 | 0.92199 | 0.92812 | 0.94379 | 0.97901 | 0 | 0
p18otc351_amps.sav | 7874.3 | 4017.7 | 1107.5 | 1896.8 | 2298.8 | 1846.1 | 1617.1 | 1071.1 | 107.9 | 766.2 | 766.2 | 92.4 | 140.6 | 70.6 | 24.6 | 25.1 | 1885.8 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2103.5 | -942.9 | -315.1 | 312.6 | 1910.1 | -745.9 | 718 | 228 | 109 | -230.3 | 513.5 | 489.6 | -52.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.6 | 1337.5 | 3173.9 | 65.5 | 17 | 21 | 9 | 10 | 10 | 0 | 0.99471 | 1.0392 | 1.0313 | 0.92028 | 1.0364 | 0.92415 | 0.95605 | 1.007 | 0.95199 | 0.93582 | 0.90489 | 0.9102 | 0.93081 | 0.9772 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 33.6 | 40.9 | 0 | 68.1 | 96.2 | 68.4 | 97.8 | 92.2 | 47.5 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1239.5 | 4943.6 | 29013.9 | 3273.9 | 241.4 | 637.1 | 4152.4 | 7581.2 | 314 | -1529.8 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 0 | 107.9 | 69.286 | 21 | 64.8 | 1.0791 | 1.0673 | 1.0672 | 1.0266 | 0 | 0 | 129 | 0 | 1846.1 | 2209.2 | 351.3 | 264.8 | 86.5 | 1.0375 | 1.0345 | 1 | 1 | 1 | 1 | 1.0427 | 1.0054 | 1.0059 | 0.98145 | 0.98069 | 0.98625 | 0.99815 | 1 | 1
p18otc351_amps_s.sav | 7873.2 | 4017.8 | 1107.5 | 1896.8 | 2298.8 | 1844.8 | 1617.1 | 1069.4 | 109.9 | 766.2 | 766.2 | 92.3 | 141.1 | 70.8 | 24.6 | 25.1 | 1886.3 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2103.6 | -941.5 | -314.1 | 313.9 | 1909.8 | -746.3 | 718.4 | 228.4 | 108.5 | -229.8 | 513 | 489.3 | -52.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.7 | 1337.4 | 3173.9 | 65.5 | 17 | 21 | 8.9 | 10 | 10 | 0 | 0.99605 | 1.0417 | 1.0345 | 0.92028 | 1.0364 | 0.92415 | 0.95605 | 1.0073 | 0.96795 | 0.98027 | 0.91188 | 0.91752 | 0.93549 | 0.97972 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 33.6 | 41 | 0 | 68.4 | 95.5 | 68.3 | 97.8 | 92.2 | 47.5 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1239.2 | 4944 | 29013.9 | 3273.9 | 241.3 | 637.2 | 4152.4 | 7581.2 | 313.8 | -1529.6 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 0 | 109.9 | 69.184 | 21 | 66.9 | 1.0793 | 1.0675 | 1.0673 | 1.0267 | 0 | 0 | 129 | 0 | 1844.8 | 2207.8 | 351.3 | 264.8 | 86.5 | 1.04 | 1.0377 | 1 | 1 | 1 | 1 | 1.043 | 1.0222 | 1.0537 | 0.98903 | 0.98858 | 0.99121 | 1.0007 | 2 | 1
p18otc351_dsbg.sav | 7764.9 | 3962.6 | 1107.5 | 1896.8 | 2299.5 | 1710.1 | 1617.1 | 915.3 | 274.8 | 772 | 772 | 96.6 | 147.3 | 72.6 | 25.2 | 25.8 | 1911.4 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2110.7 | -867.7 | -267.8 | 381.8 | 1896 | -764.1 | 729.1 | 239.5 | 83.3 | -204.9 | 488.1 | 474 | -33 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.1 | 1323 | 3173.9 | 68.5 | 21 | 16.5 | 8.7 | 10 | 10 | 0 | 0.98205 | 1.007 | 1.0038 | 0.90739 | 1.0013 | 0.91029 | 0.94026 | 0.95896 | 0.99214 | 0.97905 | 0.95244 | 0.95999 | 0.97054 | 0.98205 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 51.2 | 62.3 | 68.4 | 17.2 | 45.2 | 66.4 | 94.1 | 90.2 | 45.6 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1216.8 | 4966.3 | 29013.9 | 3273.9 | 235.9 | 642.6 | 4152.4 | 7635.3 | 318 | -1587.9 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 274.8 | 0 | 55.247 | 21 | -41.6 | 1.0786 | 1.0677 | 1.0681 | 1.0264 | 0 | 0 | 129 | 0 | 1710.1 | 2060.6 | 351.3 | 264.8 | 86.5 | 1.0053 | 1.007 | 0.98599 | 0.96614 | 0.985 | 0.98348 | 0.99295 | 1.0478 | 1.0523 | 1.033 | 1.0343 | 1.0283 | 1.0031 | 3 | 2
p18otc351_bloxhcb.sav | 7814.3 | 3961.7 | 1107.5 | 1896.8 | 2299.9 | 1511.4 | 1617.1 | 800.6 | 361.3 | 758.2 | 758.2 | 98.8 | 159.3 | 79.9 | 25.6 | 26.1 | 1906.2 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2108.4 | -714.3 | -399.7 | 489.2 | 1901.7 | -744.4 | 705.2 | 215 | 87.8 | -209.3 | 492.5 | 479.4 | -36.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129 | 1299.3 | 3173.9 | 70.8 | 24 | 12.9 | 9 | 10 | 10 | 0 | 0.97528 | 0.9936 | 0.98883 | 0.89728 | 0.98959 | 0.90389 | 0.93295 | 0.95465 | 0.93216 | 0.91439 | 0.90776 | 0.9132 | 0.93256 | 0.97278 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.2 | 72.1 | 68 | 59.6 | 78.2 | 67.6 | 120.8 | 0 | 69.4 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251.9 | 4931.3 | 29013.9 | 3273.9 | 212.4 | 666.1 | 4152.4 | 7635.3 | 317.2 | -1587.1 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 269.9 | 91.4 | 55.396 | 21 | 49 | 1.0785 | 1.0673 | 1.067 | 1.0263 | 0 | 0 | 129 | 0 | 1511.4 | 1950.9 | 351.3 | 264.8 | 86.5 | 0.99197 | 0.99194 | 0.97501 | 0.95486 | 0.97808 | 0.97584 | 0.98849 | 0.98441 | 0.98284 | 0.98457 | 0.98392 | 0.9881 | 0.99364 | 4 | 3
p18otc351_bloxhcb_s.sav | 7813 | 3961.9 | 1107.5 | 1896.8 | 2299.9 | 1509.9 | 1617.1 | 798.6 | 363.9 | 758.1 | 758.1 | 98.8 | 159.9 | 80.2 | 25.6 | 26.1 | 1906.8 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2108.5 | -712.7 | -398.4 | 490.8 | 1901.3 | -745 | 705.7 | 215.5 | 87.2 | -208.7 | 491.9 | 479 | -35.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129 | 1299.3 | 3173.9 | 70.8 | 24 | 12.9 | 9 | 10 | 10 | 0 | 0.97678 | 0.99637 | 0.99235 | 0.89975 | 0.99245 | 0.90547 | 0.93476 | 0.95553 | 0.94844 | 0.95869 | 0.91498 | 0.92077 | 0.93747 | 0.97546 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 59.2 | 72 | 68 | 60.1 | 77 | 67.6 | 120.7 | 0 | 69.4 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251.4 | 4931.7 | 29013.9 | 3273.9 | 212.3 | 666.2 | 4152.4 | 7635.3 | 317 | -1586.9 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 270.7 | 93.2 | 55.275 | 21 | 50.8 | 1.0787 | 1.0676 | 1.0671 | 1.0265 | 0 | 0 | 129 | 0 | 1509.9 | 1949.2 | 351.3 | 264.8 | 86.5 | 0.99474 | 0.99548 | 0.97769 | 0.95762 | 0.97979 | 0.97773 | 0.9894 | 1.0016 | 1.0305 | 0.9924 | 0.99208 | 0.9933 | 0.99637 | 5 | 3
p18otc351_blhcoxll.sav | 8098.4 | 3979.1 | 1107.5 | 1896.8 | 2299 | 1891 | 1617.1 | 739.8 | 373.9 | 740.6 | 740.6 | 97.9 | 157.3 | 79.3 | 25.5 | 26 | 1867.2 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2096.9 | -583.3 | -609.8 | 567 | 1932.6 | -701.6 | 659.7 | 168.1 | 126.4 | -247.5 | 530.7 | 507.6 | -65.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.6 | 1289.7 | 3173.9 | 71.3 | 25.2 | 11.5 | 8.2 | 10 | 10 | 0 | 0.97055 | 0.98118 | 0.97619 | 0.85694 | 0.94285 | 0.86756 | 0.89132 | 0.93446 | 0.90595 | 0.88596 | 0.88176 | 0.88592 | 0.91213 | 0.9612 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 62.4 | 76 | 72.8 | 65.5 | 93 | 23.4 | 0 | 0 | 98.8 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1297.1 | 4886.3 | 29013.9 | 3273.9 | 191.5 | 687 | 4152.4 | 7635.3 | 324.4 | -1594.2 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 275.6 | 98.3 | 61.251 | 21 | 55.4 | 1.0798 | 1.0731 | 1.0741 | 1.0279 | 0 | 0 | 129 | 0 | 1891 | 1891 | 351.3 | 264.8 | 86.5 | 0.97957 | 0.97927 | 0.93117 | 0.90976 | 0.93876 | 0.93229 | 0.96758 | 0.95673 | 0.95229 | 0.95637 | 0.95453 | 0.96645 | 0.98181 | 6 | 4
p18otc351_blhcoxll_s.sav | 8096.9 | 3979.4 | 1107.5 | 1896.8 | 2299 | 1889.1 | 1617.1 | 737.6 | 376.7 | 740.5 | 740.5 | 97.8 | 158 | 79.5 | 25.5 | 26 | 1867.9 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2097.1 | -581.5 | -608.2 | 568.8 | 1932.1 | -702.3 | 660.3 | 168.7 | 125.8 | -246.9 | 530 | 507.2 | -64.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.5 | 1289.7 | 3173.9 | 71.3 | 25.2 | 11.5 | 8.2 | 10 | 10 | 0 | 0.97204 | 0.98395 | 0.9797 | 0.85953 | 0.94586 | 0.86923 | 0.89324 | 0.93538 | 0.92204 | 0.9294 | 0.88889 | 0.89341 | 0.91694 | 0.96384 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 62.3 | 75.9 | 72.8 | 65.8 | 91.9 | 23.4 | 0 | 0 | 98.7 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1296.5 | 4886.9 | 29013.9 | 3273.9 | 191.4 | 687.1 | 4152.4 | 7635.3 | 324.1 | -1594 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 276.4 | 100.3 | 61.108 | 21 | 57.5 | 1.08 | 1.0733 | 1.0742 | 1.028 | 0 | 0 | 129 | 0 | 1889.1 | 1889.1 | 351.3 | 264.8 | 86.5 | 0.98234 | 0.98279 | 0.93399 | 0.91267 | 0.94057 | 0.9343 | 0.96853 | 0.97372 | 0.99898 | 0.9641 | 0.9626 | 0.97155 | 0.9845 | 7 | 4
p18otc351_mpsl.sav | 7629.1 | 4033 | 1107.5 | 1896.8 | 2300.3 | 1570.9 | 1617.1 | 796.8 | 362.6 | 757.5 | 757.5 | 98.9 | 159.3 | 80 | 25.6 | 26.2 | 1905.1 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2108.1 | -681.2 | 0 | 536.8 | 1916.5 | -709.9 | 658.3 | 166.8 | 88.8 | -210.3 | 493.5 | 488.2 | -37 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.4 | 1297.8 | 3173.9 | 71 | 24.2 | 12.9 | 9 | 10 | 10 | 0 | 0.97422 | 0.99118 | 0.98639 | 0.88979 | 0.98092 | 0.89601 | 0.92395 | 0.94875 | 0.92739 | 0.90922 | 0.90221 | 0.90739 | 0.9277 | 0.96909 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.6 | 72.6 | 68.7 | 60.5 | 80.3 | 69.5 | 101.8 | 96.4 | 53 | 35.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1200.1 | 4982.9 | 29013.9 | 3273.9 | 255.1 | 623.5 | 4152.4 | 7635.3 | 317.2 | -1587 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 270.2 | 92.4 | 56.303 | 21 | 49.9 | 1.0786 | 1.0676 | 1.0677 | 1.0263 | 0 | 0 | 129 | 0 | 1570.9 | 1948 | 351.3 | 264.8 | 86.5 | 0.98956 | 0.9895 | 0.96687 | 0.9465 | 0.96955 | 0.96642 | 0.98238 | 0.97937 | 0.97729 | 0.97855 | 0.97767 | 0.98295 | 0.98987 | 8 | 5
p18otc351_mpsl_s.sav | 7628.3 | 4032.7 | 1107.5 | 1896.8 | 2300.3 | 1569.7 | 1617.1 | 794.9 | 365.2 | 757.5 | 757.5 | 98.9 | 160 | 80.3 | 25.6 | 26.1 | 1905.8 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2108.3 | -680.1 | 0 | 538 | 1915.9 | -710.9 | 659.3 | 167.8 | 88.1 | -209.6 | 492.8 | 487.7 | -36.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.4 | 1297.8 | 3173.9 | 71 | 24.1 | 12.9 | 9 | 10 | 10 | 0 | 0.97577 | 0.99405 | 0.99001 | 0.89253 | 0.9841 | 0.8979 | 0.92612 | 0.94989 | 0.94385 | 0.9536 | 0.90969 | 0.91523 | 0.93284 | 0.97199 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 59.5 | 72.5 | 68.7 | 60.9 | 79.1 | 69.5 | 101.7 | 96.3 | 52.9 | 35.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.8 | 4983.3 | 29013.9 | 3273.9 | 254.7 | 623.8 | 4152.4 | 7635.3 | 316.9 | -1586.7 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 271 | 94.2 | 56.154 | 21 | 51.8 | 1.0788 | 1.0678 | 1.0678 | 1.0265 | 0 | 0 | 129 | 0 | 1569.7 | 1946.4 | 351.3 | 264.8 | 86.5 | 0.99242 | 0.99313 | 0.96985 | 0.94956 | 0.9716 | 0.96869 | 0.98356 | 0.99676 | 1.025 | 0.98666 | 0.98611 | 0.9884 | 0.99283 | 9 | 5
p18otc351_angr1.sav | 7724.7 | 3946 | 1107.5 | 1896.8 | 2299.8 | 1660.2 | 1617.1 | 863.9 | 322.7 | 752.2 | 752.2 | 102.7 | 178.2 | 88.8 | 26.2 | 26.8 | 1926.9 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2113.7 | -835.9 | -247.3 | 411.9 | 1882.9 | -771.6 | 734.9 | 245.6 | 66.3 | -187.9 | 471.1 | 462.5 | -19.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.9 | 1302.5 | 3173.9 | 73.1 | 25.8 | 10.9 | 9.1 | 10 | 10 | 0 | 0.96745 | 0.96814 | 0.9643 | 0.91276 | 1.0275 | 0.92775 | 0.96015 | 0.9688 | 0.92493 | 0.90656 | 0.91916 | 0.92515 | 0.94301 | 0.97804 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 120.3 | 61.5 | 51.4 | 62.8 | 65.6 | 92.6 | 89.4 | 44.8 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1215 | 4968.1 | 29013.9 | 3273.9 | 233 | 645.5 | 4152.4 | 7635.3 | 312.9 | -1582.9 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 245.7 | 77 | 49.125 | 21 | 35.1 | 1.0786 | 1.068 | 1.0685 | 1.0265 | 0 | 0 | 129 | 0 | 1660.2 | 2005.7 | 351.3 | 264.8 | 86.5 | 0.96656 | 0.96734 | 0.99183 | 0.99145 | 1.0039 | 1.0043 | 1.0031 | 0.97678 | 0.97443 | 0.99693 | 0.9968 | 0.99917 | 0.99901 | 10 | 6
p18otc351_angr2.sav | 7724.3 | 3949 | 1107.5 | 1896.8 | 2299.8 | 1659.5 | 1617.1 | 858.6 | 328.7 | 754 | 754 | 102.1 | 176.4 | 87.8 | 26.1 | 26.7 | 1927.1 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2113.8 | -832.1 | -244.4 | 415.8 | 1882.2 | -772.7 | 736.4 | 247.2 | 66.2 | -187.9 | 471.1 | 462.2 | -19.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.3 | 1303.1 | 3173.9 | 72.7 | 25.4 | 11.3 | 9.1 | 10 | 10 | 0 | 0.97026 | 0.97773 | 0.97334 | 0.91744 | 1.033 | 0.92925 | 0.96185 | 0.96934 | 0.93185 | 0.91405 | 0.92119 | 0.92728 | 0.94425 | 0.97886 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 92.9 | 0 | 62.1 | 52 | 63.4 | 65.5 | 92.5 | 89.3 | 44.7 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1210.6 | 4972.5 | 29013.9 | 3273.9 | 232.9 | 645.6 | 4152.4 | 7635.3 | 313.1 | -1583 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 249.8 | 78.9 | 49.446 | 21 | 36.9 | 1.0786 | 1.068 | 1.0685 | 1.0265 | 0 | 0 | 129 | 0 | 1659.5 | 2004.6 | 351.3 | 264.8 | 86.5 | 0.97613 | 0.97641 | 0.99691 | 0.99678 | 1.0055 | 1.0061 | 1.0037 | 0.98408 | 0.98248 | 0.99913 | 0.99909 | 1.0005 | 0.99985 | 11 | 7
p18otc351_angr12.sav | 7792.6 | 3910.9 | 1107.5 | 1896.8 | 2299.4 | 1748.2 | 1617.1 | 967.1 | 142.8 | 693.1 | 693.1 | 119.1 | 229 | 113.7 | 29.2 | 29.8 | 1907 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2107.3 | -957.5 | -335 | 293.5 | 1905.3 | -739.1 | 694.9 | 204.3 | 77.9 | -199 | 482 | 475.8 | -26.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.6 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1744.2 | 192.9 | 1237.6 | 3173.9 | 83.3 | 40.5 | 6.3 | 13 | 10 | 10 | 0 | 0.85205 | 0.73059 | 0.72083 | 0.81556 | 0.91251 | 0.90153 | 0.93025 | 0.95863 | 0.72255 | 0.68242 | 0.85672 | 0.8596 | 0.9039 | 0.95152 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 44.4 | 29.3 | 71.9 | 67.6 | 96.7 | 91.9 | 47.5 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1227.2 | 4955.9 | 29013.9 | 3273.9 | 239.9 | 638.6 | 4152.4 | 7635.3 | 313.1 | -1583 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 124 | 18.8 | 32.606 | 21 | -23.5 | 1.0751 | 1.0641 | 1.0659 | 1.0244 | 0 | 0 | 129 | 0 | 1748.2 | 2107.2 | 351.3 | 264.8 | 86.5 | 0.72939 | 0.7231 | 0.88621 | 0.88049 | 0.97552 | 0.97301 | 0.99261 | 0.76305 | 0.73351 | 0.92921 | 0.92617 | 0.95773 | 0.97192 | 12 | 8
p18otc351_grgr.sav | 7753 | 3934.2 | 1107.5 | 1896.8 | 2300 | 1698.4 | 1617.1 | 906.3 | 249.9 | 674.2 | 674.2 | 160.6 | 226.2 | 111.1 | 34.7 | 35.5 | 1916.5 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2107.7 | -882.9 | -280.9 | 366.2 | 1893 | -759.4 | 720.2 | 230.3 | 73 | -194.4 | 477.5 | 469 | -24.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -69.6 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149.9 | 1279 | 3173.9 | 89.9 | 59.4 | 14.9 | 16.7 | 10 | 10 | 0 | 0.89119 | 0.90192 | 0.8952 | 0.9056 | 1.0191 | 0.94075 | 0.97492 | 0.97749 | 0.87598 | 0.8533 | 0.9137 | 0.91943 | 0.94199 | 0.97573 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 31.5 | 38.4 | 52.3 | 38 | 49.6 | 66.4 | 94.2 | 90.3 | 45.8 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1221.1 | 4962.3 | 29013.9 | 3273.9 | 235.2 | 643.3 | 4152.4 | 7635.3 | 311.3 | -1581.2 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 198.2 | 51.8 | 40.703 | 21 | 10.1 | 1.0777 | 1.0667 | 1.0676 | 1.0265 | 0 | 0 | 129 | 0 | 1698.4 | 2049.2 | 351.3 | 264.8 | 86.5 | 0.90044 | 0.89802 | 0.98405 | 0.98331 | 1.018 | 1.0197 | 1.0121 | 0.92508 | 0.91718 | 0.99101 | 0.99064 | 0.99809 | 0.99665 | 13 | 9
p18otc351_anpf.sav | 7865.1 | 3969.1 | 1107.5 | 1896.8 | 2298.8 | 1837.3 | 1617.1 | 1064.7 | 96.3 | 764.5 | 764.5 | 92.3 | 140.5 | 70.6 | 24.6 | 25.1 | 1882.2 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2102.4 | -984.8 | -348.5 | 270.3 | 1919.7 | -732.2 | 700.5 | 209.8 | 112.5 | -233.9 | 517.1 | 495.4 | -55.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105 | 1323.1 | 3173.9 | 65.6 | 17.1 | 20.9 | 8.9 | 10 | 10 | 0 | 0.99452 | 1.0388 | 1.0308 | 1.1159 | 1.0155 | 1.0814 | 1.1332 | 1.0418 | 0.94965 | 0.9333 | 0.90415 | 0.90942 | 0.9314 | 0.97981 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 33.8 | 41.2 | 0 | 69.3 | 99.4 | 68.7 | 98.7 | 92.9 | 48.3 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1238.3 | 4944.8 | 29013.9 | 3273.9 | 244.3 | 634.2 | 4152.4 | 7635.3 | 315.2 | -1585.2 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | -13.2 | 109.5 | 72.559 | 21 | 66.4 | 1.0791 | 1.0673 | 1.0672 | 1.0266 | 0 | 0 | 129 | 0 | 1837.3 | 2203.3 | 351.3 | 264.8 | 86.5 | 1.0371 | 1.034 | 1.2125 | 0.97989 | 1.1702 | 1.1853 | 1.0787 | 1.0029 | 1.0032 | 0.98065 | 0.97985 | 0.98687 | 1.0008 | 14 | 10
p18otc351_antbdy.sav | 7733.3 | 3950.3 | 1107.5 | 1896.8 | 2299.8 | 1671 | 1617.1 | 869.5 | 321.2 | 768.8 | 768.8 | 98.3 | 157.3 | 78.7 | 25.5 | 26 | 1923.5 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2113.7 | -842.2 | -251.2 | 406.6 | 1880.4 | -767.3 | 735.8 | 246.5 | 70.8 | -192.5 | 475.7 | 463.9 | -23.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2536.9 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 117.2 | 1311.1 | 3173.9 | 69.6 | 22.4 | 15 | 8.7 | 10 | 10 | 0 | 0.98203 | 1.0087 | 1.0033 | 0.93338 | 1.0518 | 0.90899 | 0.93876 | 0.92245 | 0.94909 | 0.93269 | 0.91594 | 0.92177 | 0.93658 | 0.97099 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 53.9 | 65.7 | 56.3 | 56.8 | 69.7 | 65.8 | 92.9 | 89.5 | 44.9 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1209.8 | 4973.2 | 29013.9 | 3273.9 | 233.6 | 644.9 | 4152.4 | 7635.3 | 320.2 | -1590.3 | 6369.4 | 900 | 3158.9 | 653.1 | 248.2 | 454 | 233.2 | 88 | 44.956 | 21 | 45.8 | 1.0793 | 1.0686 | 1.0687 | 1.0269 | 0 | 0 | 129 | 0 | 1671 | 2017.5 | 351.3 | 264.8 | 86.5 | 1.007 | 1.0065 | 1.0142 | 1.0149 | 0.9836 | 0.98191 | 0.95515 | 1.0023 | 1.0025 | 0.99344 | 0.99316 | 0.99236 | 0.99181 | 15 | 11
p18otc351_brbo_brkp.sav | 7918.3 | 3640.6 | 1107.5 | 1896.8 | 2480.1 | 1590.4 | 1642.1 | 772.5 | 376 | 755.6 | 755.6 | 100 | 161.4 | 82.2 | 25.6 | 26.2 | 1906.6 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.4 | 2109.8 | -1486.3 | -741.4 | -275.7 | 733 | -445 | 888.6 | 40.7 | 88.5 | -210 | 493.1 | 513.8 | -36.9 | 288 | 591 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.2 | 151 | 39 | 59 | 2536.9 | 142.6 | 67.2 | 209.8 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 154.2 | 1285.9 | 3185.8 | 73.8 | 25.8 | 11.8 | 10 | 10 | 10 | 0 | 0.94994 | 0.95183 | 0.94646 | 0.79696 | 0.87304 | 0.81977 | 0.83603 | 0.91105 | 0.86156 | 0.83753 | 0.8548 | 0.85759 | 0.89638 | 0.96024 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 65.2 | 79.4 | 78 | 72.3 | 112.9 | 73.6 | 110.5 | 104 | 59.5 | 39.1 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1307.7 | 5241 | 29378.8 | 3292.5 | 218.9 | -449.9 | 3061.3 | 7635.3 | 338.3 | -1577.2 | 6400.2 | 917.1 | 3217.4 | 665.3 | 252.8 | 462.4 | 272.8 | 103.2 | 68.65 | 21 | 59.5 | 1.0682 | 1.0561 | 1.0561 | 1.0165 | 0 | 0 | 129 | 0 | 1590.4 | 1991 | 351.3 | 264.8 | 86.5 | 0.95027 | 0.94944 | 0.866 | 0.8424 | 0.88705 | 0.87446 | 0.94334 | 0.90985 | 0.90023 | 0.92712 | 0.92401 | 0.94977 | 0.98083 | 16 | 12
p18otc351_brbo_brkp_s.sav | 7908.3 | 3638.3 | 1107.5 | 1896.8 | 2478.9 | 1581 | 1641.2 | 761.6 | 390.9 | 756.2 | 756.2 | 99.9 | 163.2 | 82.8 | 25.6 | 26.2 | 1910.1 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2110.8 | -1476.9 | -735 | -266.4 | 731.6 | -449.2 | 888.6 | 43.8 | 85.2 | -206.7 | 489.9 | 511.7 | -34.4 | 288 | 590.5 | 468.8 | 386.8 | 195.1 | 78 | 308.8 | -76.8 | 151 | 39 | 59 | 2536.9 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 153.5 | 1286.7 | 3185.6 | 73.8 | 25.8 | 11.6 | 10 | 10 | 10 | 0 | 0.95511 | 0.96146 | 0.95651 | 0.83109 | 0.91281 | 0.84085 | 0.86049 | 0.9217 | 0.88484 | 0.88791 | 0.86699 | 0.8704 | 0.90522 | 0.9659 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 65.3 | 79.5 | 78.1 | 72 | 110.9 | 73.3 | 110.1 | 103.7 | 59.2 | 39.1 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1303.3 | 5241 | 29374.5 | 3292.5 | 217.4 | -449.1 | 3060.8 | 7635.3 | 336.9 | -1576 | 6400.2 | 916.2 | 3216.9 | 664.9 | 252.8 | 462.4 | 284.8 | 106.1 | 67.646 | 21 | 62.4 | 1.0696 | 1.0576 | 1.0573 | 1.0176 | 0 | 0 | 129 | 0 | 1581 | 1980.6 | 351.3 | 264.8 | 86.5 | 0.95989 | 0.95952 | 0.90308 | 0.88078 | 0.90986 | 0.90005 | 0.95437 | 0.93444 | 0.95438 | 0.94035 | 0.93781 | 0.95913 | 0.98661 | 17 | 12
p18otc351_brgo_brkp.sav | 7915.8 | 3627.4 | 1107.5 | 1896.8 | 2484.8 | 1580.7 | 1642.4 | 763.4 | 373.2 | 755 | 755 | 101.5 | 161.8 | 83.1 | 25.8 | 26.4 | 1908.6 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2110.5 | -1498.7 | -751.2 | -277.1 | 716.5 | -428.7 | 893.1 | 36.1 | 86.3 | -207.7 | 490.9 | 510.7 | -35 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2536.9 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 168.8 | 1271.8 | 3186.1 | 74.3 | 26.5 | 11.1 | 10.1 | 10 | 10 | 0 | 0.93944 | 0.93324 | 0.92613 | 0.75883 | 0.82842 | 0.78703 | 0.79772 | 0.89184 | 0.80914 | 0.77973 | 0.80066 | 0.80049 | 0.85466 | 0.93526 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 68 | 82.7 | 80.4 | 81.3 | 136 | 73.7 | 110.8 | 104.4 | 59.9 | 39.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1311.6 | 5244.8 | 29386.5 | 3292.5 | 228.2 | -458.2 | 3062.5 | 7635.3 | 347.3 | -1585.6 | 6400.8 | 917.1 | 3218.9 | 665.5 | 253 | 462.6 | 266.2 | 106.9 | 72.892 | 21 | 62 | 1.0662 | 1.0541 | 1.0546 | 1.0148 | 0 | 0 | 129 | 0 | 1580.7 | 1981.7 | 351.3 | 264.8 | 86.5 | 0.93171 | 0.92905 | 0.82456 | 0.79935 | 0.85163 | 0.83439 | 0.92345 | 0.8545 | 0.8381 | 0.8684 | 0.86248 | 0.90556 | 0.95531 | 18 | 13
p18otc351_brgo_brkp_s.sav | 7906 | 3626.8 | 1107.5 | 1896.8 | 2483.5 | 1571.3 | 1642.3 | 751.6 | 389 | 755.5 | 755.5 | 101.3 | 163.7 | 83.7 | 25.8 | 26.4 | 1911.8 | 330 | 330 | 812.9 | 815 | 2287.9 | 141 | 2126.5 | 2111.3 | -1487.9 | -743.7 | -266.9 | 715.5 | -433.9 | 893.1 | 39.6 | 83.1 | -204.6 | 487.8 | 508.7 | -32.6 | 288 | 591 | 469 | 387.2 | 195.1 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2536.9 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.2 | 1745.2 | 167.8 | 1272.7 | 3186 | 74.3 | 26.6 | 10.9 | 10.1 | 10 | 10 | 0 | 0.94458 | 0.94281 | 0.93616 | 0.79273 | 0.8681 | 0.80838 | 0.82274 | 0.90283 | 0.83271 | 0.82933 | 0.81348 | 0.81403 | 0.86396 | 0.94143 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 68 | 82.7 | 80.3 | 80.6 | 134.1 | 73.5 | 110.3 | 104.1 | 59.5 | 39.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1307.1 | 5246.3 | 29383.5 | 3292.5 | 226.5 | -456.6 | 3062.3 | 7635.3 | 345.5 | -1583.9 | 6400.7 | 917.1 | 3218.4 | 665.4 | 252.9 | 462.6 | 278.5 | 110.4 | 71.775 | 21 | 65.7 | 1.0675 | 1.0556 | 1.0558 | 1.0159 | 0 | 0 | 129 | 0 | 1571.3 | 1971.1 | 351.3 | 264.8 | 86.5 | 0.94127 | 0.93911 | 0.8614 | 0.83764 | 0.87473 | 0.86056 | 0.93483 | 0.87939 | 0.89142 | 0.88231 | 0.87707 | 0.91542 | 0.96161 | 19 | 13
p18otc352.sav | 7711.4 | 3948.3 | 1107.5 | 1896.8 | 2300 | 1644.7 | 1617.1 | 838.4 | 352 | 769 | 769 | 99.2 | 160.3 | 80.2 | 25.6 | 26.2 | 1929.5 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2115.6 | -817.2 | -233.8 | 430.5 | 1879.3 | -776.4 | 741.1 | 251.5 | 65 | -186.7 | 469.9 | 460.5 | -18.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.6 | 1304.9 | 3174.2 | 70.3 | 23.3 | 13.9 | 8.7 | 10 | 10 | 0 | 0.97922 | 1.0039 | 0.99877 | 0.92217 | 1.0386 | 0.92528 | 0.95734 | 0.96633 | 0.94858 | 0.93214 | 0.9228 | 0.92896 | 0.94436 | 0.97935 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57 | 69.4 | 65.1 | 56 | 69.1 | 65.3 | 91.9 | 89 | 44.3 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1205.5 | 4976.3 | 29012.6 | 3273.9 | 232.3 | 646 | 4152.2 | 7635.3 | 314 | -1584.4 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 265.3 | 86.6 | 51.895 | 21 | 44.5 | 1.0796 | 1.0691 | 1.0691 | 1.0271 | 0 | 0 | 129 | 0 | 1644.7 | 1988 | 352 | 265.3 | 86.6 | 1.0039 | 0.99877 | 0.92217 | 1.0386 | 0.92528 | 0.95734 | 0.96633 | 0.94858 | 0.93214 | 0.9228 | 0.92896 | 0.94436 | 0.97935 | 0 | 0
p18otc352_amps.sav | 7873.5 | 4016.6 | 1107.5 | 1896.8 | 2298.8 | 1846.6 | 1617.1 | 1071.4 | 108.1 | 766.4 | 766.4 | 92.4 | 140.8 | 70.6 | 24.6 | 25.1 | 1886.4 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2103.9 | -943.3 | -315.3 | 312.5 | 1909.9 | -746 | 718 | 227.5 | 108.7 | -230 | 513.2 | 489.5 | -52.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.6 | 1337.8 | 3174.2 | 65.5 | 17.1 | 21 | 8.9 | 10 | 10 | 0 | 0.99504 | 1.0417 | 1.0334 | 0.92217 | 1.0386 | 0.92528 | 0.95734 | 1.007 | 0.95379 | 0.93777 | 0.90567 | 0.91101 | 0.93133 | 0.97748 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 33.5 | 40.9 | 0 | 68.1 | 96.2 | 68.4 | 97.8 | 92.2 | 47.6 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1239.2 | 4942.7 | 29012.6 | 3273.9 | 241.4 | 636.9 | 4152.2 | 7581.2 | 313.9 | -1530.1 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 0 | 108.1 | 69.217 | 21 | 65.1 | 1.0796 | 1.0678 | 1.0675 | 1.0269 | 0 | 0 | 129 | 0 | 1846.6 | 2209.8 | 352 | 265.3 | 86.6 | 1.0377 | 1.0347 | 1 | 1 | 1 | 1 | 1.0421 | 1.0055 | 1.006 | 0.98144 | 0.98068 | 0.9862 | 0.99809 | 1 | 1
p18otc352_amps_s.sav | 7872.5 | 4016.7 | 1107.5 | 1896.8 | 2298.8 | 1845.3 | 1617.1 | 1069.7 | 110.2 | 766.4 | 766.4 | 92.3 | 141.3 | 70.8 | 24.6 | 25.1 | 1886.9 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2104 | -941.9 | -314.3 | 313.8 | 1909.5 | -746.5 | 718.4 | 227.9 | 108.2 | -229.5 | 512.7 | 489.1 | -51.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.7 | 1337.7 | 3174.2 | 65.5 | 17.1 | 21 | 8.9 | 10 | 10 | 0 | 0.99638 | 1.0442 | 1.0366 | 0.92217 | 1.0386 | 0.92528 | 0.95734 | 1.0073 | 0.96978 | 0.9823 | 0.91267 | 0.91835 | 0.93602 | 0.98001 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 33.7 | 41 | 0 | 68.3 | 95.5 | 68.3 | 97.8 | 92.2 | 47.5 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1238.8 | 4943 | 29012.6 | 3273.9 | 241.3 | 637 | 4152.2 | 7581.2 | 313.7 | -1529.9 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 0 | 110.2 | 69.115 | 21 | 67.2 | 1.0798 | 1.068 | 1.0676 | 1.0271 | 0 | 0 | 129 | 0 | 1845.3 | 2208.4 | 352 | 265.3 | 86.6 | 1.0402 | 1.0379 | 1 | 1 | 1 | 1 | 1.0424 | 1.0223 | 1.0538 | 0.98902 | 0.98858 | 0.99117 | 1.0007 | 2 | 1
p18otc352_dsbg.sav | 7764 | 3961.6 | 1107.5 | 1896.8 | 2299.5 | 1710.5 | 1617.1 | 915.4 | 275.4 | 772.1 | 772.1 | 96.5 | 147.6 | 72.6 | 25.2 | 25.8 | 1912 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2111.1 | -867.8 | -267.9 | 381.9 | 1895.8 | -764.3 | 729.1 | 239.1 | 83 | -204.6 | 487.8 | 473.8 | -32.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.1 | 1323.4 | 3174.2 | 68.5 | 21.1 | 16.5 | 8.7 | 10 | 10 | 0 | 0.98231 | 1.0093 | 1.0058 | 0.90931 | 1.0035 | 0.91141 | 0.94154 | 0.95949 | 0.99407 | 0.98113 | 0.95252 | 0.96007 | 0.97061 | 0.98213 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 50.9 | 62 | 68.4 | 17.1 | 45.2 | 66.4 | 94.1 | 90.2 | 45.6 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1216.4 | 4965.4 | 29012.6 | 3273.9 | 235.8 | 642.4 | 4152.2 | 7635.3 | 317.9 | -1588.3 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 275.4 | 0 | 55.156 | 21 | -41.6 | 1.0792 | 1.0683 | 1.0683 | 1.0268 | 0 | 0 | 129 | 0 | 1710.5 | 2061 | 352 | 265.3 | 86.6 | 1.0054 | 1.007 | 0.98606 | 0.9662 | 0.98501 | 0.9835 | 0.99292 | 1.048 | 1.0526 | 1.0322 | 1.0335 | 1.0278 | 1.0028 | 3 | 2
p18otc352_bloxhcb.sav | 7813.3 | 3960.7 | 1107.5 | 1896.8 | 2299.9 | 1511.6 | 1617.1 | 800.5 | 362.1 | 758.3 | 758.3 | 98.8 | 159.6 | 80.1 | 25.6 | 26.2 | 1906.9 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2108.8 | -714.3 | -399.6 | 489.5 | 1901.4 | -744.7 | 705.4 | 214.6 | 87.4 | -208.9 | 492.1 | 479.2 | -36 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.9 | 1299.6 | 3174.2 | 70.9 | 24.1 | 12.8 | 8.9 | 10 | 10 | 0 | 0.97559 | 0.99597 | 0.99091 | 0.8993 | 0.99193 | 0.90508 | 0.93432 | 0.95523 | 0.93409 | 0.91648 | 0.90868 | 0.91417 | 0.93321 | 0.97316 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.9 | 71.7 | 68 | 59.5 | 78 | 67.6 | 120.8 | 0 | 69.4 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251.4 | 4930.4 | 29012.6 | 3273.9 | 212.4 | 665.9 | 4152.2 | 7635.3 | 317.1 | -1587.4 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 270.5 | 91.6 | 55.298 | 21 | 49.2 | 1.0791 | 1.0678 | 1.0673 | 1.0266 | 0 | 0 | 129 | 0 | 1511.6 | 1951.2 | 352 | 265.3 | 86.6 | 0.99214 | 0.99213 | 0.9752 | 0.95507 | 0.97817 | 0.97595 | 0.98851 | 0.98472 | 0.9832 | 0.9847 | 0.98408 | 0.98819 | 0.99368 | 4 | 3
p18otc352_bloxhcb_s.sav | 7812 | 3960.9 | 1107.5 | 1896.8 | 2299.9 | 1510.1 | 1617.1 | 798.5 | 364.6 | 758.3 | 758.3 | 98.7 | 160.2 | 80.3 | 25.6 | 26.1 | 1907.4 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2108.9 | -712.7 | -398.3 | 491.1 | 1901 | -745.3 | 705.9 | 215.2 | 86.8 | -208.4 | 491.6 | 478.8 | -35.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.9 | 1299.6 | 3174.2 | 70.8 | 24.1 | 12.8 | 8.9 | 10 | 10 | 0 | 0.97704 | 0.99866 | 0.99434 | 0.90171 | 0.99472 | 0.90664 | 0.93609 | 0.9561 | 0.95022 | 0.96066 | 0.91584 | 0.92167 | 0.93807 | 0.97581 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 58.8 | 71.7 | 68 | 60 | 76.9 | 67.6 | 120.7 | 0 | 69.4 | 34.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251 | 4930.9 | 29012.6 | 3273.9 | 212.2 | 666 | 4152.2 | 7635.3 | 316.9 | -1587.2 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 271.3 | 93.4 | 55.178 | 21 | 51 | 1.0793 | 1.0681 | 1.0674 | 1.0268 | 0 | 0 | 129 | 0 | 1510.1 | 1949.5 | 352 | 265.3 | 86.6 | 0.99482 | 0.99557 | 0.97781 | 0.95775 | 0.97986 | 0.9778 | 0.98941 | 1.0017 | 1.0306 | 0.99246 | 0.99215 | 0.99334 | 0.99638 | 5 | 3
p18otc352_blhcoxll.sav | 8097.4 | 3978.2 | 1107.5 | 1896.8 | 2298.9 | 1891.2 | 1617.1 | 739.5 | 374.8 | 740.7 | 740.7 | 97.9 | 157.7 | 79.4 | 25.5 | 26 | 1867.9 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2097.3 | -583.2 | -609.7 | 567.4 | 1932.3 | -701.9 | 659.8 | 167.8 | 126.1 | -247.2 | 530.3 | 507.4 | -65 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.5 | 1290.1 | 3174.2 | 71.3 | 25.3 | 11.5 | 8.2 | 10 | 10 | 0 | 0.97084 | 0.98351 | 0.97823 | 0.85898 | 0.94521 | 0.86876 | 0.89269 | 0.93503 | 0.90789 | 0.88807 | 0.88268 | 0.88689 | 0.91278 | 0.96158 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 62 | 75.5 | 72.8 | 65.4 | 92.8 | 23.4 | 0 | 0 | 98.8 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1296.5 | 4885.6 | 29012.6 | 3273.9 | 191.5 | 686.8 | 4152.2 | 7635.3 | 324.3 | -1594.5 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 276.2 | 98.5 | 61.145 | 21 | 55.6 | 1.0803 | 1.0736 | 1.0744 | 1.0282 | 0 | 0 | 129 | 0 | 1891.2 | 1891.2 | 352 | 265.3 | 86.6 | 0.97973 | 0.97944 | 0.93148 | 0.91008 | 0.93892 | 0.93247 | 0.96761 | 0.9571 | 0.95272 | 0.95652 | 0.95471 | 0.96656 | 0.98186 | 6 | 4
p18otc352_blhcoxll_s.sav | 8095.9 | 3978.5 | 1107.5 | 1896.8 | 2299 | 1889.3 | 1617.1 | 737.4 | 377.6 | 740.6 | 740.6 | 97.8 | 158.3 | 79.6 | 25.5 | 26 | 1868.5 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2097.5 | -581.4 | -608.1 | 569.2 | 1931.9 | -702.5 | 660.5 | 168.4 | 125.4 | -246.5 | 529.7 | 506.9 | -64.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.4 | 1290.1 | 3174.2 | 71.3 | 25.3 | 11.5 | 8.2 | 10 | 10 | 0 | 0.97233 | 0.98629 | 0.98176 | 0.86157 | 0.94823 | 0.87043 | 0.89462 | 0.93595 | 0.92401 | 0.93159 | 0.88983 | 0.89439 | 0.91759 | 0.96423 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 61.9 | 75.4 | 72.8 | 65.7 | 91.8 | 23.4 | 0 | 0 | 98.7 | 35.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1295.9 | 4886.2 | 29012.6 | 3273.9 | 191.4 | 686.9 | 4152.2 | 7635.3 | 324 | -1594.3 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 277.1 | 100.6 | 61.001 | 21 | 57.7 | 1.0806 | 1.0738 | 1.0745 | 1.0284 | 0 | 0 | 129 | 0 | 1889.3 | 1889.3 | 352 | 265.3 | 86.6 | 0.9825 | 0.98297 | 0.93429 | 0.91299 | 0.94072 | 0.93449 | 0.96856 | 0.9741 | 0.99941 | 0.96427 | 0.96279 | 0.97165 | 0.98456 | 7 | 4
p18otc352_mpsl.sav | 7628.1 | 4032 | 1107.5 | 1896.8 | 2300.2 | 1571.1 | 1617.1 | 796.6 | 363.5 | 757.6 | 757.6 | 98.9 | 159.7 | 80.2 | 25.6 | 26.2 | 1905.8 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2108.5 | -681.2 | 0 | 537.1 | 1916.2 | -710.2 | 658.4 | 166.5 | 88.5 | -210 | 493.2 | 488 | -36.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.4 | 1298.2 | 3174.2 | 71 | 24.3 | 12.9 | 9 | 10 | 10 | 0 | 0.97453 | 0.99355 | 0.98847 | 0.89184 | 0.9833 | 0.89726 | 0.92537 | 0.94938 | 0.92934 | 0.91134 | 0.90318 | 0.9084 | 0.92839 | 0.96952 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.3 | 72.2 | 68.7 | 60.4 | 80.1 | 69.5 | 101.8 | 96.4 | 53 | 35.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.7 | 4982.1 | 29012.6 | 3273.9 | 255 | 623.3 | 4152.2 | 7635.3 | 317.1 | -1587.3 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 270.9 | 92.6 | 56.202 | 21 | 50.1 | 1.0791 | 1.0681 | 1.0679 | 1.0267 | 0 | 0 | 129 | 0 | 1571.1 | 1948.3 | 352 | 265.3 | 86.6 | 0.98973 | 0.98969 | 0.96711 | 0.94676 | 0.96972 | 0.96661 | 0.98246 | 0.97972 | 0.97769 | 0.97874 | 0.97787 | 0.98309 | 0.98996 | 8 | 5
p18otc352_mpsl_s.sav | 7627.3 | 4031.7 | 1107.5 | 1896.8 | 2300.2 | 1569.8 | 1617.1 | 794.7 | 366.1 | 757.6 | 757.6 | 98.8 | 160.4 | 80.4 | 25.6 | 26.2 | 1906.5 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2108.7 | -680.1 | 0 | 538.3 | 1915.6 | -711.3 | 659.5 | 167.5 | 87.8 | -209.3 | 492.5 | 487.4 | -36.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.3 | 1298.2 | 3174.2 | 71 | 24.2 | 12.9 | 8.9 | 10 | 10 | 0 | 0.97608 | 0.99643 | 0.99211 | 0.8946 | 0.9865 | 0.89916 | 0.92755 | 0.95053 | 0.94584 | 0.95581 | 0.91067 | 0.91626 | 0.93355 | 0.97242 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 59.2 | 72.1 | 68.6 | 60.8 | 79 | 69.5 | 101.7 | 96.3 | 52.9 | 35.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1199.3 | 4982.5 | 29012.6 | 3273.9 | 254.7 | 623.6 | 4152.2 | 7635.3 | 316.8 | -1587.1 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 271.7 | 94.4 | 56.052 | 21 | 52 | 1.0794 | 1.0683 | 1.0681 | 1.0268 | 0 | 0 | 129 | 0 | 1569.8 | 1946.7 | 352 | 265.3 | 86.6 | 0.9926 | 0.99333 | 0.9701 | 0.94984 | 0.97177 | 0.96888 | 0.98365 | 0.99711 | 1.0254 | 0.98686 | 0.98633 | 0.98855 | 0.99292 | 9 | 5
p18otc352_angr1.sav | 7723.3 | 3945.1 | 1107.5 | 1896.8 | 2299.8 | 1660 | 1617.1 | 863.1 | 324.4 | 752.1 | 752.1 | 102.6 | 178.9 | 89 | 26.2 | 26.8 | 1927.7 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2114.1 | -835.3 | -246.8 | 412.8 | 1882.5 | -772 | 735.2 | 245.5 | 65.8 | -187.5 | 470.6 | 462.2 | -19.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.8 | 1302.9 | 3174.2 | 73.2 | 25.9 | 10.8 | 9.1 | 10 | 10 | 0 | 0.96837 | 0.97316 | 0.96879 | 0.91675 | 1.0322 | 0.93004 | 0.96276 | 0.96991 | 0.9289 | 0.91086 | 0.92095 | 0.92703 | 0.94427 | 0.97879 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 119.7 | 61.5 | 51.3 | 62.4 | 65.6 | 92.6 | 89.3 | 44.7 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1214.4 | 4967.4 | 29012.6 | 3273.9 | 232.9 | 645.3 | 4152.2 | 7635.3 | 312.8 | -1583.1 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 247 | 77.4 | 48.973 | 21 | 35.5 | 1.0791 | 1.0685 | 1.0687 | 1.0268 | 0 | 0 | 129 | 0 | 1660 | 2005.4 | 352 | 265.3 | 86.6 | 0.96942 | 0.96998 | 0.99412 | 0.99385 | 1.0051 | 1.0057 | 1.0037 | 0.97925 | 0.97717 | 0.99799 | 0.99792 | 0.99991 | 0.99943 | 10 | 6
p18otc352_angr2.sav | 7722.9 | 3948.1 | 1107.5 | 1896.8 | 2299.8 | 1659.3 | 1617.1 | 857.8 | 330.3 | 754 | 754 | 102.1 | 177 | 87.9 | 26.1 | 26.7 | 1927.8 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2114.3 | -831.6 | -244 | 416.5 | 1881.9 | -773.2 | 736.7 | 247 | 65.7 | -187.4 | 470.6 | 461.8 | -19.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.9 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.2 | 1303.5 | 3174.2 | 72.8 | 25.6 | 11.3 | 9 | 10 | 10 | 0 | 0.97109 | 0.98237 | 0.97746 | 0.92112 | 1.0374 | 0.93135 | 0.96424 | 0.97035 | 0.93548 | 0.91798 | 0.92283 | 0.929 | 0.9454 | 0.97954 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 92.4 | 0 | 62 | 51.9 | 63.2 | 65.5 | 92.5 | 89.3 | 44.7 | 34.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1210 | 4971.8 | 29012.6 | 3273.9 | 232.8 | 645.5 | 4152.2 | 7635.3 | 313 | -1583.3 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 251 | 79.3 | 49.308 | 21 | 37.3 | 1.0791 | 1.0685 | 1.0687 | 1.0268 | 0 | 0 | 129 | 0 | 1659.3 | 2004.3 | 352 | 265.3 | 86.6 | 0.97859 | 0.97866 | 0.99886 | 0.99881 | 1.0066 | 1.0072 | 1.0042 | 0.98619 | 0.98481 | 1 | 1 | 1.0011 | 1.0002 | 11 | 7
p18otc352_angr12.sav | 7788.8 | 3914.5 | 1107.5 | 1896.8 | 2299.4 | 1744.6 | 1617.1 | 961.6 | 155.8 | 690.6 | 690.6 | 119 | 234.7 | 116 | 29.1 | 29.7 | 1909.7 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2107.6 | -949 | -328.6 | 302.1 | 1903.4 | -742.1 | 698.1 | 207 | 76.1 | -197.2 | 480.3 | 474.5 | -25.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.6 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.1 | 186.4 | 1243.3 | 3174.2 | 83.6 | 40 | 6 | 13 | 10 | 10 | 0 | 0.86504 | 0.76433 | 0.75351 | 0.83842 | 0.93964 | 0.91412 | 0.94463 | 0.96499 | 0.75302 | 0.71692 | 0.86962 | 0.87317 | 0.91288 | 0.957 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 44.5 | 29.2 | 65.8 | 67.5 | 96.4 | 91.7 | 47.3 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1225.4 | 4956.4 | 29012.6 | 3273.9 | 239.2 | 639.1 | 4152.2 | 7635.3 | 312.1 | -1582.5 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 133 | 22.8 | 32.806 | 21 | -19.2 | 1.076 | 1.065 | 1.0664 | 1.0249 | 0 | 0 | 129 | 0 | 1744.6 | 2102.8 | 352 | 265.3 | 86.6 | 0.76139 | 0.75444 | 0.90918 | 0.90472 | 0.98794 | 0.98672 | 0.99861 | 0.79384 | 0.76911 | 0.94237 | 0.93994 | 0.96666 | 0.97718 | 12 | 8
p18otc352_grgr.sav | 7750.2 | 3933.8 | 1107.5 | 1896.8 | 2300 | 1696.2 | 1617.1 | 903.3 | 254.9 | 673.7 | 673.7 | 160.5 | 228 | 111.6 | 34.7 | 35.4 | 1917.6 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2108.1 | -880 | -278.8 | 369.3 | 1892.2 | -760.5 | 721.2 | 230.9 | 72.2 | -193.6 | 476.7 | 468.3 | -23.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -69.6 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 148.9 | 1280.2 | 3174.2 | 90.1 | 59 | 14.8 | 16.7 | 10 | 10 | 0 | 0.89993 | 0.91544 | 0.90803 | 0.91525 | 1.0305 | 0.94603 | 0.98091 | 0.98007 | 0.88697 | 0.86529 | 0.91834 | 0.9243 | 0.94521 | 0.97766 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 31.3 | 38.2 | 52.3 | 37.9 | 48.2 | 66.3 | 94.1 | 90.3 | 45.7 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1220.2 | 4961.9 | 29012.6 | 3273.9 | 234.9 | 643.3 | 4152.2 | 7635.3 | 311.1 | -1581.4 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 201.7 | 53.2 | 40.561 | 21 | 11.6 | 1.0781 | 1.0671 | 1.0678 | 1.0268 | 0 | 0 | 129 | 0 | 1696.2 | 2046.8 | 352 | 265.3 | 86.6 | 0.91192 | 0.90915 | 0.9925 | 0.99215 | 1.0224 | 1.0246 | 1.0142 | 0.93505 | 0.92828 | 0.99517 | 0.99498 | 1.0009 | 0.99827 | 13 | 9
p18otc352_anpf.sav | 7864.4 | 3968 | 1107.5 | 1896.8 | 2298.8 | 1837.8 | 1617.1 | 1065 | 96.6 | 764.7 | 764.7 | 92.3 | 140.7 | 70.7 | 24.6 | 25.1 | 1882.8 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2102.8 | -985.2 | -348.7 | 270.2 | 1919.5 | -732.4 | 700.5 | 209.3 | 112.2 | -233.6 | 516.8 | 495.2 | -55 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105 | 1323.4 | 3174.2 | 65.6 | 17.2 | 20.8 | 8.9 | 10 | 10 | 0 | 0.99484 | 1.0413 | 1.0329 | 1.1159 | 1.0156 | 1.0815 | 1.1333 | 1.0418 | 0.95146 | 0.93525 | 0.90493 | 0.91023 | 0.93192 | 0.98009 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 33.8 | 41.1 | 0 | 69.2 | 99.3 | 68.7 | 98.7 | 92.9 | 48.3 | 35 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1238 | 4943.9 | 29012.6 | 3273.9 | 244.2 | 634 | 4152.2 | 7635.3 | 315.2 | -1585.5 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | -13.2 | 109.8 | 72.49 | 21 | 66.6 | 1.0797 | 1.0678 | 1.0674 | 1.0269 | 0 | 0 | 129 | 0 | 1837.8 | 2203.9 | 352 | 265.3 | 86.6 | 1.0373 | 1.0342 | 1.2101 | 0.97782 | 1.1688 | 1.1838 | 1.0781 | 1.003 | 1.0033 | 0.98064 | 0.97984 | 0.98683 | 1.0008 | 14 | 10
p18otc352_antbdy.sav | 7732.4 | 3949.3 | 1107.5 | 1896.8 | 2299.7 | 1671.2 | 1617.1 | 869.5 | 321.9 | 769 | 769 | 98.2 | 157.6 | 78.8 | 25.5 | 26 | 1924.1 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2114.2 | -842.3 | -251.2 | 406.8 | 1880.1 | -767.6 | 735.9 | 246.1 | 70.4 | -192.1 | 475.3 | 463.7 | -23 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2537.2 | 140 | 66 | 206 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 117.2 | 1311.4 | 3174.2 | 69.6 | 22.5 | 14.9 | 8.6 | 10 | 10 | 0 | 0.98231 | 1.011 | 1.0054 | 0.93587 | 1.0547 | 0.91114 | 0.94121 | 0.92415 | 0.95089 | 0.93464 | 0.9169 | 0.92278 | 0.9373 | 0.97146 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 53.7 | 65.4 | 56.3 | 56.7 | 69.5 | 65.8 | 92.9 | 89.5 | 44.9 | 34.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1209.4 | 4972.4 | 29012.6 | 3273.9 | 233.5 | 644.7 | 4152.2 | 7635.3 | 320.1 | -1590.6 | 6369 | 900 | 3157.6 | 652.8 | 247.8 | 454 | 233.8 | 88.1 | 44.844 | 21 | 46 | 1.0798 | 1.0691 | 1.069 | 1.0272 | 0 | 0 | 129 | 0 | 1671.2 | 2017.8 | 352 | 265.3 | 86.6 | 1.0072 | 1.0066 | 1.0149 | 1.0155 | 0.98472 | 0.98315 | 0.95635 | 1.0024 | 1.0027 | 0.99361 | 0.99335 | 0.99252 | 0.99194 | 15 | 11
p18otc352_brbo_brkp.sav | 7917.3 | 3639.9 | 1107.5 | 1896.8 | 2480.1 | 1590.6 | 1642.1 | 772.2 | 377 | 755.7 | 755.7 | 100 | 161.7 | 82.3 | 25.6 | 26.2 | 1907.3 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.7 | 2110.2 | -1486.1 | -741.2 | -275.2 | 732.8 | -445.4 | 888.6 | 40.5 | 88.1 | -209.6 | 492.8 | 513.5 | -36.6 | 288 | 591 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.2 | 151 | 39 | 59 | 2537.2 | 142.6 | 67.2 | 209.8 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 154.1 | 1286.3 | 3186.1 | 73.8 | 25.9 | 11.7 | 10 | 10 | 10 | 0 | 0.95031 | 0.95419 | 0.94855 | 0.79908 | 0.87553 | 0.82102 | 0.83749 | 0.91165 | 0.86363 | 0.83979 | 0.85579 | 0.85862 | 0.89707 | 0.96067 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 64.7 | 78.7 | 78 | 72.2 | 112.8 | 73.6 | 110.5 | 104 | 59.5 | 39.1 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1307.1 | 5240.3 | 29377.5 | 3292.5 | 218.8 | -450 | 3061.1 | 7635.3 | 338.2 | -1577.5 | 6399.8 | 917.1 | 3216.1 | 665.1 | 252.4 | 462.4 | 273.6 | 103.5 | 68.531 | 21 | 59.8 | 1.0689 | 1.0567 | 1.0564 | 1.0169 | 0 | 0 | 129 | 0 | 1590.6 | 1991.2 | 352 | 265.3 | 86.6 | 0.95052 | 0.94972 | 0.86652 | 0.84299 | 0.88732 | 0.87481 | 0.94342 | 0.91044 | 0.90093 | 0.92738 | 0.92428 | 0.94992 | 0.98093 | 16 | 12
p18otc352_brbo_brkp_s.sav | 7907 | 3637.8 | 1107.5 | 1896.8 | 2478.8 | 1581.1 | 1641.2 | 761.2 | 391.9 | 756.3 | 756.3 | 99.8 | 163.5 | 82.9 | 25.6 | 26.2 | 1910.8 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.7 | 2111.2 | -1476.4 | -734.5 | -265.7 | 731.3 | -449.7 | 889.1 | 43.6 | 84.8 | -206.3 | 489.5 | 511.5 | -34.1 | 288 | 590.5 | 468.8 | 386.8 | 195.1 | 78 | 308.8 | -76.8 | 151 | 39 | 59 | 2537.2 | 142.5 | 67.2 | 209.7 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.8 | 42.8 | 38.7 | 6.1 | 279 | 1745.2 | 153.3 | 1286.9 | 3185.9 | 73.8 | 26 | 11.5 | 9.9 | 10 | 10 | 0 | 0.95553 | 0.96391 | 0.9587 | 0.83343 | 0.91554 | 0.84227 | 0.86214 | 0.9224 | 0.88706 | 0.8904 | 0.8681 | 0.87157 | 0.906 | 0.96638 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 64.8 | 78.9 | 78.1 | 71.9 | 110.7 | 73.3 | 110.1 | 103.7 | 59.2 | 39.1 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1302.5 | 5240.5 | 29373.2 | 3292.5 | 217.3 | -449.1 | 3060.6 | 7635.3 | 336.8 | -1576 | 6399.8 | 916.2 | 3215.6 | 664.7 | 252.4 | 462.4 | 285.6 | 106.4 | 67.512 | 21 | 62.8 | 1.0703 | 1.0581 | 1.0576 | 1.018 | 0 | 0 | 129 | 0 | 1581.1 | 1980.7 | 352 | 265.3 | 86.6 | 0.9602 | 0.95988 | 0.90377 | 0.88151 | 0.91029 | 0.90056 | 0.95454 | 0.93515 | 0.95522 | 0.94072 | 0.93822 | 0.95938 | 0.98676 | 17 | 12
p18otc352_brgo_brkp.sav | 7915 | 3626.8 | 1107.5 | 1896.8 | 2485.1 | 1580.9 | 1642.4 | 763 | 374.3 | 755.1 | 755.1 | 101.5 | 162.2 | 83.2 | 25.8 | 26.4 | 1909.3 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2110.9 | -1498.5 | -750.9 | -276.6 | 716.3 | -429.2 | 893.3 | 35.9 | 85.9 | -207.4 | 490.6 | 510.5 | -34.8 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2537.2 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 168.6 | 1272.3 | 3186.4 | 74.3 | 26.7 | 11 | 10.1 | 10 | 10 | 0 | 0.93979 | 0.93555 | 0.9282 | 0.76096 | 0.83093 | 0.78829 | 0.7992 | 0.89246 | 0.81125 | 0.78207 | 0.80166 | 0.80155 | 0.85535 | 0.9357 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 67.3 | 82 | 80.4 | 81.2 | 135.9 | 73.7 | 110.8 | 104.4 | 59.9 | 39.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1310.9 | 5244.1 | 29385.2 | 3292.5 | 228.1 | -458.4 | 3062.1 | 7635.3 | 347.1 | -1586 | 6400.3 | 917.1 | 3217.6 | 665.2 | 252.5 | 462.6 | 267.1 | 107.3 | 72.767 | 21 | 62.4 | 1.0668 | 1.0547 | 1.0549 | 1.0153 | 0 | 0 | 129 | 0 | 1580.9 | 1982 | 352 | 265.3 | 86.6 | 0.93195 | 0.92934 | 0.82518 | 0.80005 | 0.85195 | 0.83481 | 0.92356 | 0.85523 | 0.83901 | 0.86873 | 0.86285 | 0.90575 | 0.95543 | 18 | 13
p18otc352_brgo_brkp_s.sav | 7905.7 | 3627.2 | 1107.5 | 1896.8 | 2483.8 | 1571.4 | 1642.3 | 751.2 | 390.2 | 755.6 | 755.6 | 101.3 | 164.1 | 83.9 | 25.8 | 26.4 | 1912.5 | 330 | 330 | 813.2 | 815 | 2288.2 | 141 | 2126.8 | 2111.8 | -1487.5 | -743.3 | -266.3 | 715.4 | -434.3 | 893.7 | 39.5 | 82.7 | -204.2 | 487.4 | 508.6 | -32.4 | 288 | 591 | 469 | 387.2 | 195.1 | 78 | 309.2 | -77.1 | 151 | 39 | 59 | 2537.2 | 142.7 | 67.2 | 209.9 | 12.2 | 40.8 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.2 | 1745.2 | 167.7 | 1273.1 | 3186.3 | 74.3 | 26.7 | 10.8 | 10.1 | 10 | 10 | 0 | 0.94494 | 0.94515 | 0.93826 | 0.79491 | 0.87066 | 0.80966 | 0.82424 | 0.90346 | 0.83484 | 0.83174 | 0.81448 | 0.81509 | 0.86465 | 0.94187 | 37.7 | 40 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 67.4 | 82 | 80.3 | 80.6 | 134 | 73.5 | 110.3 | 104.1 | 59.5 | 39.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1306.6 | 5246.3 | 29383.1 | 3292.5 | 226.4 | -456.7 | 3062.1 | 7635.3 | 345.4 | -1584.2 | 6400.3 | 917.1 | 3217.1 | 665.2 | 252.5 | 462.6 | 279.4 | 110.8 | 71.654 | 21 | 66 | 1.0681 | 1.0561 | 1.0561 | 1.0163 | 0 | 0 | 129 | 0 | 1571.4 | 1971.3 | 352 | 265.3 | 86.6 | 0.94152 | 0.93942 | 0.862 | 0.8383 | 0.87504 | 0.86097 | 0.93494 | 0.88009 | 0.89229 | 0.88262 | 0.87742 | 0.91559 | 0.96173 | 19 | 13
p18otc356.sav | 7766.4 | 3976.4 | 1107.5 | 1896.8 | 2300 | 1700.9 | 1617.1 | 904.5 | 355.9 | 764.1 | 764.1 | 95.4 | 154.1 | 77.2 | 25.1 | 25.6 | 1905.5 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2105.9 | -855.2 | -258.6 | 398.2 | 1865.6 | -798.9 | 714.2 | 226.3 | 85.1 | -206.7 | 489.9 | 465 | -34.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.6 | 1394.9 | 3266.2 | 58.9 | 20.2 | 23.1 | 9.4 | 10 | 10 | 0 | 0.97531 | 0.99921 | 0.9944 | 0.90784 | 1.0388 | 0.91271 | 0.94301 | 0.95964 | 0.94473 | 0.92799 | 0.92013 | 0.92617 | 0.94223 | 0.97789 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 54.6 | 66.5 | 67 | 56.5 | 69.9 | 66.3 | 93.7 | 90 | 45.4 | 33.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1217.3 | 4976.4 | 29024.6 | 3273.9 | 233.5 | 646.1 | 4153.5 | 7635.3 | 315.2 | -1674.1 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 269.2 | 86.7 | 54.108 | 23.3 | 44.6 | 1.0753 | 1.0666 | 1.0675 | 1.0269 | 0 | 0 | 129 | 0 | 1700.9 | 2049.7 | 355.9 | 269.2 | 86.7 | 0.99921 | 0.9944 | 0.90784 | 1.0388 | 0.91271 | 0.94301 | 0.95964 | 0.94473 | 0.92799 | 0.92013 | 0.92617 | 0.94223 | 0.97789 | 0 | 0
p18otc356_amps.sav | 7930.6 | 4044.6 | 1107.5 | 1896.8 | 2298.7 | 1905.6 | 1617.1 | 1141.6 | 108.6 | 761.6 | 761.6 | 88.4 | 134.3 | 67.4 | 24 | 24.6 | 1861.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2094.1 | -983.4 | -341.5 | 278.4 | 1896.6 | -768.2 | 690.4 | 201.6 | 129.3 | -250.5 | 533.7 | 494 | -67.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.4 | 1428.9 | 3266.2 | 54.2 | 13.8 | 30.2 | 11.1 | 10 | 10 | 0 | 0.99204 | 1.0394 | 1.0313 | 0.90784 | 1.0388 | 0.91271 | 0.94301 | 1.0069 | 0.95115 | 0.93492 | 0.90347 | 0.9087 | 0.92974 | 0.97678 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 30.3 | 37 | 0 | 68.8 | 97.5 | 69.5 | 99.7 | 93.3 | 48.6 | 33.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1253.1 | 4940.8 | 29024.6 | 3273.9 | 242.9 | 636.7 | 4153.5 | 7581.2 | 314.7 | -1619.5 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 0 | 108.6 | 71.812 | 23.3 | 65.5 | 1.0753 | 1.0652 | 1.0657 | 1.0266 | 0 | 0 | 129 | 0 | 1905.6 | 2274.6 | 355.9 | 269.2 | 86.7 | 1.0403 | 1.0371 | 1 | 1 | 1 | 1 | 1.0492 | 1.0068 | 1.0075 | 0.98189 | 0.98114 | 0.98674 | 0.99887 | 1 | 1
p18otc356_amps_s.sav | 7929.6 | 4044.7 | 1107.5 | 1896.8 | 2298.7 | 1904.3 | 1617.1 | 1139.9 | 110.7 | 761.6 | 761.6 | 88.4 | 134.8 | 67.6 | 24 | 24.5 | 1862.4 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2094.2 | -982 | -340.5 | 279.8 | 1896.2 | -768.6 | 690.8 | 202 | 128.8 | -250 | 533.2 | 493.6 | -67.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.5 | 1428.8 | 3266.2 | 54.2 | 13.8 | 30.1 | 11.1 | 10 | 10 | 0 | 0.99338 | 1.0419 | 1.0345 | 0.90784 | 1.0388 | 0.91271 | 0.94301 | 1.0071 | 0.9671 | 0.97933 | 0.91046 | 0.91603 | 0.93441 | 0.9793 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 30.4 | 37.1 | 0 | 69 | 96.8 | 69.4 | 99.6 | 93.3 | 48.6 | 33.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1252.7 | 4941.2 | 29024.6 | 3273.9 | 242.8 | 636.9 | 4153.5 | 7581.2 | 314.5 | -1619.3 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 0 | 110.7 | 71.707 | 23.3 | 67.6 | 1.0755 | 1.0655 | 1.0658 | 1.0268 | 0 | 0 | 129 | 0 | 1904.3 | 2273.1 | 355.9 | 269.2 | 86.7 | 1.0427 | 1.0403 | 1 | 1 | 1 | 1 | 1.0495 | 1.0237 | 1.0553 | 0.98949 | 0.98905 | 0.9917 | 1.0014 | 2 | 1
p18otc356_dsbg.sav | 7819.3 | 3989.2 | 1107.5 | 1896.8 | 2299.5 | 1767.1 | 1617.1 | 982.4 | 278.3 | 767.3 | 767.3 | 92.7 | 141.2 | 69.5 | 24.7 | 25.2 | 1887.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2101.3 | -906.6 | -293.2 | 349 | 1882.2 | -786.6 | 701.9 | 213.6 | 103.3 | -224.7 | 507.9 | 478.3 | -48.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.4 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 107 | 1413.4 | 3266.2 | 57.1 | 17.9 | 25.6 | 10 | 10 | 10 | 0 | 0.97812 | 1.004 | 1.0009 | 0.89374 | 0.98548 | 0.8978 | 0.92599 | 0.95231 | 0.98984 | 0.97658 | 0.95158 | 0.95909 | 0.96969 | 0.98123 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 48.5 | 59 | 70.3 | 17.5 | 45.3 | 67.4 | 95.9 | 91.2 | 46.6 | 33.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1228.9 | 4964.9 | 29024.6 | 3273.9 | 237.3 | 642.4 | 4153.5 | 7635.3 | 319.3 | -1678.1 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 278.3 | 0 | 57.443 | 23.3 | -41.6 | 1.0748 | 1.0657 | 1.0666 | 1.0265 | 0 | 0 | 129 | 0 | 1767.1 | 2123.2 | 355.9 | 269.2 | 86.7 | 1.0048 | 1.0065 | 0.98447 | 0.9487 | 0.98366 | 0.98195 | 0.99236 | 1.0477 | 1.0524 | 1.0342 | 1.0355 | 1.0291 | 1.0034 | 3 | 2
p18otc356_bloxhcb.sav | 7870.7 | 3988.9 | 1107.5 | 1896.8 | 2299.8 | 1567.7 | 1617.1 | 866.8 | 365.1 | 753.4 | 753.4 | 95 | 153.2 | 76.9 | 25 | 25.6 | 1882.4 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2099 | -751 | -427.1 | 457.3 | 1888.1 | -766.5 | 677.4 | 188.5 | 108 | -229.3 | 512.5 | 483.9 | -51.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.2 | 1389.3 | 3266.2 | 59.4 | 21 | 22 | 9.5 | 10 | 10 | 0 | 0.97135 | 0.9907 | 0.98588 | 0.88337 | 0.97349 | 0.89115 | 0.91838 | 0.94785 | 0.9291 | 0.91108 | 0.90522 | 0.91054 | 0.93049 | 0.97137 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56.6 | 68.9 | 70 | 60.2 | 79.1 | 68.7 | 122.9 | 0 | 70.8 | 33.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1264.7 | 4929.2 | 29024.6 | 3273.9 | 212.8 | 666.9 | 4153.5 | 7635.3 | 318.5 | -1677.3 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 273.5 | 91.6 | 57.655 | 23.3 | 49.2 | 1.0747 | 1.0653 | 1.0655 | 1.0264 | 0 | 0 | 129 | 0 | 1567.7 | 2013.2 | 355.9 | 269.2 | 86.7 | 0.99148 | 0.99143 | 0.97305 | 0.93716 | 0.97638 | 0.97388 | 0.98771 | 0.98346 | 0.98178 | 0.9838 | 0.98312 | 0.98754 | 0.99333 | 4 | 3
p18otc356_bloxhcb_s.sav | 7869.4 | 3989.1 | 1107.5 | 1896.8 | 2299.8 | 1566.1 | 1617.1 | 864.8 | 367.7 | 753.3 | 753.3 | 94.9 | 153.9 | 77.2 | 25 | 25.6 | 1883 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2099.1 | -749.3 | -425.8 | 459 | 1887.7 | -767.1 | 678 | 189 | 107.4 | -228.7 | 511.9 | 483.5 | -51.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.2 | 1389.3 | 3266.2 | 59.4 | 20.9 | 22 | 9.4 | 10 | 10 | 0 | 0.97286 | 0.9935 | 0.98944 | 0.88589 | 0.97641 | 0.89276 | 0.92023 | 0.94875 | 0.94543 | 0.95535 | 0.91247 | 0.91814 | 0.93542 | 0.97405 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56.5 | 68.8 | 70 | 60.6 | 78 | 68.7 | 122.8 | 0 | 70.8 | 33.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1264.2 | 4929.7 | 29024.6 | 3273.9 | 212.6 | 667 | 4153.5 | 7635.3 | 318.3 | -1677.1 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 274.3 | 93.5 | 57.528 | 23.3 | 51.1 | 1.075 | 1.0655 | 1.0656 | 1.0265 | 0 | 0 | 129 | 0 | 1566.1 | 2011.5 | 355.9 | 269.2 | 86.7 | 0.99428 | 0.99501 | 0.97582 | 0.93997 | 0.97814 | 0.97584 | 0.98865 | 1.0007 | 1.0295 | 0.99167 | 0.99133 | 0.99277 | 0.99607 | 5 | 3
p18otc356_blhcoxll.sav | 8157.1 | 4004.4 | 1107.5 | 1896.8 | 2298.9 | 1952.9 | 1617.1 | 805.4 | 376.3 | 735.2 | 735.2 | 94 | 151.1 | 76.2 | 24.9 | 25.5 | 1841.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2087.2 | -618.3 | -640.6 | 535.3 | 1919.8 | -722.5 | 630.4 | 140.2 | 148.1 | -268.9 | 552.1 | 512.6 | -81.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 141.3 | 1379.2 | 3266.2 | 59.8 | 22.2 | 20.3 | 8.2 | 10 | 10 | 0 | 0.96629 | 0.97752 | 0.97246 | 0.8398 | 0.92294 | 0.85185 | 0.8732 | 0.92611 | 0.90122 | 0.88082 | 0.87759 | 0.88155 | 0.90881 | 0.95905 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.8 | 72.9 | 74.9 | 66.3 | 94.6 | 23.7 | 0 | 0 | 100.8 | 34 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1313.2 | 4881 | 29024.6 | 3273.9 | 191.2 | 688.4 | 4153.5 | 7635.3 | 326.3 | -1685.1 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 277.6 | 98.7 | 63.863 | 23.3 | 55.8 | 1.076 | 1.0712 | 1.0729 | 1.028 | 0 | 0 | 129 | 0 | 1952.9 | 1952.9 | 355.9 | 269.2 | 86.7 | 0.97829 | 0.97794 | 0.92505 | 0.88849 | 0.93332 | 0.92597 | 0.96506 | 0.95395 | 0.94917 | 0.95377 | 0.95182 | 0.96453 | 0.98073 | 6 | 4
p18otc356_blhcoxll_s.sav | 8155.5 | 4004.7 | 1107.5 | 1896.8 | 2298.9 | 1951 | 1617.1 | 803.2 | 379.2 | 735.1 | 735.1 | 93.9 | 151.7 | 76.4 | 24.9 | 25.4 | 1842.6 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2087.3 | -616.5 | -639 | 537.2 | 1919.3 | -723.1 | 631 | 140.9 | 147.5 | -268.3 | 551.5 | 512.2 | -80.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 141.3 | 1379.3 | 3266.2 | 59.8 | 22.2 | 20.3 | 8.2 | 10 | 10 | 0 | 0.96779 | 0.98029 | 0.97598 | 0.84242 | 0.92599 | 0.85354 | 0.87515 | 0.92703 | 0.91728 | 0.9241 | 0.88471 | 0.88902 | 0.9136 | 0.96168 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 59.8 | 72.8 | 74.9 | 66.6 | 93.6 | 23.7 | 0 | 0 | 100.8 | 34 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1312.5 | 4881.6 | 29024.6 | 3273.9 | 191.1 | 688.5 | 4153.5 | 7635.3 | 326 | -1684.8 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 278.4 | 100.8 | 63.713 | 23.3 | 57.8 | 1.0763 | 1.0715 | 1.073 | 1.0282 | 0 | 0 | 129 | 0 | 1951 | 1951 | 355.9 | 269.2 | 86.7 | 0.98106 | 0.98148 | 0.92794 | 0.89143 | 0.93517 | 0.92804 | 0.96602 | 0.97094 | 0.99581 | 0.96151 | 0.95989 | 0.96962 | 0.98342 | 7 | 4
p18otc356_mpsl.sav | 7675.2 | 4069.3 | 1107.5 | 1896.8 | 2300.2 | 1620.5 | 1617.1 | 859.4 | 366.9 | 751.6 | 751.6 | 95 | 153.2 | 77 | 25 | 25.6 | 1879 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2098 | -705.5 | 0 | 516 | 1906.9 | -724.8 | 621.3 | 131 | 111.3 | -232.6 | 515.8 | 495.4 | -54.1 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133.3 | 1387.1 | 3266.2 | 59.7 | 21.2 | 21.9 | 9.5 | 10 | 10 | 0 | 0.96975 | 0.98709 | 0.98224 | 0.87227 | 0.96063 | 0.87989 | 0.90549 | 0.9399 | 0.92201 | 0.9034 | 0.89723 | 0.90217 | 0.9236 | 0.96631 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.2 | 69.6 | 71 | 61.5 | 82.4 | 71.1 | 104.8 | 98.3 | 55 | 33.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1211 | 4982.8 | 29024.6 | 3273.9 | 259.1 | 620.5 | 4153.5 | 7635.3 | 318.8 | -1677.5 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 273.7 | 93.2 | 59.034 | 23.3 | 50.7 | 1.0747 | 1.0654 | 1.0661 | 1.0264 | 0 | 0 | 129 | 0 | 1620.5 | 2006.9 | 355.9 | 269.2 | 86.7 | 0.98787 | 0.98777 | 0.96082 | 0.92478 | 0.96404 | 0.96021 | 0.97943 | 0.97595 | 0.9735 | 0.97511 | 0.97409 | 0.98023 | 0.98816 | 8 | 5
p18otc356_mpsl_s.sav | 7674.3 | 4069.1 | 1107.5 | 1896.8 | 2300.3 | 1619.3 | 1617.1 | 857.5 | 369.6 | 751.6 | 751.6 | 94.9 | 153.8 | 77.2 | 25 | 25.6 | 1879.8 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2098.2 | -704.4 | 0 | 517.2 | 1906.3 | -725.9 | 622.3 | 132.1 | 110.6 | -231.9 | 515.1 | 494.9 | -53.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133.3 | 1387.1 | 3266.2 | 59.7 | 21.2 | 21.9 | 9.5 | 10 | 10 | 0 | 0.97129 | 0.98996 | 0.98586 | 0.87506 | 0.96387 | 0.88182 | 0.9077 | 0.94106 | 0.93844 | 0.9476 | 0.9047 | 0.91 | 0.92874 | 0.9692 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 57.1 | 69.6 | 71 | 61.9 | 81.2 | 71 | 104.6 | 98.2 | 54.9 | 33.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1210.6 | 4983.2 | 29024.6 | 3273.9 | 258.8 | 620.9 | 4153.5 | 7635.3 | 318.5 | -1677.2 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 274.6 | 95 | 58.877 | 23.3 | 52.6 | 1.075 | 1.0657 | 1.0662 | 1.0265 | 0 | 0 | 129 | 0 | 1619.3 | 2005.3 | 355.9 | 269.2 | 86.7 | 0.99074 | 0.99141 | 0.96389 | 0.9279 | 0.96616 | 0.96256 | 0.98064 | 0.99334 | 1.0211 | 0.98323 | 0.98254 | 0.98568 | 0.99111 | 9 | 5
p18otc356_angr1.sav | 7778.6 | 3973.8 | 1107.5 | 1896.8 | 2299.8 | 1716.5 | 1617.1 | 928.9 | 328.9 | 748.3 | 748.3 | 98.6 | 171.3 | 85.4 | 25.6 | 26.2 | 1903.7 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2104.5 | -873.1 | -271.4 | 380.8 | 1868.8 | -794.6 | 708.4 | 220.4 | 86 | -207.4 | 490.6 | 466.6 | -34.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127.4 | 1393.2 | 3266.2 | 61.5 | 22.6 | 20.2 | 9.1 | 10 | 10 | 0 | 0.96415 | 0.96613 | 0.96231 | 0.90037 | 1.0298 | 0.91637 | 0.94719 | 0.9627 | 0.92291 | 0.90437 | 0.91709 | 0.92299 | 0.94127 | 0.97688 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 114.7 | 63.6 | 52.1 | 63.9 | 66.6 | 94.3 | 90.4 | 45.8 | 33.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1225.7 | 4968.1 | 29024.6 | 3273.9 | 234.2 | 645.4 | 4153.5 | 7635.3 | 314.1 | -1672.9 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 251.2 | 77.7 | 51.417 | 23.3 | 35.7 | 1.0749 | 1.0661 | 1.0671 | 1.0267 | 0 | 0 | 129 | 0 | 1716.5 | 2067.5 | 355.9 | 269.2 | 86.7 | 0.96689 | 0.96773 | 0.99177 | 0.99137 | 1.004 | 1.0044 | 1.0032 | 0.9769 | 0.97455 | 0.9967 | 0.99657 | 0.99898 | 0.99897 | 10 | 6
p18otc356_angr2.sav | 7778.1 | 3976.5 | 1107.5 | 1896.8 | 2299.8 | 1715.6 | 1617.1 | 923.8 | 334.5 | 750.1 | 750.1 | 98.1 | 169.6 | 84.4 | 25.5 | 26.1 | 1903.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2104.6 | -869.5 | -268.6 | 384.4 | 1868.1 | -795.7 | 709.8 | 221.9 | 85.9 | -207.4 | 490.6 | 466.3 | -34.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 126.9 | 1393.7 | 3266.2 | 61.2 | 22.3 | 20.6 | 9.2 | 10 | 10 | 0 | 0.96681 | 0.97535 | 0.97098 | 0.90486 | 1.0352 | 0.91775 | 0.94876 | 0.96318 | 0.92956 | 0.91157 | 0.91907 | 0.92505 | 0.94248 | 0.97766 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 88.5 | 0 | 64.1 | 52.7 | 64.5 | 66.6 | 94.2 | 90.3 | 45.7 | 33.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1221.6 | 4972.2 | 29024.6 | 3273.9 | 234.1 | 645.5 | 4153.5 | 7635.3 | 314.2 | -1673.1 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 255.1 | 79.4 | 51.707 | 23.3 | 37.4 | 1.0749 | 1.0661 | 1.0671 | 1.0266 | 0 | 0 | 129 | 0 | 1715.6 | 2066.3 | 355.9 | 269.2 | 86.7 | 0.97612 | 0.97645 | 0.99672 | 0.99656 | 1.0055 | 1.0061 | 1.0037 | 0.98394 | 0.98231 | 0.99885 | 0.99879 | 1.0003 | 0.99977 | 11 | 7
p18otc356_angr12.sav | 7843.3 | 3948.5 | 1107.5 | 1896.8 | 2299.4 | 1800 | 1617.1 | 1024.9 | 171.3 | 690 | 690 | 113.7 | 225.1 | 111.8 | 28.2 | 28.8 | 1887.7 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2098.5 | -979.7 | -347.7 | 277.3 | 1887.9 | -766.9 | 673.7 | 184.6 | 95.1 | -216 | 499.1 | 477.7 | -40 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 180.8 | 1340.8 | 3266.2 | 70.5 | 35.7 | 8.1 | 9.9 | 10 | 10 | 0 | 0.86846 | 0.76178 | 0.75346 | 0.82513 | 0.9393 | 0.90311 | 0.93207 | 0.95943 | 0.75411 | 0.71816 | 0.86815 | 0.87163 | 0.91146 | 0.95643 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 47.5 | 31.8 | 65.9 | 68.5 | 98 | 92.6 | 48.2 | 33.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1236.2 | 4957.6 | 29024.6 | 3273.9 | 240.2 | 639.4 | 4153.5 | 7635.3 | 313 | -1671.8 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 144.9 | 26.5 | 36.594 | 23.3 | -15.6 | 1.0725 | 1.0632 | 1.065 | 1.0252 | 0 | 0 | 129 | 0 | 1800 | 2163.2 | 355.9 | 269.2 | 86.7 | 0.76238 | 0.7577 | 0.90889 | 0.90424 | 0.98948 | 0.9884 | 0.99978 | 0.79823 | 0.77389 | 0.94351 | 0.94111 | 0.96734 | 0.97806 | 12 | 8
p18otc356_grgr.sav | 7806.2 | 3965.2 | 1107.5 | 1896.8 | 2299.9 | 1753.6 | 1617.1 | 968.7 | 263.2 | 675.7 | 675.7 | 152.4 | 216.5 | 106.5 | 33.5 | 34.2 | 1894.5 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2099 | -915.6 | -301.6 | 339.6 | 1877.7 | -783.8 | 695.2 | 206.7 | 91.9 | -213 | 496.2 | 472.3 | -38.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.2 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 147.7 | 1373.3 | 3266.2 | 76.4 | 53.8 | 4.1 | 12.2 | 10 | 10 | 0 | 0.89214 | 0.90375 | 0.89741 | 0.89483 | 1.0232 | 0.93013 | 0.96285 | 0.9718 | 0.87772 | 0.85519 | 0.91242 | 0.91809 | 0.94066 | 0.97502 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.4 | 37 | 55.1 | 39.8 | 51.2 | 67.3 | 95.8 | 91.3 | 46.7 | 33.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1230.4 | 4963.6 | 29024.6 | 3273.9 | 236.2 | 643.4 | 4153.5 | 7635.3 | 312.4 | -1671.2 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 208.6 | 54.5 | 43.684 | 23.3 | 12.8 | 1.0744 | 1.0651 | 1.0664 | 1.0269 | 0 | 0 | 129 | 0 | 1753.6 | 2109.6 | 355.9 | 269.2 | 86.7 | 0.90446 | 0.90246 | 0.98567 | 0.98497 | 1.0191 | 1.021 | 1.0127 | 0.92907 | 0.92155 | 0.99162 | 0.99128 | 0.99833 | 0.99706 | 13 | 9
p18otc356_anpf.sav | 7921.5 | 3995.9 | 1107.5 | 1896.8 | 2298.8 | 1896.9 | 1617.1 | 1135.3 | 97 | 759.8 | 759.8 | 88.3 | 134.3 | 67.5 | 24 | 24.5 | 1858.3 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2093.1 | -1025.4 | -374.9 | 236.2 | 1906.2 | -754.5 | 672.7 | 183.4 | 132.9 | -254 | 537.2 | 499.7 | -70.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.8 | 1414.5 | 3266.2 | 54.3 | 13.9 | 30 | 11.1 | 10 | 10 | 0 | 0.99185 | 1.039 | 1.0307 | 1.1157 | 1.0154 | 1.0813 | 1.1331 | 1.0416 | 0.94878 | 0.93236 | 0.90268 | 0.90788 | 0.93029 | 0.97937 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.5 | 37.2 | 0 | 69.9 | 100.6 | 69.8 | 100.6 | 94 | 49.4 | 33.6 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1251.9 | 4942 | 29024.6 | 3273.9 | 245.8 | 633.8 | 4153.5 | 7635.3 | 316 | -1674.9 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | -13.2 | 110.3 | 75.088 | 23.3 | 67.1 | 1.0753 | 1.0652 | 1.0657 | 1.0267 | 0 | 0 | 129 | 0 | 1896.9 | 2268.8 | 355.9 | 269.2 | 86.7 | 1.0398 | 1.0365 | 1.2289 | 0.97748 | 1.1847 | 1.2015 | 1.0854 | 1.0043 | 1.0047 | 0.98103 | 0.98025 | 0.98733 | 1.0015 | 14 | 10
p18otc356_antbdy.sav | 7788.3 | 3977.1 | 1107.5 | 1896.8 | 2299.7 | 1728.6 | 1617.1 | 937.1 | 324.6 | 764.1 | 764.1 | 94.4 | 151.3 | 75.7 | 24.9 | 25.5 | 1899.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2104.4 | -881.6 | -276.9 | 373.3 | 1866.6 | -789.7 | 708.6 | 220.5 | 90.9 | -212.4 | 495.6 | 468.3 | -38.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2533.2 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 118.7 | 1401.9 | 3266.2 | 58.2 | 19.3 | 24.1 | 9.6 | 10 | 10 | 0 | 0.97839 | 1.0064 | 1.001 | 0.92061 | 1.0541 | 0.89366 | 0.92124 | 0.90966 | 0.94664 | 0.93005 | 0.91315 | 0.91885 | 0.93403 | 0.96884 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 51.1 | 62.2 | 57.8 | 57.2 | 70.4 | 66.8 | 94.7 | 90.6 | 46 | 33.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1221.6 | 4972.2 | 29024.6 | 3273.9 | 234.8 | 644.8 | 4153.5 | 7635.3 | 322.1 | -1681 | 6280.5 | 900 | 3169.6 | 654.2 | 229.3 | 384 | 236.3 | 88.3 | 46.753 | 23.3 | 46.1 | 1.0755 | 1.0666 | 1.0673 | 1.027 | 0 | 0 | 129 | 0 | 1728.6 | 2080.9 | 355.9 | 269.2 | 86.7 | 1.0072 | 1.0066 | 1.0141 | 1.0147 | 0.97913 | 0.97691 | 0.94792 | 1.002 | 1.0022 | 0.99241 | 0.9921 | 0.9913 | 0.99074 | 15 | 11
p18otc356_brbo_brkp.sav | 7972.4 | 3665.4 | 1107.5 | 1896.8 | 2481.9 | 1646.5 | 1642.3 | 837.7 | 375.4 | 749.9 | 749.9 | 96.1 | 155 | 79.1 | 25.1 | 25.6 | 1880.7 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.8 | 2099.8 | -1525.5 | -766.5 | -307.4 | 725.4 | -468.2 | 860.6 | 11.3 | 110.9 | -232.2 | 515.4 | 520.5 | -53.8 | 288 | 591 | 469 | 387.2 | 195.1 | 78 | 309.2 | -77.5 | 151 | 39 | 59 | 2533.2 | 192 | 67.2 | 259.2 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 156.7 | 1372.9 | 3275.2 | 62.7 | 22.8 | 20.8 | 10.3 | 10 | 10 | 0 | 0.94514 | 0.94769 | 0.94225 | 0.77819 | 0.85111 | 0.80245 | 0.8158 | 0.9016 | 0.85612 | 0.83155 | 0.85006 | 0.8526 | 0.89262 | 0.9577 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 62.6 | 76.2 | 79.9 | 73.1 | 114.5 | 74.8 | 112.6 | 105.3 | 60.8 | 37.7 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1323.7 | 5237.7 | 29391.4 | 3292.5 | 222.6 | -452.3 | 3062.7 | 7635.3 | 339.1 | -1668.5 | 6309.8 | 917.1 | 3228.8 | 666.5 | 233.6 | 391.2 | 272.2 | 103.2 | 71.314 | 23.3 | 59.4 | 1.0638 | 1.053 | 1.0533 | 1.0159 | 0 | 0 | 129 | 0 | 1646.5 | 2052.5 | 355.9 | 269.2 | 86.7 | 0.94844 | 0.94756 | 0.85719 | 0.81934 | 0.87919 | 0.8651 | 0.93952 | 0.90621 | 0.89608 | 0.92385 | 0.92056 | 0.94735 | 0.97935 | 16 | 12
p18otc356_brbo_brkp_s.sav | 7963.8 | 3665.3 | 1107.5 | 1896.8 | 2480.1 | 1637.4 | 1642.1 | 826.5 | 390.5 | 750.5 | 750.5 | 95.9 | 156.8 | 79.7 | 25 | 25.6 | 1883.9 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2100.7 | -1515.4 | -759.4 | -297.9 | 723.8 | -472.7 | 861 | 14.8 | 107.7 | -229 | 512.2 | 518.4 | -51.5 | 288 | 591 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.5 | 151 | 39 | 59 | 2533.2 | 192 | 67.2 | 259.2 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 155.9 | 1373.5 | 3275.2 | 62.8 | 22.9 | 20.6 | 10.3 | 10 | 10 | 0 | 0.9503 | 0.95726 | 0.95225 | 0.81208 | 0.89069 | 0.82344 | 0.8403 | 0.91218 | 0.87945 | 0.88189 | 0.86237 | 0.86555 | 0.90153 | 0.96341 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 62.6 | 76.2 | 79.9 | 72.8 | 112.4 | 74.5 | 112.1 | 105 | 60.4 | 37.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1319.3 | 5240.3 | 29389.7 | 3292.5 | 221.2 | -451 | 3062.5 | 7635.3 | 337.6 | -1666.9 | 6309.7 | 917.1 | 3228.3 | 666.5 | 233.6 | 391.1 | 284.3 | 106.1 | 70.261 | 23.3 | 62.5 | 1.0652 | 1.0546 | 1.0546 | 1.017 | 0 | 0 | 129 | 0 | 1637.4 | 2042.4 | 355.9 | 269.2 | 86.7 | 0.95802 | 0.95761 | 0.89452 | 0.85745 | 0.90219 | 0.89108 | 0.95054 | 0.9309 | 0.95032 | 0.93723 | 0.93455 | 0.95681 | 0.98519 | 17 | 12
p18otc356_brgo_brkp.sav | 7970.9 | 3652.6 | 1107.5 | 1896.8 | 2487.1 | 1638 | 1642.4 | 830.3 | 370.5 | 749.3 | 749.3 | 97.5 | 155.3 | 80 | 25.2 | 25.8 | 1882.2 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.8 | 2100.4 | -1539.3 | -777 | -310.2 | 708.1 | -450.4 | 865.1 | 6.3 | 109 | -230.3 | 513.4 | 517.4 | -52.2 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2533.2 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 171.3 | 1358.6 | 3275.4 | 63.1 | 23.6 | 20.2 | 10.4 | 10 | 10 | 0 | 0.93444 | 0.92881 | 0.9216 | 0.73833 | 0.80434 | 0.76785 | 0.77508 | 0.88118 | 0.80252 | 0.77237 | 0.794 | 0.79346 | 0.84913 | 0.93102 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 65.3 | 79.5 | 82.2 | 82 | 137.5 | 75 | 113 | 105.7 | 61.2 | 37.9 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1328.3 | 5241.3 | 29399.6 | 3292.5 | 232 | -460.8 | 3063.6 | 7635.3 | 348.2 | -1676.7 | 6310.6 | 917.1 | 3230.4 | 666.7 | 233.7 | 391.4 | 264 | 106.4 | 75.724 | 23.3 | 61.5 | 1.0616 | 1.0508 | 1.0514 | 1.0141 | 0 | 0 | 129 | 0 | 1638 | 2044.7 | 355.9 | 269.2 | 86.7 | 0.92954 | 0.92679 | 0.81328 | 0.77432 | 0.84129 | 0.82192 | 0.91824 | 0.84947 | 0.8323 | 0.86292 | 0.85671 | 0.90119 | 0.95207 | 18 | 13
p18otc356_brgo_brkp_s.sav | 7962.6 | 3653.4 | 1107.5 | 1896.8 | 2485.4 | 1628.7 | 1642.4 | 818.3 | 386.7 | 749.8 | 749.8 | 97.3 | 157.2 | 80.6 | 25.2 | 25.8 | 1885.6 | 330 | 330 | 809.2 | 815 | 2284.2 | 141 | 2122.7 | 2101.2 | -1528 | -769.2 | -299.7 | 707.2 | -455.8 | 866.2 | 10.1 | 105.7 | -227 | 510.2 | 515.5 | -49.8 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2533.2 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 170.2 | 1359.5 | 3275.4 | 63.2 | 23.6 | 20 | 10.3 | 10 | 10 | 0 | 0.93962 | 0.93837 | 0.93164 | 0.77209 | 0.84397 | 0.7893 | 0.80039 | 0.8923 | 0.82629 | 0.82207 | 0.80728 | 0.80749 | 0.85886 | 0.93762 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 65.2 | 79.4 | 82.1 | 81.4 | 135.6 | 74.7 | 112.5 | 105.4 | 60.8 | 37.8 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1323.7 | 5244.3 | 29398 | 3292.5 | 230.2 | -459.1 | 3063.6 | 7635.3 | 346.4 | -1675.1 | 6310.3 | 917.1 | 3230.2 | 666.6 | 233.7 | 391.3 | 276.7 | 110 | 74.552 | 23.3 | 65.2 | 1.063 | 1.0524 | 1.0529 | 1.0153 | 0 | 0 | 129 | 0 | 1628.7 | 2034.2 | 355.9 | 269.2 | 86.7 | 0.93911 | 0.93689 | 0.85047 | 0.81247 | 0.86479 | 0.84876 | 0.92983 | 0.87463 | 0.88586 | 0.87735 | 0.87186 | 0.91152 | 0.95882 | 19 | 13
p18otc360.sav | 7901.4 | 4051.4 | 1107.5 | 1896.8 | 2300 | 1655.6 | 1617.1 | 870.3 | 359.5 | 751.7 | 751.7 | 94.2 | 151.9 | 76 | 24.9 | 25.5 | 1875.8 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2097.9 | -945.5 | -321.8 | 324.7 | 1837.3 | -848.5 | 638.7 | 155.2 | 116.1 | -237.4 | 520.6 | 464.7 | -58.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127 | 1395 | 3267.7 | 59.3 | 20.7 | 22.3 | 9.4 | 10 | 10 | 0 | 0.9737 | 0.99556 | 0.991 | 0.89397 | 1.0305 | 0.90028 | 0.92882 | 0.95306 | 0.94131 | 0.92429 | 0.91791 | 0.92384 | 0.94051 | 0.97681 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55.6 | 67.7 | 69 | 57 | 70.7 | 67.7 | 96.8 | 92.1 | 47.5 | 30.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1243.8 | 5176.8 | 29251.3 | 3273.9 | 236 | 645.8 | 4155.6 | 7635.3 | 315.1 | -1875.2 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 272.7 | 86.8 | 56.305 | 25.4 | 44.6 | 1.0753 | 1.0661 | 1.0669 | 1.0267 | 0 | 0 | 129 | 0 | 1655.6 | 2015 | 359.5 | 272.7 | 86.8 | 0.99556 | 0.991 | 0.89397 | 1.0305 | 0.90028 | 0.92882 | 0.95306 | 0.94131 | 0.92429 | 0.91791 | 0.92384 | 0.94051 | 0.97681 | 0 | 0
p18otc360_amps.sav | 8068.4 | 4120 | 1107.5 | 1896.8 | 2298.7 | 1864.1 | 1617.1 | 1111.3 | 109.4 | 749.4 | 749.4 | 87 | 131.8 | 66.1 | 23.8 | 24.4 | 1831.7 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2086.3 | -1075.7 | -406 | 203.6 | 1868.5 | -817.5 | 614.3 | 130 | 160.7 | -281.5 | 564.6 | 493.5 | -91.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.5 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.5 | 1430.4 | 3267.7 | 54.6 | 14.2 | 29.5 | 11 | 10 | 10 | 0 | 0.9921 | 1.0396 | 1.0313 | 0.89397 | 1.0305 | 0.90028 | 0.92882 | 1.0068 | 0.94996 | 0.93364 | 0.90201 | 0.90717 | 0.92873 | 0.97654 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 30.7 | 37.4 | 0 | 69.5 | 98.8 | 71 | 102.9 | 95.5 | 50.9 | 30.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1280.9 | 5139.7 | 29251.3 | 3273.9 | 245.9 | 635.9 | 4155.6 | 7581.2 | 314 | -1820 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 0 | 109.4 | 74.388 | 25.4 | 66.2 | 1.0755 | 1.0648 | 1.065 | 1.0266 | 0 | 0 | 129 | 0 | 1864.1 | 2243.8 | 359.5 | 272.7 | 86.8 | 1.0442 | 1.0407 | 1 | 1 | 1 | 1 | 1.0564 | 1.0092 | 1.0101 | 0.98268 | 0.98196 | 0.98747 | 0.99972 | 1 | 1
p18otc360_amps_s.sav | 8067.3 | 4120.1 | 1107.5 | 1896.8 | 2298.7 | 1862.8 | 1617.1 | 1109.6 | 111.5 | 749.3 | 749.3 | 86.9 | 132.2 | 66.2 | 23.8 | 24.3 | 1832.2 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2086.4 | -1074.3 | -405 | 204.9 | 1868.1 | -817.9 | 614.7 | 130.4 | 160.2 | -281 | 564.2 | 493.2 | -90.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.5 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.6 | 1430.3 | 3267.7 | 54.6 | 14.3 | 29.5 | 11 | 10 | 10 | 0 | 0.99343 | 1.042 | 1.0345 | 0.89397 | 1.0305 | 0.90028 | 0.92882 | 1.0071 | 0.9659 | 0.978 | 0.90899 | 0.91449 | 0.9334 | 0.97906 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 30.8 | 37.5 | 0 | 69.8 | 98.1 | 70.9 | 102.9 | 95.5 | 50.8 | 30.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1280.6 | 5140.1 | 29251.3 | 3273.9 | 245.8 | 636 | 4155.6 | 7581.2 | 313.8 | -1819.8 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 0 | 111.5 | 74.282 | 25.4 | 68.4 | 1.0757 | 1.065 | 1.0652 | 1.0268 | 0 | 0 | 129 | 0 | 1862.8 | 2242.4 | 359.5 | 272.7 | 86.8 | 1.0467 | 1.0439 | 1 | 1 | 1 | 1 | 1.0567 | 1.0261 | 1.0581 | 0.99028 | 0.98988 | 0.99244 | 1.0023 | 2 | 1
p18otc360_dsbg.sav | 7954.9 | 4063.9 | 1107.5 | 1896.8 | 2299.5 | 1722.7 | 1617.1 | 949.1 | 281.2 | 754.9 | 754.9 | 91.4 | 138.9 | 68.4 | 24.5 | 25 | 1858 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2093.4 | -997.6 | -356.9 | 275 | 1853.9 | -835.9 | 626.1 | 142.2 | 134.4 | -255.5 | 538.7 | 477.9 | -71.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 108.2 | 1413.7 | 3267.7 | 57.6 | 18.5 | 24.9 | 9.9 | 10 | 10 | 0 | 0.97662 | 1.0005 | 0.99763 | 0.87907 | 0.9685 | 0.88451 | 0.91077 | 0.9453 | 0.98671 | 0.97322 | 0.95098 | 0.95847 | 0.96912 | 0.98066 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 49.4 | 60.1 | 72.3 | 17.7 | 45.3 | 68.9 | 99 | 93.3 | 48.8 | 30.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1255.7 | 5164.9 | 29251.3 | 3273.9 | 240 | 641.8 | 4155.6 | 7635.3 | 319.1 | -1879.2 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 281.2 | 0 | 59.709 | 25.4 | -41.6 | 1.0748 | 1.0651 | 1.066 | 1.0263 | 0 | 0 | 129 | 0 | 1722.7 | 2089.4 | 359.5 | 272.7 | 86.8 | 1.005 | 1.0067 | 0.98333 | 0.93981 | 0.98248 | 0.98057 | 0.99186 | 1.0482 | 1.0529 | 1.036 | 1.0375 | 1.0304 | 1.0039 | 3 | 2
p18otc360_bloxhcb.sav | 8009.8 | 4064.1 | 1107.5 | 1896.8 | 2299.8 | 1521 | 1617.1 | 832.4 | 367.8 | 740.7 | 740.7 | 93.7 | 150.8 | 75.7 | 24.9 | 25.4 | 1851.9 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2090.9 | -837.8 | -495.5 | 384.7 | 1860.5 | -815 | 600.4 | 116 | 139.8 | -260.7 | 543.9 | 483.9 | -75.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133 | 1389 | 3267.7 | 59.9 | 21.5 | 21.2 | 9.5 | 10 | 10 | 0 | 0.96927 | 0.98616 | 0.98156 | 0.86737 | 0.95494 | 0.87693 | 0.90208 | 0.94037 | 0.92421 | 0.90578 | 0.90195 | 0.90711 | 0.92799 | 0.96983 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.6 | 70.2 | 72 | 60.8 | 80.3 | 70.2 | 126.8 | 0 | 73.7 | 30.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1294 | 5126.6 | 29251.3 | 3273.9 | 213.3 | 668.5 | 4155.6 | 7635.3 | 318.4 | -1878.5 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 276 | 91.8 | 60.058 | 25.4 | 49.3 | 1.0745 | 1.0645 | 1.0646 | 1.0261 | 0 | 0 | 129 | 0 | 1521 | 1978.1 | 359.5 | 272.7 | 86.8 | 0.99056 | 0.99047 | 0.97025 | 0.92665 | 0.97406 | 0.97121 | 0.98669 | 0.98183 | 0.97997 | 0.98261 | 0.98189 | 0.98669 | 0.99285 | 4 | 3
p18otc360_bloxhcb_s.sav | 8008.4 | 4064.4 | 1107.5 | 1896.8 | 2299.8 | 1519.4 | 1617.1 | 830.3 | 370.5 | 740.6 | 740.6 | 93.6 | 151.5 | 76 | 24.8 | 25.4 | 1852.5 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2091.1 | -836.1 | -494.1 | 386.4 | 1860.1 | -815.6 | 601 | 116.6 | 139.2 | -260.1 | 543.3 | 483.6 | -75.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133 | 1389 | 3267.7 | 59.9 | 21.5 | 21.1 | 9.5 | 10 | 10 | 0 | 0.97079 | 0.98896 | 0.98511 | 0.86991 | 0.9579 | 0.87856 | 0.90395 | 0.94127 | 0.94049 | 0.94987 | 0.90918 | 0.9147 | 0.9329 | 0.97251 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 57.6 | 70.1 | 72 | 61.3 | 79.1 | 70.2 | 126.7 | 0 | 73.6 | 30.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1293.5 | 5127.1 | 29251.3 | 3273.9 | 213.2 | 668.6 | 4155.6 | 7635.3 | 318.2 | -1878.3 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 276.8 | 93.6 | 59.926 | 25.4 | 51.2 | 1.0748 | 1.0647 | 1.0648 | 1.0262 | 0 | 0 | 129 | 0 | 1519.4 | 1976.3 | 359.5 | 272.7 | 86.8 | 0.99337 | 0.99406 | 0.97309 | 0.92952 | 0.97587 | 0.97322 | 0.98763 | 0.99913 | 1.0277 | 0.99049 | 0.99011 | 0.99191 | 0.9956 | 5 | 3
p18otc360_blhcoxll.sav | 8305.2 | 4079.4 | 1107.5 | 1896.8 | 2298.9 | 1918.1 | 1617.1 | 771.2 | 377 | 722 | 722 | 92.7 | 148.5 | 74.9 | 24.7 | 25.3 | 1810.2 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2078.9 | -701.3 | -715.5 | 463.6 | 1893 | -768.8 | 550.5 | 65.1 | 181 | -301.4 | 584.5 | 513.1 | -105.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 143.8 | 1378.2 | 3267.7 | 60.3 | 22.7 | 19.5 | 8.2 | 10 | 10 | 0 | 0.96382 | 0.97201 | 0.96715 | 0.82013 | 0.90006 | 0.8342 | 0.85278 | 0.91668 | 0.89432 | 0.8733 | 0.87232 | 0.876 | 0.90468 | 0.95638 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 61 | 74.3 | 77 | 67.3 | 96.5 | 23.8 | 0 | 0 | 104.5 | 30.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1346.3 | 5074.6 | 29251.3 | 3273.9 | 190 | 691.7 | 4155.6 | 7635.3 | 326.7 | -1886.7 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 278.1 | 98.9 | 66.641 | 25.4 | 55.8 | 1.0759 | 1.0708 | 1.0725 | 1.0278 | 0 | 0 | 129 | 0 | 1918.1 | 1918.1 | 359.5 | 272.7 | 86.8 | 0.97635 | 0.97593 | 0.9174 | 0.8734 | 0.9266 | 0.91813 | 0.96183 | 0.95008 | 0.94483 | 0.95033 | 0.94822 | 0.9619 | 0.97908 | 6 | 4
p18otc360_blhcoxll_s.sav | 8303.5 | 4079.8 | 1107.5 | 1896.8 | 2298.9 | 1916.1 | 1617.1 | 768.8 | 380 | 722 | 722 | 92.6 | 149.1 | 75.1 | 24.7 | 25.3 | 1810.8 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2079.1 | -699.4 | -713.8 | 465.6 | 1892.6 | -769.6 | 551.2 | 65.9 | 180.3 | -300.8 | 583.9 | 512.7 | -105 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 143.7 | 1378.3 | 3267.7 | 60.3 | 22.7 | 19.5 | 8.1 | 10 | 10 | 0 | 0.96533 | 0.97481 | 0.97068 | 0.82288 | 0.90326 | 0.83606 | 0.85495 | 0.91779 | 0.91038 | 0.91642 | 0.87957 | 0.88362 | 0.90962 | 0.95919 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.9 | 74.1 | 77 | 67.6 | 95.4 | 23.8 | 0 | 0 | 104.4 | 30.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1345.6 | 5075.3 | 29251.3 | 3273.9 | 189.9 | 691.9 | 4155.6 | 7635.3 | 326.4 | -1886.4 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 279.1 | 101 | 66.481 | 25.4 | 57.9 | 1.0762 | 1.0711 | 1.0727 | 1.028 | 0 | 0 | 129 | 0 | 1916.1 | 1916.1 | 359.5 | 272.7 | 86.8 | 0.97916 | 0.9795 | 0.92048 | 0.8765 | 0.92867 | 0.92047 | 0.96299 | 0.96714 | 0.99148 | 0.95823 | 0.95646 | 0.96716 | 0.98196 | 7 | 4
p18otc360_mpsl.sav | 7788.9 | 4167.7 | 1107.5 | 1896.8 | 2300.3 | 1557.3 | 1617.1 | 816 | 370.7 | 736.1 | 736.1 | 93.7 | 150.5 | 75.8 | 24.9 | 25.4 | 1842.5 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2088.2 | -759.9 | 0 | 471.8 | 1889.6 | -754.8 | 520.1 | 34.5 | 149 | -269.9 | 553 | 502.8 | -82.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 137.2 | 1384.8 | 3267.7 | 60.3 | 22 | 20.9 | 9.5 | 10 | 10 | 0 | 0.96616 | 0.97931 | 0.97463 | 0.8466 | 0.93084 | 0.85678 | 0.87889 | 0.92718 | 0.91089 | 0.89133 | 0.88767 | 0.89212 | 0.91597 | 0.96145 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.8 | 71.7 | 73.9 | 63.3 | 86.5 | 73.8 | 110.7 | 102.6 | 59.8 | 30.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1236.2 | 5184.3 | 29251.3 | 3273.9 | 268.7 | 613.1 | 4155.6 | 7635.3 | 319.5 | -1879.5 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 276.1 | 94.6 | 62.698 | 25.4 | 51.9 | 1.0743 | 1.0643 | 1.065 | 1.0259 | 0 | 0 | 129 | 0 | 1557.3 | 1963.2 | 359.5 | 272.7 | 86.8 | 0.98368 | 0.98348 | 0.94701 | 0.90326 | 0.95168 | 0.94624 | 0.97284 | 0.96768 | 0.96434 | 0.96706 | 0.96566 | 0.97391 | 0.98428 | 8 | 5
p18otc360_mpsl_s.sav | 7788 | 4167.5 | 1107.5 | 1896.8 | 2300.3 | 1556 | 1617.1 | 814 | 373.5 | 736.1 | 736.1 | 93.6 | 151.1 | 76 | 24.8 | 25.4 | 1843.2 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2088.4 | -758.7 | 0 | 473 | 1889 | -755.9 | 521.3 | 35.7 | 148.3 | -269.2 | 552.3 | 502.2 | -81.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 137.1 | 1384.9 | 3267.7 | 60.3 | 22 | 20.9 | 9.5 | 10 | 10 | 0 | 0.96771 | 0.98217 | 0.97825 | 0.84946 | 0.93416 | 0.85875 | 0.88117 | 0.92836 | 0.92722 | 0.93515 | 0.89511 | 0.89993 | 0.92107 | 0.96434 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 58.8 | 71.5 | 73.9 | 63.6 | 85.3 | 73.7 | 110.6 | 102.5 | 59.6 | 30.7 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1235.8 | 5184.8 | 29251.3 | 3273.9 | 268.4 | 613.4 | 4155.6 | 7635.3 | 319.2 | -1879.2 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 277 | 96.5 | 62.529 | 25.4 | 53.8 | 1.0746 | 1.0646 | 1.0651 | 1.026 | 0 | 0 | 129 | 0 | 1556 | 1961.5 | 359.5 | 272.7 | 86.8 | 0.98655 | 0.98713 | 0.95021 | 0.90648 | 0.95387 | 0.9487 | 0.97408 | 0.98503 | 1.0117 | 0.97516 | 0.97412 | 0.97933 | 0.98723 | 9 | 5
p18otc360_angr1.sav | 7913.9 | 4048.6 | 1107.5 | 1896.8 | 2299.8 | 1671.6 | 1617.1 | 895.4 | 332 | 735.8 | 735.8 | 97.4 | 169.2 | 84.4 | 25.4 | 26 | 1874.1 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2096.6 | -963.8 | -334.9 | 307 | 1840.4 | -844.1 | 632.8 | 149.1 | 116.9 | -238 | 521.2 | 466.2 | -58.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.9 | 1393.3 | 3267.7 | 62 | 23.2 | 19.3 | 9.2 | 10 | 10 | 0 | 0.96185 | 0.96049 | 0.95698 | 0.88606 | 1.021 | 0.90431 | 0.93343 | 0.95639 | 0.91784 | 0.89888 | 0.9144 | 0.92016 | 0.93928 | 0.97564 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 116.9 | 65.5 | 52.6 | 64.6 | 68.1 | 97.4 | 92.5 | 47.9 | 30.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1252.5 | 5168.1 | 29251.3 | 3273.9 | 236.8 | 645 | 4155.6 | 7635.3 | 313.8 | -1873.9 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 254.5 | 77.4 | 53.568 | 25.4 | 35.4 | 1.0749 | 1.0655 | 1.0665 | 1.0264 | 0 | 0 | 129 | 0 | 1671.6 | 2033.1 | 359.5 | 272.7 | 86.8 | 0.96477 | 0.96567 | 0.99115 | 0.9907 | 1.0045 | 1.005 | 1.0035 | 0.97507 | 0.97251 | 0.99618 | 0.99602 | 0.99869 | 0.9988 | 10 | 6
p18otc360_angr2.sav | 7913.3 | 4051.5 | 1107.5 | 1896.8 | 2299.8 | 1670.7 | 1617.1 | 890.1 | 337.8 | 737.6 | 737.6 | 97 | 167.5 | 83.4 | 25.4 | 25.9 | 1874.3 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2096.7 | -960.1 | -332 | 310.7 | 1839.8 | -845.2 | 634.2 | 150.6 | 116.8 | -238 | 521.2 | 465.9 | -58.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.4 | 1393.8 | 3267.7 | 61.7 | 22.9 | 19.8 | 9.2 | 10 | 10 | 0 | 0.96464 | 0.9701 | 0.96603 | 0.8907 | 1.0266 | 0.90568 | 0.935 | 0.95684 | 0.92481 | 0.90643 | 0.91648 | 0.92234 | 0.94055 | 0.97646 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 90.2 | 0 | 66 | 53.1 | 65.2 | 68 | 97.3 | 92.4 | 47.8 | 30.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1248.2 | 5172.3 | 29251.3 | 3273.9 | 236.6 | 645.1 | 4155.6 | 7635.3 | 314 | -1874.1 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 258.5 | 79.2 | 53.857 | 25.4 | 37.2 | 1.0748 | 1.0655 | 1.0665 | 1.0264 | 0 | 0 | 129 | 0 | 1670.7 | 2031.9 | 359.5 | 272.7 | 86.8 | 0.97443 | 0.9748 | 0.99634 | 0.99616 | 1.006 | 1.0067 | 1.004 | 0.98247 | 0.98068 | 0.99844 | 0.99838 | 1 | 0.99964 | 11 | 7
p18otc360_angr12.sav | 7982.7 | 4017.7 | 1107.5 | 1896.8 | 2299.3 | 1760.7 | 1617.1 | 998.7 | 161.2 | 679.5 | 679.5 | 113.1 | 219.6 | 109.4 | 28.2 | 28.8 | 1858.2 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2092 | -1080.7 | -418.9 | 193.9 | 1860.2 | -813.7 | 593.6 | 109 | 124.9 | -245.4 | 528.4 | 476.5 | -61.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1744.4 | 190 | 1333.9 | 3267.7 | 70.7 | 37.4 | 7.2 | 10.2 | 10 | 10 | 0 | 0.8507 | 0.72612 | 0.71775 | 0.79624 | 0.9118 | 0.8859 | 0.91237 | 0.9508 | 0.72064 | 0.68027 | 0.85437 | 0.85713 | 0.90197 | 0.95068 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 48.5 | 31.8 | 72.5 | 70.1 | 101.4 | 95 | 50.6 | 30.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1265.4 | 5155.3 | 29251.3 | 3273.9 | 243.8 | 638 | 4155.6 | 7635.3 | 313.1 | -1873.1 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 139.6 | 21.6 | 38.011 | 25.4 | -20.6 | 1.0717 | 1.0617 | 1.0636 | 1.0244 | 0 | 0 | 129 | 0 | 1760.7 | 2135.2 | 359.5 | 272.7 | 86.8 | 0.72936 | 0.72427 | 0.89068 | 0.88479 | 0.98403 | 0.98229 | 0.99763 | 0.76557 | 0.73599 | 0.93078 | 0.92779 | 0.95902 | 0.97325 | 12 | 8
p18otc360_grgr.sav | 7941.9 | 4039.5 | 1107.5 | 1896.8 | 2299.9 | 1709.3 | 1617.1 | 935.9 | 265.1 | 662.7 | 662.7 | 151.9 | 214.5 | 105.6 | 33.4 | 34.2 | 1865.1 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2091.2 | -1007.3 | -365.8 | 265 | 1849.3 | -833.1 | 619.1 | 135 | 122.4 | -243.2 | 526.4 | 471.7 | -61.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.1 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149.9 | 1372.6 | 3267.7 | 76.8 | 55 | 4.8 | 12.6 | 10 | 10 | 0 | 0.88433 | 0.89367 | 0.88755 | 0.87983 | 1.0134 | 0.91895 | 0.95013 | 0.96607 | 0.86913 | 0.84581 | 0.90868 | 0.91416 | 0.93803 | 0.97342 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 31.2 | 38 | 56.7 | 40 | 52.4 | 68.8 | 98.9 | 93.4 | 48.9 | 30.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1257.6 | 5163.2 | 29251.3 | 3273.9 | 238.9 | 642.8 | 4155.6 | 7635.3 | 311.9 | -1872 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 211.6 | 53.5 | 45.667 | 25.4 | 11.8 | 1.0744 | 1.0645 | 1.0658 | 1.0266 | 0 | 0 | 129 | 0 | 1709.3 | 2075.9 | 359.5 | 272.7 | 86.8 | 0.89766 | 0.89561 | 0.98418 | 0.98339 | 1.0207 | 1.0229 | 1.0137 | 0.92332 | 0.91509 | 0.98994 | 0.98952 | 0.99736 | 0.99653 | 13 | 9
p18otc360_anpf.sav | 8059.3 | 4071 | 1107.5 | 1896.8 | 2298.8 | 1855.4 | 1617.1 | 1105 | 97.7 | 747.6 | 747.6 | 86.9 | 131.8 | 66.1 | 23.8 | 24.3 | 1828.2 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2085.2 | -1117.8 | -439.5 | 161.4 | 1878.1 | -803.8 | 596.5 | 111.7 | 164.2 | -284.9 | 568.1 | 499.2 | -93.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.5 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.9 | 1415.9 | 3267.7 | 54.7 | 14.4 | 29.4 | 11 | 10 | 10 | 0 | 0.99189 | 1.0392 | 1.0308 | 1.1156 | 1.0152 | 1.0812 | 1.1329 | 1.0415 | 0.94754 | 0.93102 | 0.90117 | 0.90629 | 0.92925 | 0.97911 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.9 | 37.7 | 0 | 70.7 | 102 | 71.3 | 103.8 | 96.2 | 51.7 | 30.5 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1280 | 5140.7 | 29251.3 | 3273.9 | 249 | 632.8 | 4155.6 | 7635.3 | 315.2 | -1875.2 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | -13.3 | 111 | 77.668 | 25.4 | 67.7 | 1.0755 | 1.0648 | 1.065 | 1.0266 | 0 | 0 | 129 | 0 | 1855.4 | 2238 | 359.5 | 272.7 | 86.8 | 1.0438 | 1.0401 | 1.2479 | 0.98515 | 1.2009 | 1.2197 | 1.0928 | 1.0066 | 1.0073 | 0.98176 | 0.981 | 0.98803 | 1.0024 | 14 | 10
p18otc360_antbdy.sav | 7924.1 | 4051.9 | 1107.5 | 1896.8 | 2299.7 | 1684.4 | 1617.1 | 904.1 | 327.1 | 751.6 | 751.6 | 93.1 | 149 | 74.6 | 24.7 | 25.3 | 1869.9 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2096.4 | -973.1 | -341 | 298.8 | 1838.4 | -838.9 | 632.8 | 149.1 | 122.1 | -243.3 | 526.5 | 468.2 | -62.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534.7 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119.6 | 1402.4 | 3267.7 | 58.6 | 19.8 | 23.3 | 9.6 | 10 | 10 | 0 | 0.97693 | 1.003 | 0.99784 | 0.90604 | 1.0451 | 0.87646 | 0.90153 | 0.89539 | 0.94308 | 0.92621 | 0.90996 | 0.91551 | 0.93125 | 0.96664 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 51.9 | 63.2 | 59.3 | 57.8 | 71.2 | 68.3 | 97.8 | 92.7 | 48.1 | 30.2 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1248.3 | 5172.2 | 29251.3 | 3273.9 | 237.3 | 644.4 | 4155.6 | 7635.3 | 322.6 | -1882.8 | 6079.2 | 1100 | 3196.3 | 656.3 | 252 | 220 | 238.6 | 88.5 | 48.674 | 25.4 | 46.3 | 1.0755 | 1.066 | 1.0667 | 1.0268 | 0 | 0 | 129 | 0 | 1684.4 | 2047.3 | 359.5 | 272.7 | 86.8 | 1.0075 | 1.0069 | 1.0135 | 1.0142 | 0.97354 | 0.97062 | 0.93949 | 1.0019 | 1.0021 | 0.99134 | 0.99098 | 0.99015 | 0.98959 | 15 | 11
p18otc360_brbo_brkp.sav | 8111.1 | 3742.3 | 1107.5 | 1896.8 | 2481.8 | 1603.2 | 1642.3 | 805.1 | 373 | 736.1 | 736.1 | 94.7 | 152.1 | 77.7 | 24.9 | 25.4 | 1847.1 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2090.9 | -1612.3 | -827.5 | -375.1 | 709 | -518 | 782.7 | -61.4 | 145.7 | -266.6 | 549.7 | 524.5 | -79.9 | 288 | 591 | 469 | 387.2 | 195.1 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2534.7 | 192 | 67.2 | 259.2 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 158.8 | 1372.3 | 3276.7 | 63.1 | 23.4 | 20.1 | 10.4 | 10 | 10 | 0 | 0.94218 | 0.94192 | 0.93664 | 0.75803 | 0.8275 | 0.78434 | 0.79455 | 0.89184 | 0.84913 | 0.82388 | 0.84534 | 0.84763 | 0.8891 | 0.95556 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 63.5 | 77.4 | 81.6 | 73.9 | 116 | 76.3 | 115.8 | 107.6 | 63.1 | 34.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1357.5 | 5435 | 29622.5 | 3292.5 | 229.3 | -456.8 | 3064.9 | 7635.3 | 336.4 | -1862.2 | 6113.3 | 1120.9 | 3256.1 | 668.7 | 256.7 | 224.1 | 270.1 | 102.9 | 74.004 | 25.4 | 59 | 1.0631 | 1.0514 | 1.0513 | 1.0152 | 0 | 0 | 129 | 0 | 1603.2 | 2018.6 | 359.5 | 272.7 | 86.8 | 0.94612 | 0.94515 | 0.84794 | 0.80298 | 0.87122 | 0.85544 | 0.93576 | 0.90207 | 0.89136 | 0.92094 | 0.91751 | 0.94534 | 0.97825 | 16 | 12
p18otc360_brbo_brkp_s.sav | 8102.7 | 3742.1 | 1107.5 | 1896.8 | 2480 | 1594 | 1642.1 | 793.9 | 388.4 | 736.7 | 736.7 | 94.5 | 153.9 | 78.3 | 24.9 | 25.4 | 1850.4 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.3 | 2091.8 | -1602.4 | -820.5 | -365.7 | 707.4 | -522.6 | 783.3 | -57.8 | 142.5 | -263.4 | 546.5 | 522.5 | -77.5 | 288 | 591 | 468.8 | 387.2 | 195.1 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2534.7 | 192 | 67.2 | 259.2 | 12.2 | 40.7 | 50.9 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.1 | 1745.2 | 158 | 1373.1 | 3276.7 | 63.2 | 23.4 | 19.9 | 10.3 | 10 | 10 | 0 | 0.94729 | 0.95137 | 0.94654 | 0.79152 | 0.86669 | 0.80511 | 0.81892 | 0.90227 | 0.87237 | 0.87396 | 0.85763 | 0.86056 | 0.89799 | 0.96124 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 63.6 | 77.4 | 81.6 | 73.6 | 113.8 | 76 | 115.3 | 107.2 | 62.7 | 34.2 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1352.9 | 5437.7 | 29620.7 | 3292.5 | 227.7 | -455.5 | 3064.6 | 7635.3 | 334.9 | -1860.8 | 6113.2 | 1120.9 | 3255.5 | 668.6 | 256.7 | 224.1 | 282.6 | 105.8 | 72.92 | 25.4 | 62 | 1.0645 | 1.053 | 1.0528 | 1.0163 | 0 | 0 | 129 | 0 | 1594 | 2008.5 | 359.5 | 272.7 | 86.8 | 0.95561 | 0.95514 | 0.8854 | 0.84101 | 0.89429 | 0.88168 | 0.94671 | 0.92676 | 0.94555 | 0.93433 | 0.9315 | 0.95479 | 0.98406 | 17 | 12
p18otc360_brgo_brkp.sav | 8111.3 | 3729.9 | 1107.5 | 1896.8 | 2487 | 1596.9 | 1642.4 | 800.1 | 365.6 | 735.5 | 735.5 | 96.1 | 152.3 | 78.5 | 25 | 25.6 | 1848.4 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.2 | 2091.3 | -1627.3 | -838.9 | -379.3 | 690.5 | -497.8 | 787.2 | -67 | 144.1 | -264.9 | 548 | 521.2 | -78.4 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2534.7 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 173.2 | 1358.1 | 3276.9 | 63.5 | 24.1 | 19.5 | 10.5 | 10 | 10 | 0 | 0.93119 | 0.92258 | 0.91549 | 0.71621 | 0.77827 | 0.74746 | 0.75082 | 0.86967 | 0.79418 | 0.7631 | 0.78655 | 0.78557 | 0.84278 | 0.92577 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 66.2 | 80.6 | 83.8 | 82.7 | 138.4 | 76.5 | 116.3 | 108.1 | 63.6 | 34.5 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1363.2 | 5437.9 | 29631 | 3292.5 | 238.5 | -465.2 | 3065.8 | 7635.3 | 345.5 | -1870.3 | 6114.3 | 1120.9 | 3258 | 668.8 | 256.9 | 224.2 | 260.2 | 105.4 | 78.58 | 25.4 | 60.3 | 1.0607 | 1.0489 | 1.0493 | 1.0133 | 0 | 0 | 129 | 0 | 1596.9 | 2012.9 | 359.5 | 272.7 | 86.8 | 0.9267 | 0.9238 | 0.80116 | 0.75521 | 0.83025 | 0.80836 | 0.9125 | 0.8437 | 0.82561 | 0.85689 | 0.85033 | 0.89609 | 0.94775 | 18 | 13
p18otc360_brgo_brkp_s.sav | 8103 | 3730.8 | 1107.5 | 1896.8 | 2485.7 | 1587.2 | 1642.4 | 787.7 | 382.4 | 736.1 | 736.1 | 95.9 | 154.2 | 79.1 | 25 | 25.6 | 1851.9 | 330 | 330 | 810.7 | 815 | 2285.7 | 141 | 2124.3 | 2092.2 | -1616 | -831 | -368.8 | 689.6 | -503.7 | 788.2 | -62.8 | 140.7 | -261.6 | 544.8 | 519.3 | -76.1 | 288 | 591 | 469 | 387.2 | 195.2 | 78 | 309.2 | -77.4 | 151 | 39 | 59 | 2534.7 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 172.1 | 1359.2 | 3276.9 | 63.6 | 24.1 | 19.3 | 10.4 | 10 | 10 | 0 | 0.93641 | 0.93218 | 0.9256 | 0.75002 | 0.81808 | 0.76938 | 0.77688 | 0.88134 | 0.81837 | 0.8131 | 0.80098 | 0.80083 | 0.85372 | 0.93365 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 66.1 | 80.5 | 83.7 | 82 | 136.5 | 76.2 | 115.7 | 107.7 | 63.2 | 34.5 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1358.2 | 5440.9 | 29629.1 | 3292.5 | 236.5 | -463.2 | 3065.8 | 7635.3 | 343.6 | -1868.8 | 6114 | 1120.9 | 3257.5 | 668.8 | 256.9 | 224.2 | 273.3 | 109.1 | 77.343 | 25.4 | 64.1 | 1.0622 | 1.0506 | 1.0508 | 1.0144 | 0 | 0 | 129 | 0 | 1587.2 | 2002.2 | 359.5 | 272.7 | 86.8 | 0.93634 | 0.93401 | 0.83898 | 0.79384 | 0.8546 | 0.83642 | 0.92475 | 0.8694 | 0.8797 | 0.87261 | 0.86685 | 0.90772 | 0.95581 | 19 | 13
p18otc365.sav | 8033.5 | 4125.4 | 1107.5 | 1896.8 | 2300 | 1796.3 | 1840 | 836 | 364.5 | 742 | 742 | 91.8 | 148.9 | 74.6 | 24.6 | 25.1 | 1849 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2091.8 | -1037.2 | -379.1 | 252.8 | 1831.6 | -915.4 | 565.6 | 84.1 | 145.1 | -266 | 549.2 | 472.6 | -79.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130 | 1394.3 | 3270 | 67.2 | 22.7 | 19.3 | 8.6 | 10 | 10 | 0 | 0.97317 | 0.99285 | 0.98832 | 0.8742 | 1.0066 | 0.88132 | 0.90711 | 0.94247 | 0.9382 | 0.92093 | 0.91508 | 0.92088 | 0.938 | 0.9747 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 56.5 | 68.8 | 71.8 | 57.5 | 71.2 | 70 | 101.2 | 94.5 | 49.6 | 32 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1292.2 | 5376.3 | 29499.2 | 3273.9 | 243.8 | 646 | 4163.7 | 7635.3 | 326.1 | -2073.8 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 277.6 | 86.9 | 59.568 | 28.7 | 44.7 | 1.0754 | 1.0669 | 1.0657 | 1.028 | 0 | 0 | 129 | 0 | 1796.3 | 2172.9 | 364.5 | 277.6 | 86.9 | 0.99285 | 0.98832 | 0.8742 | 1.0066 | 0.88132 | 0.90711 | 0.94247 | 0.9382 | 0.92093 | 0.91508 | 0.92088 | 0.938 | 0.9747 | 0 | 0
p18otc365_amps.sav | 8203.8 | 4194.4 | 1107.5 | 1896.8 | 2298.7 | 2009.8 | 1840 | 1082.5 | 110.5 | 739.9 | 739.9 | 84.4 | 128.5 | 64.3 | 23.5 | 24 | 1804.4 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2080.1 | -1169.9 | -464.6 | 130 | 1863.2 | -884.2 | 540.4 | 58.3 | 190.1 | -310.6 | 593.7 | 501.3 | -112.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.3 | 1431.8 | 3270 | 62.3 | 16 | 26.6 | 9.9 | 10 | 10 | 0 | 0.99416 | 1.0427 | 1.034 | 0.8742 | 1.0066 | 0.88132 | 0.90711 | 1.0057 | 0.95056 | 0.93428 | 0.90054 | 0.90563 | 0.9274 | 0.97576 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 0 | 30.6 | 37.3 | 0 | 70.4 | 100.2 | 73.4 | 107.5 | 98 | 53.1 | 32.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1331.9 | 5336.7 | 29499.2 | 3273.9 | 254.3 | 635.4 | 4163.7 | 7581.2 | 324.2 | -2017.8 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 0 | 110.5 | 78.187 | 28.7 | 67.3 | 1.0758 | 1.0655 | 1.0635 | 1.028 | 0 | 0 | 129 | 0 | 2009.8 | 2407 | 364.5 | 277.6 | 86.9 | 1.0502 | 1.0462 | 1 | 1 | 1 | 1 | 1.0671 | 1.0132 | 1.0145 | 0.98411 | 0.98344 | 0.9887 | 1.0011 | 1 | 1
p18otc365_amps_s.sav | 8202.8 | 4194.6 | 1107.5 | 1896.8 | 2298.7 | 2008.4 | 1840 | 1080.8 | 112.6 | 739.9 | 739.9 | 84.3 | 128.9 | 64.4 | 23.5 | 24 | 1804.9 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2080.3 | -1168.5 | -463.6 | 131.4 | 1862.9 | -884.7 | 540.8 | 58.7 | 189.6 | -310.1 | 593.2 | 500.9 | -112.3 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.4 | 1431.7 | 3270 | 62.3 | 16 | 26.6 | 9.9 | 10 | 10 | 0 | 0.9954 | 1.045 | 1.037 | 0.8742 | 1.0066 | 0.88132 | 0.90711 | 1.006 | 0.96639 | 0.97855 | 0.90749 | 0.91292 | 0.93204 | 0.97826 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 0 | 30.7 | 37.4 | 0 | 70.6 | 99.6 | 73.4 | 107.5 | 98 | 53.1 | 32.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1331.5 | 5337.1 | 29499.2 | 3273.9 | 254.2 | 635.6 | 4163.7 | 7581.2 | 324 | -2017.7 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 0 | 112.6 | 78.08 | 28.7 | 69.4 | 1.076 | 1.0657 | 1.0636 | 1.0281 | 0 | 0 | 129 | 0 | 2008.4 | 2405.5 | 364.5 | 277.6 | 86.9 | 1.0526 | 1.0493 | 1 | 1 | 1 | 1 | 1.0674 | 1.03 | 1.0626 | 0.99171 | 0.99136 | 0.99365 | 1.0037 | 2 | 1
p18otc365_dsbg.sav | 8087.7 | 4137.4 | 1107.5 | 1896.8 | 2299.5 | 1864.5 | 1840 | 916 | 284.9 | 745.1 | 745.1 | 89.1 | 135.9 | 66.8 | 24.2 | 24.7 | 1831 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2087.3 | -1090.3 | -414.9 | 202.4 | 1848.4 | -902.6 | 552.5 | 70.7 | 163.5 | -284.3 | 567.5 | 485.8 | -93.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.4 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 111.1 | 1413.2 | 3270 | 65.4 | 20.4 | 21.9 | 9 | 10 | 10 | 0 | 0.97622 | 0.99786 | 0.99514 | 0.85802 | 0.94409 | 0.86418 | 0.88742 | 0.93403 | 0.98436 | 0.9707 | 0.94899 | 0.95639 | 0.96717 | 0.97876 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 50.2 | 61.1 | 75.1 | 18.1 | 45.4 | 71.2 | 103.5 | 95.8 | 51 | 32.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1304.9 | 5363.6 | 29499.2 | 3273.9 | 248.1 | 641.6 | 4163.7 | 7635.3 | 330.2 | -2077.9 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 284.9 | 0 | 63.077 | 28.7 | -41.6 | 1.0748 | 1.0658 | 1.0646 | 1.0275 | 0 | 0 | 129 | 0 | 1864.5 | 2248.3 | 364.5 | 277.6 | 86.9 | 1.005 | 1.0069 | 0.98149 | 0.93791 | 0.98055 | 0.97829 | 0.99104 | 1.0492 | 1.054 | 1.0371 | 1.0386 | 1.0311 | 1.0042 | 3 | 2
p18otc365_bloxhcb.sav | 8145.3 | 4137.3 | 1107.5 | 1896.8 | 2299.8 | 1658.9 | 1840 | 797.4 | 371.4 | 730.4 | 730.4 | 91.4 | 147.7 | 74.2 | 24.6 | 25.1 | 1823.6 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2084.5 | -925.2 | -557.8 | 313.8 | 1855.9 | -880.6 | 525.4 | 43.3 | 170.1 | -290.7 | 573.9 | 492.5 | -97.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 136.6 | 1387.7 | 3270 | 67.8 | 23.5 | 18.1 | 8.8 | 10 | 10 | 0 | 0.96814 | 0.98236 | 0.97779 | 0.84427 | 0.92813 | 0.85504 | 0.87689 | 0.9283 | 0.91934 | 0.9005 | 0.89763 | 0.90258 | 0.92432 | 0.96706 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 58.6 | 71.4 | 75 | 61.6 | 81.6 | 72.7 | 132.4 | 0 | 76.8 | 32.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1346.9 | 5321.7 | 29499.2 | 3273.9 | 218.7 | 671.1 | 4163.7 | 7635.3 | 329.7 | -2077.4 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 279.4 | 92 | 63.67 | 28.7 | 49.5 | 1.0744 | 1.0648 | 1.0627 | 1.0272 | 0 | 0 | 129 | 0 | 1658.9 | 2135.1 | 364.5 | 277.6 | 86.9 | 0.98943 | 0.98935 | 0.96576 | 0.92205 | 0.97018 | 0.96669 | 0.98496 | 0.9799 | 0.97782 | 0.98093 | 0.98013 | 0.98542 | 0.99216 | 4 | 3
p18otc365_bloxhcb_s.sav | 8144 | 4137.6 | 1107.5 | 1896.8 | 2299.8 | 1657.3 | 1840 | 795.3 | 374.2 | 730.3 | 730.3 | 91.3 | 148.4 | 74.4 | 24.5 | 25.1 | 1824.2 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2084.6 | -923.4 | -556.4 | 315.6 | 1855.4 | -881.2 | 526 | 43.9 | 169.5 | -290.1 | 573.3 | 492.1 | -97.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 136.6 | 1387.7 | 3270 | 67.8 | 23.5 | 18.1 | 8.7 | 10 | 10 | 0 | 0.96967 | 0.98517 | 0.98136 | 0.84687 | 0.93116 | 0.8567 | 0.87881 | 0.92921 | 0.9356 | 0.94445 | 0.90486 | 0.91016 | 0.92923 | 0.96974 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 58.5 | 71.3 | 75 | 62.1 | 80.4 | 72.7 | 132.3 | 0 | 76.7 | 32.3 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1346.3 | 5322.3 | 29499.2 | 3273.9 | 218.6 | 671.2 | 4163.7 | 7635.3 | 329.5 | -2077.2 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 280.3 | 93.9 | 63.529 | 28.7 | 51.4 | 1.0747 | 1.0651 | 1.0629 | 1.0274 | 0 | 0 | 129 | 0 | 1657.3 | 2133.3 | 364.5 | 277.6 | 86.9 | 0.99226 | 0.99296 | 0.96874 | 0.92506 | 0.97206 | 0.9688 | 0.98593 | 0.99723 | 1.0255 | 0.98883 | 0.98836 | 0.99065 | 0.99491 | 5 | 3
p18otc365_blhcoxll.sav | 8450.1 | 4147.8 | 1107.5 | 1896.8 | 2298.8 | 2075.4 | 1840 | 736.3 | 376.5 | 711 | 711 | 90.3 | 144.7 | 73.1 | 24.4 | 24.9 | 1779.4 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2072.8 | -783.6 | -788.6 | 393.1 | 1888.9 | -829.6 | 469.9 | -12.8 | 213.5 | -333.5 | 616.5 | 521.9 | -127.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149.2 | 1375.1 | 3270 | 68.1 | 24.8 | 16.9 | 7.4 | 10 | 10 | 0 | 0.96133 | 0.96514 | 0.96019 | 0.78708 | 0.86151 | 0.8025 | 0.81587 | 0.8984 | 0.88322 | 0.8612 | 0.8614 | 0.86452 | 0.8954 | 0.94935 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 62.3 | 75.9 | 80.3 | 68.9 | 99.6 | 24.3 | 0 | 0 | 109.5 | 32.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1409.5 | 5259.5 | 29499.2 | 3273.9 | 193.3 | 696.4 | 4163.7 | 7635.3 | 339.6 | -2087.2 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 277.2 | 99.4 | 71.283 | 28.7 | 56.2 | 1.0758 | 1.0719 | 1.0719 | 1.0289 | 0 | 0 | 129 | 0 | 2075.4 | 2075.4 | 364.5 | 277.6 | 86.9 | 0.97209 | 0.97154 | 0.90034 | 0.85587 | 0.91057 | 0.89942 | 0.95324 | 0.9414 | 0.93514 | 0.94134 | 0.9388 | 0.95458 | 0.97399 | 6 | 4
p18otc365_blhcoxll_s.sav | 8448.3 | 4148.2 | 1107.5 | 1896.8 | 2298.8 | 2073.1 | 1840 | 733.7 | 379.8 | 710.9 | 710.9 | 90.2 | 145.4 | 73.3 | 24.4 | 24.9 | 1780 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2072.8 | -781.5 | -786.7 | 395.3 | 1888.5 | -830.5 | 470.8 | -11.9 | 213 | -333 | 616 | 521.6 | -127.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149.1 | 1375.3 | 3270 | 68.1 | 24.7 | 16.8 | 7.4 | 10 | 10 | 0 | 0.96292 | 0.96807 | 0.96388 | 0.79006 | 0.86499 | 0.80454 | 0.81825 | 0.8996 | 0.8994 | 0.90418 | 0.86877 | 0.87227 | 0.90044 | 0.95225 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 62.2 | 75.7 | 80.3 | 69.1 | 98.5 | 24.3 | 0 | 0 | 109.4 | 32.9 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1408.6 | 5260.4 | 29499.2 | 3273.9 | 193.2 | 696.6 | 4163.7 | 7635.3 | 339.3 | -2086.9 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 278.3 | 101.5 | 71.102 | 28.7 | 58.4 | 1.076 | 1.0722 | 1.072 | 1.0291 | 0 | 0 | 129 | 0 | 2073.1 | 2073.1 | 364.5 | 277.6 | 86.9 | 0.97504 | 0.97527 | 0.90375 | 0.85933 | 0.91288 | 0.90204 | 0.95451 | 0.95864 | 0.98181 | 0.94939 | 0.94721 | 0.95996 | 0.97697 | 7 | 4
p18otc365_mpsl.sav | 7902.5 | 4263.2 | 1107.5 | 1896.8 | 2300.4 | 1682.9 | 1840 | 775 | 373.3 | 723.5 | 723.5 | 91.3 | 147 | 74.1 | 24.5 | 25.1 | 1809 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2080.3 | -820.2 | 0 | 425.8 | 1894.2 | -802.5 | 421.7 | -61.1 | 184.5 | -304.9 | 588 | 517.6 | -107.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 142.8 | 1381.5 | 3270 | 68.4 | 24.1 | 17.7 | 8.9 | 10 | 10 | 0 | 0.96343 | 0.97214 | 0.96745 | 0.81299 | 0.89173 | 0.82483 | 0.84191 | 0.90892 | 0.89946 | 0.8789 | 0.87632 | 0.88021 | 0.90639 | 0.95447 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 60.4 | 73.5 | 77.6 | 65.2 | 90.4 | 77.3 | 118 | 107.2 | 64.4 | 32.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1283.8 | 5384.6 | 29499.2 | 3273.9 | 284.2 | 605.6 | 4163.7 | 7635.3 | 331.6 | -2079.2 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 277.5 | 95.8 | 67.57 | 28.7 | 53 | 1.074 | 1.0642 | 1.0627 | 1.0269 | 0 | 0 | 129 | 0 | 1682.9 | 2114.3 | 364.5 | 277.6 | 86.9 | 0.97914 | 0.97888 | 0.92998 | 0.88589 | 0.9359 | 0.92812 | 0.9644 | 0.95871 | 0.95436 | 0.95764 | 0.95584 | 0.9663 | 0.97925 | 8 | 5
p18otc365_mpsl_s.sav | 7901.6 | 4263 | 1107.5 | 1896.8 | 2300.4 | 1681.5 | 1840 | 772.8 | 376.3 | 723.5 | 723.5 | 91.2 | 147.6 | 74.3 | 24.5 | 25.1 | 1809.7 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2080.5 | -818.9 | 0 | 427.1 | 1893.6 | -803.7 | 423 | -59.8 | 183.8 | -304.2 | 587.3 | 517.1 | -107.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 142.7 | 1381.7 | 3270 | 68.4 | 24.1 | 17.7 | 8.9 | 10 | 10 | 0 | 0.96499 | 0.97503 | 0.97109 | 0.81595 | 0.89518 | 0.82687 | 0.84428 | 0.91012 | 0.91572 | 0.92237 | 0.88375 | 0.88801 | 0.91148 | 0.95736 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 60.2 | 73.3 | 77.6 | 65.5 | 89.3 | 77.3 | 117.9 | 107.1 | 64.3 | 32.8 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1283.3 | 5385.1 | 29499.2 | 3273.9 | 283.8 | 606 | 4163.7 | 7635.3 | 331.3 | -2078.9 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 278.5 | 97.7 | 67.386 | 28.7 | 55 | 1.0742 | 1.0645 | 1.0629 | 1.027 | 0 | 0 | 129 | 0 | 1681.5 | 2112.5 | 364.5 | 277.6 | 86.9 | 0.98205 | 0.98257 | 0.93337 | 0.88932 | 0.93822 | 0.93074 | 0.96567 | 0.97604 | 1.0016 | 0.96576 | 0.96431 | 0.97173 | 0.98221 | 9 | 5
p18otc365_angr1.sav | 8046.2 | 4122.5 | 1107.5 | 1896.8 | 2299.8 | 1812.6 | 1840 | 861.6 | 336.4 | 726 | 726 | 95.2 | 166.3 | 83 | 25.1 | 25.7 | 1847.4 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2090.5 | -1055.9 | -392.4 | 234.8 | 1834.8 | -911 | 559.5 | 77.8 | 145.7 | -266.5 | 549.7 | 474.1 | -79.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 132 | 1392.5 | 3270 | 69.9 | 25.2 | 16.4 | 8.5 | 10 | 10 | 0 | 0.96044 | 0.95495 | 0.95166 | 0.86549 | 0.99603 | 0.88578 | 0.91223 | 0.94615 | 0.91266 | 0.89325 | 0.91091 | 0.91651 | 0.93635 | 0.97332 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 119 | 68.2 | 53 | 65.2 | 70.4 | 101.9 | 94.9 | 50.1 | 32 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1301.2 | 5367.2 | 29499.2 | 3273.9 | 244.6 | 645.1 | 4163.7 | 7635.3 | 324.6 | -2072.4 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 259.3 | 77.1 | 56.815 | 28.7 | 35.1 | 1.075 | 1.0663 | 1.0653 | 1.0277 | 0 | 0 | 129 | 0 | 1812.6 | 2191.2 | 364.5 | 277.6 | 86.9 | 0.96183 | 0.96291 | 0.99004 | 0.98951 | 1.0051 | 1.0056 | 1.0039 | 0.97278 | 0.96994 | 0.99544 | 0.99526 | 0.99824 | 0.99858 | 10 | 6
p18otc365_angr2.sav | 8045.7 | 4125.4 | 1107.5 | 1896.8 | 2299.8 | 1811.7 | 1840 | 856.2 | 342.3 | 727.8 | 727.8 | 94.7 | 164.6 | 82 | 25.1 | 25.6 | 1847.5 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2090.6 | -1052 | -389.5 | 238.6 | 1834.1 | -912.1 | 561 | 79.4 | 145.7 | -266.5 | 549.7 | 473.8 | -80 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.5 | 1393 | 3270 | 69.5 | 24.9 | 16.8 | 8.5 | 10 | 10 | 0 | 0.96336 | 0.96499 | 0.96111 | 0.8703 | 1.0019 | 0.88711 | 0.91376 | 0.94655 | 0.91996 | 0.90118 | 0.91311 | 0.91881 | 0.93771 | 0.97418 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 91.8 | 0 | 68.7 | 53.6 | 65.7 | 70.3 | 101.8 | 94.8 | 50 | 32 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1296.8 | 5371.6 | 29499.2 | 3273.9 | 244.5 | 645.3 | 4163.7 | 7635.3 | 324.8 | -2072.6 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 263.4 | 79 | 57.096 | 28.7 | 36.9 | 1.0749 | 1.0663 | 1.0653 | 1.0277 | 0 | 0 | 129 | 0 | 1811.7 | 2190.1 | 364.5 | 277.6 | 86.9 | 0.97194 | 0.97247 | 0.99554 | 0.9953 | 1.0066 | 1.0073 | 1.0043 | 0.98056 | 0.97855 | 0.99785 | 0.99775 | 0.99969 | 0.99947 | 11 | 7
p18otc365_angr12.sav | 8124.3 | 4089.3 | 1107.5 | 1896.8 | 2299.2 | 1913.5 | 1840 | 980.2 | 150.3 | 673.8 | 673.8 | 111 | 210.7 | 105.4 | 28.1 | 28.7 | 1831.6 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2087.9 | -1185.2 | -485.1 | 110.2 | 1855 | -877.6 | 515.2 | 32.9 | 152.4 | -272.4 | 555.4 | 483 | -80.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1736.1 | 202.9 | 1331.9 | 3270 | 77.3 | 40.4 | 6.4 | 10.4 | 10 | 10 | 0 | 0.82801 | 0.67985 | 0.67167 | 0.75578 | 0.8623 | 0.86073 | 0.88345 | 0.93766 | 0.67842 | 0.63322 | 0.83585 | 0.83762 | 0.88879 | 0.94232 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 0 | 50.2 | 31.7 | 80.9 | 72.6 | 106.4 | 97.7 | 53.1 | 32.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1318.6 | 5349.9 | 29499.2 | 3273.9 | 253.1 | 636.6 | 4163.7 | 7635.3 | 324.5 | -2072.2 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 134 | 16.3 | 40.682 | 28.7 | -26.2 | 1.0706 | 1.061 | 1.0612 | 1.0249 | 0 | 0 | 129 | 0 | 1913.5 | 2306.5 | 364.5 | 277.6 | 86.9 | 0.68475 | 0.67961 | 0.86454 | 0.85666 | 0.97664 | 0.97392 | 0.9949 | 0.72311 | 0.68759 | 0.91342 | 0.90959 | 0.94754 | 0.96678 | 12 | 8
p18otc365_grgr.sav | 8074.7 | 4112.6 | 1107.5 | 1896.8 | 2299.9 | 1851 | 1840 | 903.4 | 268.1 | 655.4 | 655.4 | 148.6 | 209.4 | 103.4 | 33.1 | 33.8 | 1839.1 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2085.6 | -1100.5 | -424.2 | 191.8 | 1843.5 | -899.7 | 545 | 63.1 | 150.5 | -271 | 554.2 | 479 | -82.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.2 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 153.9 | 1371 | 3270 | 83.4 | 57 | 7.6 | 13 | 10 | 10 | 0 | 0.87132 | 0.87775 | 0.87197 | 0.85396 | 0.98205 | 0.89895 | 0.92731 | 0.95531 | 0.85534 | 0.83069 | 0.90163 | 0.90678 | 0.93269 | 0.96976 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 32.6 | 39.8 | 59.4 | 40.8 | 54.4 | 71.2 | 103.5 | 95.9 | 51.1 | 32.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1307.1 | 5361.6 | 29499.2 | 3273.9 | 247 | 642.7 | 4163.7 | 7635.3 | 322.5 | -2070.3 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 215.8 | 52.3 | 49.111 | 28.7 | 10.6 | 1.0746 | 1.0653 | 1.0644 | 1.0279 | 0 | 0 | 129 | 0 | 1851 | 2234.9 | 364.5 | 277.6 | 86.9 | 0.88407 | 0.88228 | 0.97685 | 0.97562 | 1.02 | 1.0223 | 1.0136 | 0.91168 | 0.90201 | 0.9853 | 0.98469 | 0.99434 | 0.99493 | 13 | 9
p18otc365_anpf.sav | 8194.9 | 4145.4 | 1107.5 | 1896.8 | 2298.8 | 2001.1 | 1840 | 1076.2 | 98.8 | 738.2 | 738.2 | 84.3 | 128.5 | 64.3 | 23.5 | 24 | 1800.9 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2079.2 | -1211.9 | -498.1 | 88 | 1872.9 | -870.5 | 522.4 | 40 | 193.5 | -313.9 | 597 | 506.8 | -115 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 106.8 | 1417.4 | 3270 | 62.4 | 16.1 | 26.5 | 9.9 | 10 | 10 | 0 | 0.99395 | 1.0422 | 1.0334 | 1.1142 | 1.0139 | 1.0798 | 1.1314 | 1.0403 | 0.94807 | 0.9316 | 0.89962 | 0.90466 | 0.92785 | 0.97828 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 30.8 | 37.6 | 0 | 71.5 | 103.4 | 73.8 | 108.4 | 98.7 | 53.9 | 32.4 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1331 | 5337.5 | 29499.2 | 3273.9 | 257.6 | 632.2 | 4163.7 | 7635.3 | 325.2 | -2072.9 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | -13.3 | 112.1 | 81.478 | 28.7 | 68.8 | 1.0758 | 1.0655 | 1.0634 | 1.028 | 0 | 0 | 129 | 0 | 2001.1 | 2401.3 | 364.5 | 277.6 | 86.9 | 1.0497 | 1.0457 | 1.2745 | 1.0073 | 1.2252 | 1.2473 | 1.1038 | 1.0105 | 1.0116 | 0.98311 | 0.98239 | 0.98918 | 1.0037 | 14 | 10
p18otc365_antbdy.sav | 8057.5 | 4125.4 | 1107.5 | 1896.8 | 2299.7 | 1826.9 | 1840 | 871.8 | 330.4 | 741.9 | 741.9 | 90.7 | 145.9 | 73 | 24.4 | 25 | 1842.7 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2090.2 | -1066.7 | -399.6 | 225.2 | 1833 | -905.4 | 559.2 | 77.5 | 151.5 | -272.3 | 555.5 | 476.3 | -84.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 121.9 | 1402.4 | 3270 | 66.5 | 21.7 | 20.4 | 8.7 | 10 | 10 | 0 | 0.97669 | 1.0009 | 0.99572 | 0.88618 | 1.0211 | 0.85137 | 0.87264 | 0.87416 | 0.93997 | 0.92284 | 0.90583 | 0.91118 | 0.92727 | 0.96297 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 52.6 | 64 | 61.5 | 58.4 | 71.8 | 70.6 | 102.4 | 95.2 | 50.3 | 32.1 | 560 | 560 | 545 | 545 | 2210 | 22788.6 | 1297.2 | 5371.3 | 29499.2 | 3273.9 | 245.2 | 644.5 | 4163.7 | 7635.3 | 334.8 | -2082.6 | 5891.6 | 1100 | 3221.2 | 664.3 | 314.4 | 220 | 241.7 | 88.7 | 51.448 | 28.7 | 46.5 | 1.0756 | 1.0668 | 1.0655 | 1.0281 | 0 | 0 | 129 | 0 | 1826.9 | 2207.2 | 364.5 | 277.6 | 86.9 | 1.0081 | 1.0075 | 1.0137 | 1.0144 | 0.96602 | 0.962 | 0.92752 | 1.0019 | 1.0021 | 0.98989 | 0.98947 | 0.98856 | 0.98797 | 15 | 11
p18otc365_brbo_brkp.sav | 8236.5 | 3805.8 | 1107.5 | 1896.8 | 2486.7 | 1732.5 | 1840 | 778.7 | 368.9 | 726.5 | 726.5 | 92.5 | 148.7 | 76 | 24.5 | 25.1 | 1819.8 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.5 | 2085.1 | -1703.6 | -884.4 | -445 | 707.4 | -578.9 | 712.5 | -136.9 | 175 | -295.5 | 578.6 | 533.9 | -100.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.9 | 151 | 39 | 59 | 2537 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 162.9 | 1370.7 | 3279.2 | 69.1 | 25.1 | 17.2 | 9.7 | 10 | 10 | 0 | 0.94039 | 0.93643 | 0.93116 | 0.7278 | 0.79195 | 0.75531 | 0.76017 | 0.87545 | 0.84087 | 0.8148 | 0.83757 | 0.83944 | 0.88254 | 0.95045 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 64.5 | 78.5 | 84.3 | 74.9 | 117.7 | 78.8 | 120.6 | 110.5 | 65.6 | 36.3 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1411.8 | 5610.7 | 29852.3 | 3292.5 | 242.4 | -460.9 | 3073.9 | 7635.3 | 346.6 | -2057.2 | 5928.5 | 1120.9 | 3283.1 | 677 | 317.1 | 224.2 | 266.3 | 102.6 | 78.188 | 28.7 | 58.6 | 1.0627 | 1.0507 | 1.0481 | 1.0164 | 0 | 0 | 129 | 0 | 1732.5 | 2163.9 | 364.5 | 277.6 | 86.9 | 0.94317 | 0.94216 | 0.83253 | 0.78677 | 0.85702 | 0.83801 | 0.92889 | 0.89626 | 0.88476 | 0.9153 | 0.91156 | 0.94087 | 0.97512 | 16 | 12
p18otc365_brbo_brkp_s.sav | 8228.7 | 3807.6 | 1107.5 | 1896.8 | 2485.4 | 1722.9 | 1840 | 766.6 | 384.7 | 726.8 | 726.8 | 92.3 | 150.5 | 76.6 | 24.6 | 25.1 | 1822.7 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2085.6 | -1693 | -876.9 | -435.2 | 705.9 | -583.8 | 714.9 | -132.8 | 172.2 | -292.8 | 575.8 | 532.2 | -99 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.9 | 151 | 39 | 59 | 2537 | 192 | 67.2 | 259.2 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.7 | 6.1 | 279.3 | 1745.2 | 161.9 | 1371.7 | 3279.2 | 69.2 | 25.1 | 16.9 | 9.6 | 10 | 10 | 0 | 0.9456 | 0.94598 | 0.94118 | 0.76102 | 0.831 | 0.77599 | 0.7847 | 0.8858 | 0.86437 | 0.86498 | 0.85006 | 0.85259 | 0.89156 | 0.95621 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 64.4 | 78.4 | 84.2 | 74.5 | 115.5 | 78.5 | 120.1 | 110.1 | 65.3 | 36.2 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1407 | 5615 | 29851.9 | 3292.5 | 240.7 | -459.2 | 3073.9 | 7635.3 | 345 | -2055.8 | 5928.3 | 1120.9 | 3282.9 | 677 | 317.1 | 224.2 | 279.2 | 105.5 | 77.03 | 28.7 | 61.7 | 1.0642 | 1.0524 | 1.0497 | 1.0175 | 0 | 0 | 129 | 0 | 1722.9 | 2153.5 | 364.5 | 277.6 | 86.9 | 0.95279 | 0.9523 | 0.87053 | 0.82556 | 0.88049 | 0.86506 | 0.93987 | 0.92131 | 0.93925 | 0.92895 | 0.92584 | 0.95049 | 0.98103 | 17 | 12
p18otc365_brgo_brkp.sav | 8243.9 | 3797.6 | 1107.5 | 1896.8 | 2492.2 | 1730 | 1840 | 778.6 | 355.1 | 725.7 | 725.7 | 93.9 | 148.2 | 76.5 | 24.7 | 25.2 | 1820 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.6 | 2085.6 | -1722.1 | -897.6 | -452.3 | 687.5 | -553.9 | 717 | -145.4 | 174.4 | -294.9 | 578 | 530.5 | -99.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.8 | 151 | 39 | 59 | 2537 | 192 | 67.4 | 259.4 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.8 | 6.1 | 279.4 | 1745.2 | 177.7 | 1356.3 | 3279.5 | 69.5 | 25.7 | 16.8 | 9.9 | 10 | 10 | 0 | 0.92768 | 0.91451 | 0.90722 | 0.67822 | 0.73324 | 0.7093 | 0.70478 | 0.84615 | 0.77931 | 0.74648 | 0.76858 | 0.76653 | 0.82657 | 0.91146 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 67.2 | 81.8 | 86.3 | 84 | 140.3 | 79.1 | 121.4 | 111.3 | 66.4 | 36.6 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1421.8 | 5616.1 | 29867.7 | 3292.5 | 252.9 | -470.3 | 3075 | 7635.3 | 356.7 | -2065.8 | 5929.9 | 1122 | 3285.1 | 677.6 | 317.2 | 224.4 | 251.5 | 103.6 | 83.454 | 28.7 | 58.5 | 1.0596 | 1.0473 | 1.0451 | 1.0138 | 0 | 0 | 129 | 0 | 1730 | 2162.6 | 364.5 | 277.6 | 86.9 | 0.9211 | 0.91794 | 0.77582 | 0.72844 | 0.80482 | 0.77695 | 0.8978 | 0.83064 | 0.81057 | 0.83991 | 0.83239 | 0.88121 | 0.93512 | 18 | 13
p18otc365_brgo_brkp_s.sav | 8236.6 | 3803.7 | 1107.5 | 1896.8 | 2493.2 | 1718.9 | 1840 | 763.9 | 374.3 | 726.1 | 726.1 | 93.7 | 150.3 | 77.3 | 24.7 | 25.2 | 1823.5 | 330 | 330 | 813 | 815 | 2288 | 141 | 2126.5 | 2086.2 | -1709 | -888.3 | -440.2 | 687.4 | -561.5 | 724.5 | -139.1 | 171 | -291.5 | 574.6 | 529.1 | -97.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.8 | 151 | 39 | 59 | 2537 | 192 | 67.4 | 259.4 | 12.2 | 40.8 | 51 | 26.5 | 14.3 | 46.9 | 42.8 | 38.8 | 6.1 | 279.4 | 1745.2 | 176.6 | 1357.4 | 3279.5 | 69.6 | 25.8 | 16.5 | 9.8 | 10 | 10 | 0 | 0.93349 | 0.92493 | 0.91826 | 0.71422 | 0.77592 | 0.73504 | 0.73593 | 0.86157 | 0.80613 | 0.79919 | 0.78841 | 0.78754 | 0.84297 | 0.92492 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 67.1 | 81.6 | 86.2 | 83.2 | 138.6 | 78.8 | 120.8 | 110.8 | 65.9 | 36.5 | 0 | 0 | 545 | 545 | 1090 | 22788.6 | 1416.3 | 5622.3 | 29868.4 | 3292.5 | 250.4 | -467.8 | 3075 | 7635.3 | 354.2 | -2063.3 | 5930 | 1122 | 3285.2 | 677.6 | 317.2 | 224.4 | 266.5 | 107.9 | 81.962 | 28.7 | 62.8 | 1.0613 | 1.0493 | 1.0469 | 1.0152 | 0 | 0 | 129 | 0 | 1718.9 | 2150.3 | 364.5 | 277.6 | 86.9 | 0.93159 | 0.92911 | 0.817 | 0.77084 | 0.83402 | 0.81129 | 0.91416 | 0.85923 | 0.86781 | 0.86157 | 0.8552 | 0.89869 | 0.94893 | 19 | 13
p18otc352b.sav | 7627 | 3886.2 | 1107.5 | 1896.8 | 2300 | 1665.4 | 1522.1 | 937.2 | 352.1 | 774.8 | 774.8 | 97.2 | 156.6 | 78.4 | 25.3 | 25.9 | 1932.8 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2112.7 | -778.3 | -213.7 | 436.7 | 1612 | -543.2 | 802.7 | 312.1 | 55.9 | -177.7 | 460.9 | 481.3 | -11.5 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.6 | 1394.8 | 3264.1 | 45 | 19.3 | 22.1 | 8.6 | 10 | 10 | 0 | 0.97767 | 1.0016 | 0.99697 | 0.92336 | 1.0313 | 0.92939 | 0.96201 | 0.97153 | 0.94912 | 0.93272 | 0.9277 | 0.9341 | 0.95004 | 0.98583 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 53.8 | 65.6 | 65.1 | 56.1 | 69.7 | 64.4 | 89.8 | 87.5 | 42.9 | 33.5 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1179.8 | 4776.7 | 28787.4 | 3273.9 | 203.2 | 146.2 | 3623.3 | 7635.3 | 297.9 | -974.3 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 265.4 | 86.7 | 51.773 | 21.7 | 44.5 | 1.0772 | 1.0688 | 1.0691 | 1.0286 | 0 | 0 | 129 | 0 | 1665.4 | 2001.1 | 352.1 | 265.4 | 86.7 | 1.0016 | 0.99697 | 0.92336 | 1.0313 | 0.92939 | 0.96201 | 0.97153 | 0.94912 | 0.93272 | 0.9277 | 0.9341 | 0.95004 | 0.98583 | 0 | 0
p18otc352b_amps.sav | 7788.7 | 3954.2 | 1107.5 | 1896.8 | 2298.8 | 1866.4 | 1522.1 | 1170.2 | 108 | 772 | 772 | 90.4 | 137.1 | 69 | 24.3 | 24.8 | 1889.7 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2100.9 | -904.6 | -295.6 | 318.2 | 1642 | -512.3 | 779.7 | 287.9 | 99.6 | -221.1 | 504.3 | 510.4 | -45.2 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 20.7 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 103.9 | 1427.5 | 3264.1 | 40.5 | 13 | 29 | 10.1 | 10 | 10 | 0 | 0.99252 | 1.0376 | 1.03 | 0.92336 | 1.0313 | 0.92939 | 0.96201 | 1.0131 | 0.95315 | 0.93708 | 0.9106 | 0.91618 | 0.93719 | 0.98421 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 30.3 | 36.9 | 0 | 68.1 | 96.6 | 67.5 | 95.7 | 90.8 | 46 | 33.9 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1213.6 | 4743 | 28787.4 | 3273.9 | 211.8 | 137.6 | 3623.3 | 7581.2 | 298.5 | -920.8 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 0 | 108 | 68.984 | 21.7 | 64.9 | 1.0769 | 1.0674 | 1.0674 | 1.0283 | 0 | 0 | 129 | 0 | 1866.4 | 2222 | 352.1 | 265.4 | 86.7 | 1.0359 | 1.0331 | 1 | 1 | 1 | 1 | 1.0428 | 1.0042 | 1.0047 | 0.98157 | 0.98082 | 0.98647 | 0.99836 | 1 | 1
p18otc352b_amps_s.sav | 7787.7 | 3954.4 | 1107.5 | 1896.8 | 2298.8 | 1865.1 | 1522.1 | 1168.6 | 110 | 772 | 772 | 90.3 | 137.6 | 69.1 | 24.3 | 24.8 | 1890.2 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2101 | -903.2 | -294.6 | 319.5 | 1641.7 | -512.7 | 780.1 | 288.3 | 99.1 | -220.5 | 503.8 | 510 | -44.9 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 20.7 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104 | 1427.4 | 3264.1 | 40.5 | 13 | 29 | 10.1 | 10 | 10 | 0 | 0.99387 | 1.0401 | 1.0332 | 0.92336 | 1.0313 | 0.92939 | 0.96201 | 1.0134 | 0.96913 | 0.98157 | 0.91759 | 0.92351 | 0.94187 | 0.98673 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 30.4 | 37 | 0 | 68.4 | 95.9 | 67.4 | 95.6 | 90.7 | 46 | 33.9 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1213.3 | 4743.3 | 28787.4 | 3273.9 | 211.7 | 137.7 | 3623.3 | 7581.2 | 298.2 | -920.6 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 0 | 110 | 68.882 | 21.7 | 67 | 1.0771 | 1.0676 | 1.0675 | 1.0284 | 0 | 0 | 129 | 0 | 1865.1 | 2220.6 | 352.1 | 265.4 | 86.7 | 1.0384 | 1.0363 | 1 | 1 | 1 | 1 | 1.0431 | 1.0211 | 1.0524 | 0.9891 | 0.98866 | 0.9914 | 1.0009 | 2 | 1
p18otc352b_dsbg.sav | 7679.5 | 3899.1 | 1107.5 | 1896.8 | 2299.5 | 1730.9 | 1522.1 | 1014.2 | 275.3 | 777.9 | 777.9 | 94.5 | 143.8 | 70.9 | 24.9 | 25.5 | 1915.3 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2108.1 | -829.4 | -248.3 | 387.6 | 1628.3 | -531 | 790.7 | 299.5 | 73.9 | -195.7 | 478.9 | 494.7 | -25.6 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 20.9 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.2 | 1413.2 | 3264.1 | 43.3 | 17 | 24.6 | 9.1 | 10 | 10 | 0 | 0.98028 | 1.0062 | 1.0031 | 0.91001 | 1.0043 | 0.91537 | 0.94605 | 0.96466 | 0.99194 | 0.97884 | 0.96054 | 0.96847 | 0.97844 | 0.98979 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 47.8 | 58.2 | 68.4 | 17.2 | 44.8 | 65.5 | 91.9 | 88.7 | 44.1 | 33.6 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1190.7 | 4765.8 | 28787.4 | 3273.9 | 206.6 | 142.8 | 3623.3 | 7635.3 | 302.5 | -978.9 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 275.3 | 0 | 55.033 | 21.7 | -41.6 | 1.0766 | 1.0679 | 1.0683 | 1.0282 | 0 | 0 | 129 | 0 | 1730.9 | 2073.9 | 352.1 | 265.4 | 86.7 | 1.0046 | 1.0061 | 0.98554 | 0.97381 | 0.98491 | 0.98341 | 0.99293 | 1.0451 | 1.0494 | 1.0354 | 1.0368 | 1.0299 | 1.004 | 3 | 2
p18otc352b_bloxhcb.sav | 7727 | 3898.9 | 1107.5 | 1896.8 | 2299.9 | 1534.3 | 1522.1 | 899.9 | 362.2 | 764.3 | 764.3 | 96.7 | 156 | 78.4 | 25.3 | 25.8 | 1910.8 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2106 | -677.8 | -376.6 | 494.5 | 1633.4 | -512 | 767.9 | 275.9 | 77.8 | -199.5 | 482.7 | 499.7 | -28.5 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.8 | 1389.7 | 3264.1 | 45.5 | 20 | 21.1 | 8.6 | 10 | 10 | 0 | 0.97427 | 0.99415 | 0.98955 | 0.9013 | 0.99425 | 0.9099 | 0.93981 | 0.96082 | 0.93523 | 0.91771 | 0.91411 | 0.91986 | 0.93931 | 0.97992 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55.7 | 67.8 | 68 | 59.5 | 78.5 | 66.7 | 118 | 0 | 67.4 | 33.8 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1224 | 4732.6 | 28787.4 | 3273.9 | 183.3 | 166.1 | 3623.3 | 7635.3 | 301.6 | -978 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 270.7 | 91.6 | 55.078 | 21.7 | 49.2 | 1.0767 | 1.0677 | 1.0674 | 1.0282 | 0 | 0 | 129 | 0 | 1534.3 | 1965.2 | 352.1 | 265.4 | 86.7 | 0.99256 | 0.99256 | 0.97611 | 0.96406 | 0.97903 | 0.97692 | 0.98898 | 0.98537 | 0.98391 | 0.98535 | 0.98476 | 0.98871 | 0.99401 | 4 | 3
p18otc352b_bloxhcb_s.sav | 7725.7 | 3899 | 1107.5 | 1896.8 | 2299.9 | 1532.8 | 1522.1 | 898 | 364.7 | 764.3 | 764.3 | 96.7 | 156.6 | 78.5 | 25.3 | 25.8 | 1911.4 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2106.1 | -676.2 | -375.4 | 496.1 | 1633 | -512.6 | 768.4 | 276.4 | 77.2 | -198.9 | 482.1 | 499.3 | -28 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.8 | 1389.7 | 3264.1 | 45.5 | 20 | 21.1 | 8.5 | 10 | 10 | 0 | 0.97566 | 0.99674 | 0.99286 | 0.90364 | 0.99694 | 0.91141 | 0.94154 | 0.96167 | 0.95125 | 0.9618 | 0.92122 | 0.92731 | 0.94414 | 0.98255 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 55.7 | 67.8 | 67.9 | 60 | 77.3 | 66.7 | 118 | 0 | 67.3 | 33.8 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1223.6 | 4733 | 28787.4 | 3273.9 | 183.2 | 166.2 | 3623.3 | 7635.3 | 301.4 | -977.8 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 271.4 | 93.3 | 54.96 | 21.7 | 51 | 1.0769 | 1.0679 | 1.0675 | 1.0283 | 0 | 0 | 129 | 0 | 1532.8 | 1963.5 | 352.1 | 265.4 | 86.7 | 0.99515 | 0.99588 | 0.97864 | 0.96666 | 0.98065 | 0.97872 | 0.98985 | 1.0022 | 1.0312 | 0.99301 | 0.99273 | 0.99379 | 0.99667 | 5 | 3
p18otc352b_blhcoxll.sav | 8009.6 | 3920 | 1107.5 | 1896.8 | 2299 | 1907.8 | 1522.1 | 841.8 | 374.8 | 747.6 | 747.6 | 95.9 | 154.2 | 77.8 | 25.2 | 25.7 | 1873.9 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2095.1 | -549.8 | -582.6 | 570.2 | 1663 | -470.3 | 723.9 | 230.2 | 114.4 | -235.6 | 518.8 | 526.8 | -56.1 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 137.7 | 1380.8 | 3264.1 | 45.9 | 21.2 | 19.7 | 7.4 | 10 | 10 | 0 | 0.96994 | 0.98268 | 0.97786 | 0.86362 | 0.9506 | 0.87601 | 0.90102 | 0.942 | 0.91081 | 0.89124 | 0.88988 | 0.89445 | 0.92029 | 0.96923 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.7 | 71.5 | 72.5 | 65.1 | 92.5 | 23.4 | 0 | 0 | 95.8 | 34.3 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1264.6 | 4692.2 | 28787.4 | 3273.9 | 161.7 | 187.7 | 3623.3 | 7635.3 | 309.1 | -985.4 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 276.5 | 98.3 | 60.58 | 21.7 | 55.5 | 1.0779 | 1.0732 | 1.0742 | 1.0296 | 0 | 0 | 129 | 0 | 1907.8 | 1907.8 | 352.1 | 265.4 | 86.7 | 0.98111 | 0.98083 | 0.9353 | 0.92173 | 0.94256 | 0.9366 | 0.96961 | 0.95964 | 0.95553 | 0.95923 | 0.95755 | 0.96869 | 0.98316 | 6 | 4
p18otc352b_blhcoxll_s.sav | 8008.1 | 3920.3 | 1107.5 | 1896.8 | 2299 | 1905.9 | 1522.1 | 839.7 | 377.7 | 747.5 | 747.5 | 95.8 | 154.9 | 78 | 25.2 | 25.7 | 1874.6 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2095.3 | -548 | -581 | 572.1 | 1662.5 | -471 | 724.5 | 230.9 | 113.7 | -235 | 518.1 | 526.3 | -55.6 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 137.7 | 1380.8 | 3264.1 | 45.9 | 21.2 | 19.7 | 7.4 | 10 | 10 | 0 | 0.97143 | 0.98545 | 0.98138 | 0.8662 | 0.95359 | 0.87767 | 0.90293 | 0.94292 | 0.92695 | 0.93485 | 0.89702 | 0.90194 | 0.92511 | 0.97187 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 58.6 | 71.4 | 72.5 | 65.4 | 91.5 | 23.4 | 0 | 0 | 95.7 | 34.3 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1264 | 4692.8 | 28787.4 | 3273.9 | 161.7 | 187.7 | 3623.3 | 7635.3 | 308.8 | -985.2 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 277.3 | 100.4 | 60.438 | 21.7 | 57.5 | 1.0781 | 1.0735 | 1.0743 | 1.0297 | 0 | 0 | 129 | 0 | 1905.9 | 1905.9 | 352.1 | 265.4 | 86.7 | 0.98388 | 0.98436 | 0.9381 | 0.92463 | 0.94435 | 0.93859 | 0.97055 | 0.97664 | 1.0023 | 0.96693 | 0.96557 | 0.97376 | 0.98584 | 7 | 4
p18otc352b_mpsl.sav | 7550.5 | 3962.4 | 1107.5 | 1896.8 | 2300.2 | 1597.8 | 1522.1 | 898.5 | 363.1 | 764.3 | 764.3 | 96.8 | 156.2 | 78.5 | 25.3 | 25.8 | 1911.1 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2106.1 | -654 | 0 | 534 | 1645.7 | -483 | 728 | 234.6 | 77.5 | -199.1 | 482.3 | 506.5 | -28.2 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.7 | 1388.7 | 3264.1 | 45.6 | 20.1 | 21.2 | 8.6 | 10 | 10 | 0 | 0.9736 | 0.99256 | 0.98794 | 0.89611 | 0.98825 | 0.9042 | 0.93331 | 0.95631 | 0.93203 | 0.91425 | 0.91024 | 0.91581 | 0.93587 | 0.97724 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56 | 68.1 | 68.4 | 60.1 | 79.9 | 68.3 | 98.8 | 94.3 | 50.7 | 34 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1174.4 | 4782.1 | 28787.4 | 3273.9 | 222.7 | 126.7 | 3623.3 | 7635.3 | 301.8 | -978.2 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 270.8 | 92.3 | 55.68 | 21.7 | 49.8 | 1.0768 | 1.068 | 1.0681 | 1.0283 | 0 | 0 | 129 | 0 | 1597.8 | 1964.6 | 352.1 | 265.4 | 86.7 | 0.99097 | 0.99094 | 0.97049 | 0.95824 | 0.9729 | 0.97017 | 0.98433 | 0.98199 | 0.9802 | 0.98118 | 0.98042 | 0.98508 | 0.99129 | 8 | 5
p18otc352b_mpsl_s.sav | 7549.7 | 3962.2 | 1107.5 | 1896.8 | 2300.2 | 1596.6 | 1522.1 | 896.7 | 365.5 | 764.3 | 764.3 | 96.8 | 156.8 | 78.7 | 25.3 | 25.8 | 1911.8 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2106.3 | -652.9 | 0 | 535.1 | 1645 | -484 | 728.9 | 235.6 | 76.7 | -198.4 | 481.6 | 506 | -27.6 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.7 | 1388.7 | 3264.1 | 45.6 | 20.1 | 21.2 | 8.6 | 10 | 10 | 0 | 0.97508 | 0.99531 | 0.99143 | 0.89871 | 0.99125 | 0.90593 | 0.93529 | 0.95727 | 0.94833 | 0.95857 | 0.91754 | 0.92345 | 0.94083 | 0.97994 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 55.9 | 68.1 | 68.3 | 60.5 | 78.7 | 68.2 | 98.7 | 94.2 | 50.6 | 33.9 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1174.1 | 4782.4 | 28787.4 | 3273.9 | 222.4 | 127 | 3623.3 | 7635.3 | 301.6 | -977.8 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 271.5 | 94.1 | 55.532 | 21.7 | 51.7 | 1.077 | 1.0682 | 1.0682 | 1.0284 | 0 | 0 | 129 | 0 | 1596.6 | 1963 | 352.1 | 265.4 | 86.7 | 0.99372 | 0.99444 | 0.9733 | 0.96115 | 0.97476 | 0.97223 | 0.98532 | 0.99917 | 1.0277 | 0.98905 | 0.9886 | 0.99031 | 0.99403 | 9 | 5
p18otc352b_angr1.sav | 7639 | 3883.8 | 1107.5 | 1896.8 | 2299.8 | 1680.7 | 1522.1 | 960.9 | 325.8 | 758.9 | 758.9 | 100.3 | 174 | 86.7 | 25.8 | 26.4 | 1931 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2111.2 | -795.8 | -226.2 | 419.6 | 1615 | -539 | 797.2 | 306.3 | 56.8 | -178.6 | 461.8 | 483 | -12.1 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.4 | 1393.2 | 3264.1 | 47.6 | 21.7 | 19.3 | 8.3 | 10 | 10 | 0 | 0.96749 | 0.97144 | 0.96767 | 0.91715 | 1.0241 | 0.93315 | 0.96629 | 0.97454 | 0.92978 | 0.91182 | 0.92554 | 0.93183 | 0.94964 | 0.98514 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 112.9 | 61.7 | 51.7 | 63.7 | 64.7 | 90.4 | 87.9 | 43.2 | 33.5 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1187.7 | 4768.8 | 28787.4 | 3273.9 | 203.8 | 145.6 | 3623.3 | 7635.3 | 297 | -973.4 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 247.8 | 78 | 49.084 | 21.7 | 36 | 1.0768 | 1.0684 | 1.0688 | 1.0284 | 0 | 0 | 129 | 0 | 1680.7 | 2018.5 | 352.1 | 265.4 | 86.7 | 0.96989 | 0.97061 | 0.99328 | 0.99297 | 1.004 | 1.0044 | 1.0031 | 0.97962 | 0.97759 | 0.99767 | 0.99757 | 0.99958 | 0.9993 | 10 | 6
p18otc352b_angr2.sav | 7638.4 | 3886.4 | 1107.5 | 1896.8 | 2299.8 | 1679.8 | 1522.1 | 955.9 | 331.3 | 760.7 | 760.7 | 99.8 | 172.2 | 85.7 | 25.7 | 26.3 | 1931.2 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2111.4 | -792.3 | -223.5 | 423.2 | 1614.4 | -540 | 798.6 | 307.7 | 56.7 | -178.6 | 461.7 | 482.7 | -12.1 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 124.9 | 1393.7 | 3264.1 | 47.2 | 21.4 | 19.7 | 8.3 | 10 | 10 | 0 | 0.96998 | 0.98016 | 0.97585 | 0.92137 | 1.029 | 0.93448 | 0.9678 | 0.975 | 0.93599 | 0.91854 | 0.92734 | 0.93372 | 0.95073 | 0.98585 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 87.2 | 0 | 62.2 | 52.3 | 64.4 | 64.6 | 90.3 | 87.8 | 43.2 | 33.5 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1183.8 | 4772.7 | 28787.4 | 3273.9 | 203.7 | 145.7 | 3623.3 | 7635.3 | 297.1 | -973.5 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 251.6 | 79.7 | 49.383 | 21.7 | 37.7 | 1.0767 | 1.0683 | 1.0688 | 1.0284 | 0 | 0 | 129 | 0 | 1679.8 | 2017.3 | 352.1 | 265.4 | 86.7 | 0.97859 | 0.97882 | 0.99784 | 0.99775 | 1.0055 | 1.006 | 1.0036 | 0.98617 | 0.9848 | 0.99961 | 0.99959 | 1.0007 | 1 | 11 | 7
p18otc352b_angr12.sav | 7701.2 | 3863.5 | 1107.5 | 1896.8 | 2299.4 | 1760.7 | 1522.1 | 1051.8 | 179.8 | 699.6 | 699.6 | 114.7 | 230.8 | 114.1 | 28.3 | 28.9 | 1916 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2105 | -894.7 | -296.9 | 323.4 | 1632.8 | -513.6 | 765.9 | 273.7 | 65.7 | -187 | 470.1 | 493.7 | -17.7 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21.3 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 172.3 | 1347.2 | 3264.1 | 57.6 | 34.2 | 8 | 9.4 | 10 | 10 | 0 | 0.88808 | 0.79719 | 0.7888 | 0.85719 | 0.95384 | 0.92551 | 0.9576 | 0.97371 | 0.78811 | 0.75632 | 0.88729 | 0.89173 | 0.92711 | 0.96912 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 46.4 | 31.8 | 60.8 | 66.4 | 93.8 | 90 | 45.4 | 33.6 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1196.2 | 4760.3 | 28787.4 | 3273.9 | 208.8 | 140.6 | 3623.3 | 7635.3 | 296.4 | -972.8 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 149 | 30.8 | 34.85 | 21.7 | -11.1 | 1.0749 | 1.066 | 1.0671 | 1.0273 | 0 | 0 | 129 | 0 | 1760.7 | 2110.1 | 352.1 | 265.4 | 86.7 | 0.79592 | 0.7912 | 0.92834 | 0.92487 | 0.99582 | 0.99542 | 1.0022 | 0.83036 | 0.81088 | 0.95644 | 0.95464 | 0.97586 | 0.98305 | 12 | 8
p18otc352b_grgr.sav | 7665.5 | 3875.9 | 1107.5 | 1896.8 | 2300 | 1716.2 | 1522.1 | 998.4 | 263 | 685 | 685 | 154.4 | 220.9 | 108.3 | 33.7 | 34.4 | 1921.7 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2105.5 | -836.4 | -255.2 | 380.1 | 1623.6 | -528.6 | 784.8 | 293.4 | 62.9 | -184.4 | 467.5 | 488.7 | -16.2 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 22.1 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 144.8 | 1374.1 | 3264.1 | 63.5 | 52.5 | 5.7 | 12.1 | 10 | 10 | 0 | 0.90896 | 0.92152 | 0.91507 | 0.91857 | 1.0257 | 0.9496 | 0.98496 | 0.98475 | 0.89476 | 0.87379 | 0.92492 | 0.93119 | 0.95179 | 0.9849 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 29.3 | 35.7 | 53.3 | 39.3 | 50 | 65.4 | 91.8 | 88.8 | 44.1 | 33.6 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1191.5 | 4765.3 | 28787.4 | 3273.9 | 205.6 | 143.8 | 3623.3 | 7635.3 | 295.7 | -972.1 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 206.9 | 56 | 41.29 | 21.7 | 14.4 | 1.0762 | 1.0673 | 1.0681 | 1.0286 | 0 | 0 | 129 | 0 | 1716.2 | 2058.9 | 352.1 | 265.4 | 86.7 | 0.92005 | 0.91785 | 0.99481 | 0.99458 | 1.0217 | 1.0239 | 1.0136 | 0.94273 | 0.93682 | 0.997 | 0.99689 | 1.0018 | 0.99906 | 13 | 9
p18otc352b_anpf.sav | 7779.6 | 3905.5 | 1107.5 | 1896.8 | 2298.8 | 1857.6 | 1522.1 | 1163.8 | 96.4 | 770.3 | 770.3 | 90.3 | 137.1 | 69 | 24.3 | 24.8 | 1886.1 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2099.8 | -946.7 | -329.2 | 275.8 | 1651.7 | -498.8 | 762.2 | 269.7 | 103.2 | -224.6 | 507.8 | 516.2 | -47.9 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 20.7 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.2 | 1413.1 | 3264.1 | 40.6 | 13.1 | 28.9 | 10.1 | 10 | 10 | 0 | 0.99237 | 1.0373 | 1.0295 | 1.1248 | 1.0239 | 1.09 | 1.1428 | 1.0496 | 0.95114 | 0.93491 | 0.91077 | 0.91636 | 0.93877 | 0.9879 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.5 | 37.2 | 0 | 69.2 | 99.8 | 67.8 | 96.5 | 91.4 | 46.8 | 33.9 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1212.3 | 4744.2 | 28787.4 | 3273.9 | 214.5 | 134.9 | 3623.3 | 7635.3 | 300.1 | -976.5 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | -13.3 | 109.7 | 72.218 | 21.7 | 66.5 | 1.077 | 1.0674 | 1.0674 | 1.0283 | 0 | 0 | 129 | 0 | 1857.6 | 2216.1 | 352.1 | 265.4 | 86.7 | 1.0356 | 1.0327 | 1.2182 | 0.99281 | 1.1728 | 1.188 | 1.0804 | 1.0021 | 1.0023 | 0.98175 | 0.98101 | 0.98814 | 1.0021 | 14 | 10
p18otc352b_antbdy.sav | 7647.3 | 3887.2 | 1107.5 | 1896.8 | 2299.8 | 1691 | 1522.1 | 967.3 | 322.7 | 774.7 | 774.7 | 96.2 | 154 | 77.1 | 25.2 | 25.7 | 1927.6 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2111.2 | -802.6 | -230.6 | 413.8 | 1613 | -534.5 | 797.7 | 306.7 | 61.2 | -183.1 | 466.3 | 484.5 | -15.7 | 288 | 580 | 465.6 | 285 | 191.5 | 78 | 207 | 21 | 151 | 39 | 59 | 2531.1 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 117.6 | 1400.9 | 3264.1 | 44.4 | 18.4 | 23.1 | 8.7 | 10 | 10 | 0 | 0.98025 | 1.0076 | 1.0025 | 0.93303 | 1.0426 | 0.91061 | 0.94061 | 0.92559 | 0.9505 | 0.93422 | 0.92123 | 0.92732 | 0.94251 | 0.97758 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 50.7 | 61.7 | 56.7 | 56.7 | 70.2 | 64.8 | 90.8 | 88.1 | 43.4 | 33.6 | 560 | 560 | 300 | 250 | 1670 | 22788.6 | 1183.6 | 4772.9 | 28787.4 | 3273.9 | 204.1 | 145.3 | 3623.3 | 7635.3 | 304 | -980.5 | 6962.9 | 900 | 3027.4 | 663.9 | 805.7 | 490 | 234.6 | 88.1 | 45.247 | 21.7 | 45.9 | 1.0773 | 1.0688 | 1.0689 | 1.0286 | 0 | 0 | 129 | 0 | 1691 | 2029.9 | 352.1 | 265.4 | 86.7 | 1.006 | 1.0056 | 1.0105 | 1.0109 | 0.97979 | 0.97776 | 0.95271 | 1.0015 | 1.0016 | 0.99303 | 0.99274 | 0.99207 | 0.99163 | 15 | 11
p18otc352b_brbo_brkp.sav | 7757.4 | 3679.9 | 1107.5 | 1896.8 | 2393.7 | 1667.6 | 1534 | 944.7 | 369.9 | 787.7 | 787.7 | 100.1 | 162 | 82.1 | 25.6 | 26.2 | 1971.5 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2124.8 | -1210.4 | -541.8 | -27.9 | 794.1 | -243.4 | 918.4 | 236.8 | 17.8 | -140 | 423.1 | 425.8 | 18.2 | 288 | 585.5 | 467.4 | 287.7 | 193.4 | 78 | 209.7 | 18.7 | 151 | 39 | 59 | 2531.1 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 141.7 | 1381.8 | 3269.1 | 46.5 | 20.3 | 21.5 | 9.1 | 10 | 10 | 0 | 0.96069 | 0.97197 | 0.96731 | 0.84741 | 0.93179 | 0.86067 | 0.88338 | 0.93013 | 0.90063 | 0.88018 | 0.8851 | 0.88943 | 0.91704 | 0.96749 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57.9 | 70.6 | 73 | 64.7 | 93.6 | 69.7 | 101.6 | 96.8 | 52.3 | 38 | 0 | 560 | 300 | 250 | 1110 | 22788.6 | 1235.3 | 4911.4 | 28977.2 | 3283.2 | 204.7 | -408.8 | 3079 | 7635.3 | 322.7 | -987.1 | 6974.8 | 909 | 3057.2 | 670.5 | 805.8 | 490 | 272.6 | 97.3 | 61.829 | 21.7 | 54.4 | 1.0706 | 1.061 | 1.0613 | 1.0228 | 0 | 0 | 129 | 0 | 1667.6 | 2041 | 352.1 | 265.4 | 86.7 | 0.97042 | 0.97025 | 0.91775 | 0.90349 | 0.92606 | 0.91826 | 0.95739 | 0.94891 | 0.94367 | 0.95408 | 0.95218 | 0.96527 | 0.9814 | 16 | 12
p18otc352b_brbo_brkp_s.sav | 7749.9 | 3679.7 | 1107.5 | 1896.8 | 2393 | 1659.1 | 1534 | 934.3 | 383.5 | 788.1 | 788.1 | 99.9 | 163.6 | 82.7 | 25.6 | 26.2 | 1974.3 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2125.5 | -1201.2 | -535.3 | -19.2 | 792.9 | -247.2 | 918.6 | 239.3 | 14.9 | -137.1 | 420.2 | 423.9 | 20.5 | 288 | 585.5 | 467.4 | 287.7 | 193.4 | 78 | 209.7 | 18.7 | 151 | 39 | 59 | 2531.1 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.4 | 42.4 | 38.4 | 6.1 | 276.7 | 1745.2 | 141.3 | 1382 | 3268.9 | 46.6 | 20.4 | 21.3 | 9 | 10 | 10 | 0 | 0.96561 | 0.98137 | 0.97705 | 0.88195 | 0.97185 | 0.88188 | 0.90777 | 0.94088 | 0.92349 | 0.93101 | 0.89704 | 0.90196 | 0.92577 | 0.97306 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 58.1 | 70.8 | 73.2 | 64.6 | 91.5 | 69.5 | 101.2 | 96.6 | 52 | 37.9 | 0 | 560 | 300 | 250 | 1110 | 22788.6 | 1232.3 | 4913 | 28975.7 | 3283.2 | 203.7 | -407.8 | 3079 | 7635.3 | 321.6 | -986 | 6974.8 | 909 | 3056.7 | 670.5 | 805.8 | 490 | 283.8 | 99.7 | 60.957 | 21.7 | 56.8 | 1.0718 | 1.0622 | 1.0623 | 1.0237 | 0 | 0 | 129 | 0 | 1659.1 | 2031.5 | 352.1 | 265.4 | 86.7 | 0.9798 | 0.98002 | 0.95515 | 0.94234 | 0.94888 | 0.94362 | 0.96845 | 0.973 | 0.99817 | 0.96695 | 0.96559 | 0.97445 | 0.98705 | 17 | 12
p18otc352b_brgo_brkp.sav | 7749.4 | 3665.9 | 1107.5 | 1896.8 | 2398.5 | 1651.5 | 1534.9 | 926.8 | 376.5 | 786.7 | 786.7 | 101.6 | 163.4 | 83.5 | 25.8 | 26.4 | 1974.1 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2125.6 | -1217.2 | -547.8 | -22.7 | 782.3 | -233.7 | 924.1 | 234.1 | 14.8 | -137 | 420.1 | 424.1 | 20.5 | 288 | 586 | 467.4 | 288 | 193.5 | 78 | 210 | 18.4 | 151 | 39 | 59 | 2531.1 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 156.1 | 1367.4 | 3269.1 | 47.1 | 21.3 | 20.6 | 9 | 10 | 10 | 0 | 0.95136 | 0.95521 | 0.94908 | 0.81392 | 0.89282 | 0.83246 | 0.85077 | 0.91418 | 0.85396 | 0.82918 | 0.83871 | 0.84064 | 0.8822 | 0.94959 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.9 | 74.1 | 75.6 | 74.4 | 119.3 | 69.7 | 101.6 | 97 | 52.5 | 38.1 | 0 | 560 | 300 | 250 | 1110 | 22788.6 | 1236.6 | 4917.6 | 28984.7 | 3283.2 | 215.5 | -418.9 | 3079.8 | 7635.3 | 331.1 | -994.8 | 6975.5 | 909 | 3058.6 | 670.7 | 805.8 | 490 | 270.3 | 106.1 | 65.743 | 21.7 | 62.1 | 1.069 | 1.0595 | 1.0603 | 1.0216 | 0 | 0 | 129 | 0 | 1651.5 | 2024.5 | 352.1 | 265.4 | 86.7 | 0.95368 | 0.95196 | 0.88148 | 0.86571 | 0.89571 | 0.88437 | 0.94097 | 0.89974 | 0.88899 | 0.90407 | 0.89995 | 0.92859 | 0.96324 | 18 | 13
p18otc352b_brgo_brkp_s.sav | 7742.2 | 3667.8 | 1107.5 | 1896.8 | 2398.4 | 1642.6 | 1534.9 | 915.7 | 391.2 | 787.1 | 787.1 | 101.3 | 165.2 | 84.1 | 25.8 | 26.4 | 1977.1 | 330 | 330 | 807.1 | 815 | 2282.1 | 141 | 2120.7 | 2126.4 | -1206.8 | -540.4 | -12.7 | 781.6 | -238.2 | 925.4 | 237.2 | 11.9 | -134.1 | 417.2 | 422.2 | 22.8 | 288 | 586 | 467.4 | 288 | 193.5 | 78 | 210 | 18.4 | 151 | 39 | 59 | 2531.1 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 155.4 | 1368.1 | 3269.1 | 47.2 | 21.3 | 20.5 | 9 | 10 | 10 | 0 | 0.95649 | 0.96487 | 0.95917 | 0.84844 | 0.93298 | 0.85399 | 0.87568 | 0.92529 | 0.87744 | 0.87964 | 0.85136 | 0.85397 | 0.89146 | 0.9557 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 61 | 74.2 | 75.7 | 74 | 117.4 | 69.5 | 101.2 | 96.7 | 52.2 | 38 | 0 | 560 | 300 | 250 | 1110 | 22788.6 | 1233.5 | 4920 | 28984 | 3283.2 | 214.2 | -417.6 | 3079.8 | 7635.3 | 329.7 | -993.4 | 6975.5 | 909 | 3058.3 | 670.7 | 805.8 | 490 | 282 | 109.2 | 64.772 | 21.7 | 65.3 | 1.0703 | 1.0609 | 1.0614 | 1.0226 | 0 | 0 | 129 | 0 | 1642.6 | 2014.6 | 352.1 | 265.4 | 86.7 | 0.96333 | 0.96208 | 0.91886 | 0.90465 | 0.91887 | 0.91026 | 0.9524 | 0.92448 | 0.94309 | 0.91771 | 0.91422 | 0.93834 | 0.96944 | 19 | 13
p18otc355b.sav | 7658.5 | 3898.7 | 1107.5 | 1896.8 | 2299.9 | 1693.3 | 1572.1 | 925.6 | 354.9 | 771.8 | 771.8 | 96.4 | 155.8 | 77.9 | 25.2 | 25.8 | 1924.7 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2110.6 | -804 | -231.1 | 413.6 | 1603.8 | -561.1 | 792.2 | 301.2 | 64.4 | -186.2 | 469.4 | 487.7 | -18.2 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 124.4 | 1394.6 | 3264.6 | 52.2 | 19.6 | 22.8 | 9 | 10 | 10 | 0 | 0.97793 | 1.003 | 0.99819 | 0.91963 | 1.0356 | 0.92528 | 0.95733 | 0.96929 | 0.9503 | 0.934 | 0.92824 | 0.93466 | 0.95033 | 0.98582 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 54.1 | 65.9 | 66 | 56 | 69.4 | 64.9 | 90.9 | 88.1 | 43.5 | 33.7 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1190.7 | 4826.7 | 28848.3 | 3273.9 | 204 | 146.3 | 3624.2 | 7635.3 | 299 | -1023.6 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 268.3 | 86.6 | 52.689 | 22.9 | 44.5 | 1.0762 | 1.0678 | 1.0684 | 1.0277 | 0 | 0 | 129 | 0 | 1693.3 | 2032.6 | 354.9 | 268.3 | 86.6 | 1.003 | 0.99819 | 0.91963 | 1.0356 | 0.92528 | 0.95733 | 0.96929 | 0.9503 | 0.934 | 0.92824 | 0.93466 | 0.95033 | 0.98582 | 0 | 0
p18otc355b_amps.sav | 7821.9 | 3966.9 | 1107.5 | 1896.8 | 2298.7 | 1896.6 | 1572.1 | 1161.3 | 108.3 | 769.1 | 769.1 | 89.6 | 136.1 | 68.4 | 24.2 | 24.7 | 1881.2 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2098.7 | -931.9 | -314 | 293.8 | 1634.1 | -529.8 | 768.7 | 276.6 | 108.5 | -229.9 | 513.1 | 516.8 | -52 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -28.1 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104 | 1427.8 | 3264.6 | 47.6 | 13.2 | 29.8 | 10.7 | 10 | 10 | 0 | 0.99354 | 1.0407 | 1.0328 | 0.91963 | 1.0356 | 0.92528 | 0.95733 | 1.0131 | 0.95534 | 0.93945 | 0.91145 | 0.91707 | 0.93775 | 0.98454 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 30.2 | 36.8 | 0 | 68.2 | 96.6 | 68.1 | 96.8 | 91.4 | 46.7 | 34 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1225.3 | 4792.2 | 28848.3 | 3273.9 | 212.8 | 137.5 | 3624.2 | 7581.2 | 299.5 | -969.9 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 0 | 108.3 | 70.132 | 22.9 | 65.3 | 1.0759 | 1.0664 | 1.0667 | 1.0274 | 0 | 0 | 129 | 0 | 1896.6 | 2256 | 354.9 | 268.3 | 86.6 | 1.0376 | 1.0346 | 1 | 1 | 1 | 1 | 1.0452 | 1.0053 | 1.0058 | 0.98191 | 0.98118 | 0.98676 | 0.9987 | 1 | 1
p18otc355b_amps_s.sav | 7820.8 | 3967 | 1107.5 | 1896.8 | 2298.7 | 1895.4 | 1572.1 | 1159.6 | 110.4 | 769.1 | 769.1 | 89.5 | 136.6 | 68.5 | 24.2 | 24.7 | 1881.7 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2098.9 | -930.5 | -313 | 295.1 | 1633.7 | -530.3 | 769.1 | 277 | 108 | -229.4 | 512.6 | 516.5 | -51.6 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -28.1 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.1 | 1427.7 | 3264.6 | 47.6 | 13.3 | 29.8 | 10.6 | 10 | 10 | 0 | 0.99483 | 1.0431 | 1.0359 | 0.91963 | 1.0356 | 0.92528 | 0.95733 | 1.0134 | 0.97127 | 0.98394 | 0.91842 | 0.92438 | 0.94242 | 0.98705 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 30.3 | 36.9 | 0 | 68.5 | 95.9 | 68 | 96.8 | 91.4 | 46.7 | 34 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1225 | 4792.5 | 28848.3 | 3273.9 | 212.7 | 137.6 | 3624.2 | 7581.2 | 299.3 | -969.7 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 0 | 110.4 | 70.03 | 22.9 | 67.4 | 1.0761 | 1.0666 | 1.0668 | 1.0275 | 0 | 0 | 129 | 0 | 1895.4 | 2254.6 | 354.9 | 268.3 | 86.6 | 1.04 | 1.0377 | 1 | 1 | 1 | 1 | 1.0455 | 1.0221 | 1.0535 | 0.98942 | 0.989 | 0.99168 | 1.0012 | 2 | 1
p18otc355b_dsbg.sav | 7711 | 3911.2 | 1107.5 | 1896.8 | 2299.4 | 1758.9 | 1572.1 | 1002.8 | 277.9 | 774.9 | 774.9 | 93.8 | 143 | 70.4 | 24.8 | 25.3 | 1907.2 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2106 | -855.4 | -265.8 | 364.3 | 1620.1 | -548.8 | 780 | 288.4 | 82.5 | -204.1 | 487.3 | 501 | -32.2 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.8 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 106.1 | 1412.8 | 3264.6 | 50.4 | 17.3 | 25.3 | 9.6 | 10 | 10 | 0 | 0.98052 | 1.0075 | 1.0042 | 0.90585 | 0.9995 | 0.91082 | 0.94086 | 0.96217 | 0.99302 | 0.98001 | 0.96018 | 0.96809 | 0.97809 | 0.98944 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 48.1 | 58.6 | 69.3 | 17.2 | 44.9 | 66 | 93 | 89.4 | 44.7 | 33.8 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1201.8 | 4815.6 | 28848.3 | 3273.9 | 207.5 | 142.8 | 3624.2 | 7635.3 | 303.8 | -1028.3 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 277.9 | 0 | 55.97 | 22.9 | -41.6 | 1.0756 | 1.0669 | 1.0676 | 1.0273 | 0 | 0 | 129 | 0 | 1758.9 | 2105.4 | 354.9 | 268.3 | 86.6 | 1.0045 | 1.006 | 0.98502 | 0.96513 | 0.98437 | 0.9828 | 0.99265 | 1.045 | 1.0493 | 1.0344 | 1.0358 | 1.0292 | 1.0037 | 3 | 2
p18otc355b_bloxhcb.sav | 7759.6 | 3911.4 | 1107.5 | 1896.8 | 2299.8 | 1561.7 | 1572.1 | 888.3 | 364.8 | 761.3 | 761.3 | 96 | 155.1 | 77.8 | 25.2 | 25.7 | 1902.4 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2103.8 | -702.4 | -395.4 | 471.7 | 1625.4 | -529.5 | 756.9 | 264.5 | 86.6 | -208.1 | 491.3 | 506.1 | -35.2 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.7 | 1389.3 | 3264.6 | 52.7 | 20.3 | 21.7 | 9 | 10 | 10 | 0 | 0.97443 | 0.99537 | 0.99058 | 0.89689 | 0.98914 | 0.90517 | 0.93441 | 0.95825 | 0.93616 | 0.91872 | 0.91441 | 0.92018 | 0.93942 | 0.97981 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56 | 68.2 | 68.9 | 59.5 | 78.2 | 67.3 | 119.3 | 0 | 68.3 | 34 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1235.8 | 4781.7 | 28848.3 | 3273.9 | 183.6 | 166.7 | 3624.2 | 7635.3 | 302.8 | -1027.4 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 273.2 | 91.6 | 56.059 | 22.9 | 49.2 | 1.0756 | 1.0667 | 1.0666 | 1.0273 | 0 | 0 | 129 | 0 | 1561.7 | 1996.5 | 354.9 | 268.3 | 86.6 | 0.99236 | 0.99238 | 0.97527 | 0.95513 | 0.97827 | 0.97606 | 0.98861 | 0.98512 | 0.98364 | 0.9851 | 0.98451 | 0.98852 | 0.9939 | 4 | 3
p18otc355b_bloxhcb_s.sav | 7758.3 | 3911.6 | 1107.5 | 1896.8 | 2299.8 | 1560.3 | 1572.1 | 886.3 | 367.3 | 761.2 | 761.2 | 95.9 | 155.7 | 78 | 25.1 | 25.7 | 1903 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2104 | -700.8 | -394.1 | 473.3 | 1625 | -530.1 | 757.4 | 265.1 | 86 | -207.6 | 490.8 | 505.7 | -34.8 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.7 | 1389.3 | 3264.6 | 52.7 | 20.3 | 21.7 | 9 | 10 | 10 | 0 | 0.97584 | 0.99799 | 0.99393 | 0.89926 | 0.99188 | 0.90669 | 0.93616 | 0.95911 | 0.9522 | 0.96285 | 0.92153 | 0.92764 | 0.94426 | 0.98244 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56 | 68.2 | 68.9 | 60 | 77.1 | 67.3 | 119.3 | 0 | 68.2 | 34 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1235.3 | 4782.2 | 28848.3 | 3273.9 | 183.5 | 166.8 | 3624.2 | 7635.3 | 302.6 | -1027.2 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 274 | 93.3 | 55.939 | 22.9 | 51 | 1.0759 | 1.0669 | 1.0667 | 1.0274 | 0 | 0 | 129 | 0 | 1560.3 | 1994.8 | 354.9 | 268.3 | 86.6 | 0.99498 | 0.99573 | 0.97785 | 0.95777 | 0.97991 | 0.97789 | 0.9895 | 1.002 | 1.0309 | 0.99277 | 0.99249 | 0.99361 | 0.99657 | 5 | 3
p18otc355b_blhcoxll.sav | 8043.5 | 3931.4 | 1107.5 | 1896.8 | 2298.9 | 1938.5 | 1572.1 | 829.4 | 377 | 744.3 | 744.3 | 95.1 | 153.3 | 77.2 | 25 | 25.6 | 1864.7 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2092.8 | -573.1 | -603.2 | 548 | 1655.4 | -487.2 | 712.1 | 218.1 | 124 | -245.1 | 528.3 | 533.5 | -63.3 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.9 | 1380.1 | 3264.6 | 53.1 | 21.5 | 20.2 | 7.8 | 10 | 10 | 0 | 0.96991 | 0.98345 | 0.97845 | 0.85759 | 0.9436 | 0.86979 | 0.89388 | 0.93865 | 0.91093 | 0.89138 | 0.88943 | 0.89397 | 0.9198 | 0.96877 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.1 | 72 | 73.5 | 65.3 | 92.7 | 23.5 | 0 | 0 | 97 | 34.4 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1278.2 | 4739.4 | 28848.3 | 3273.9 | 161.5 | 188.8 | 3624.2 | 7635.3 | 310.7 | -1035.2 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 278.4 | 98.5 | 61.736 | 22.9 | 55.6 | 1.0769 | 1.0723 | 1.0736 | 1.0288 | 0 | 0 | 129 | 0 | 1938.5 | 1938.5 | 354.9 | 268.3 | 86.6 | 0.98048 | 0.98022 | 0.93254 | 0.91115 | 0.94003 | 0.93372 | 0.96839 | 0.95857 | 0.95437 | 0.95819 | 0.95647 | 0.96787 | 0.98271 | 6 | 4
p18otc355b_blhcoxll_s.sav | 8042 | 3931.7 | 1107.5 | 1896.8 | 2298.9 | 1936.7 | 1572.1 | 827.3 | 379.8 | 744.2 | 744.2 | 95 | 153.9 | 77.4 | 25 | 25.6 | 1865.4 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2092.9 | -571.3 | -601.6 | 549.8 | 1654.9 | -487.9 | 712.7 | 218.8 | 123.3 | -244.4 | 527.6 | 533.1 | -62.8 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.9 | 1380.1 | 3264.6 | 53.1 | 21.5 | 20.2 | 7.8 | 10 | 10 | 0 | 0.97141 | 0.98623 | 0.98197 | 0.86019 | 0.94662 | 0.87147 | 0.89581 | 0.93957 | 0.92709 | 0.93501 | 0.89658 | 0.90148 | 0.92463 | 0.97141 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 59 | 71.9 | 73.5 | 65.6 | 91.6 | 23.5 | 0 | 0 | 97 | 34.4 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1277.6 | 4740 | 28848.3 | 3273.9 | 161.4 | 188.9 | 3624.2 | 7635.3 | 310.4 | -1034.9 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 279.3 | 100.5 | 61.591 | 22.9 | 57.7 | 1.0771 | 1.0725 | 1.0737 | 1.0289 | 0 | 0 | 129 | 0 | 1936.7 | 1936.7 | 354.9 | 268.3 | 86.6 | 0.98325 | 0.98375 | 0.93537 | 0.91407 | 0.94185 | 0.93574 | 0.96934 | 0.97558 | 1.0011 | 0.96589 | 0.9645 | 0.97296 | 0.98538 | 7 | 4
p18otc355b_mpsl.sav | 7575.9 | 3981 | 1107.5 | 1896.8 | 2300.2 | 1620.4 | 1572.1 | 884.1 | 366.3 | 760.5 | 760.5 | 96.1 | 155.2 | 78 | 25.2 | 25.7 | 1901.1 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2103.5 | -669.8 | 0 | 519.1 | 1640.5 | -495.8 | 710.7 | 216.9 | 87.8 | -209.4 | 492.6 | 514.9 | -36.1 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.1 | 1387.8 | 3264.6 | 52.9 | 20.5 | 21.8 | 9 | 10 | 10 | 0 | 0.9734 | 0.99299 | 0.98818 | 0.88949 | 0.98058 | 0.89755 | 0.92571 | 0.95273 | 0.93151 | 0.91368 | 0.9092 | 0.91472 | 0.93494 | 0.97655 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 56.4 | 68.7 | 69.6 | 60.4 | 80.4 | 69.1 | 100.7 | 95.5 | 52 | 34.1 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1185 | 4832.4 | 28848.3 | 3273.9 | 225.3 | 125 | 3624.2 | 7635.3 | 303.4 | -1027.9 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 273.6 | 92.7 | 56.973 | 22.9 | 50.2 | 1.0757 | 1.0669 | 1.0673 | 1.0273 | 0 | 0 | 129 | 0 | 1620.4 | 1993.3 | 354.9 | 268.3 | 86.6 | 0.98999 | 0.98997 | 0.96723 | 0.94686 | 0.97003 | 0.96697 | 0.98291 | 0.98023 | 0.97824 | 0.97949 | 0.97867 | 0.98381 | 0.9906 | 8 | 5
p18otc355b_mpsl_s.sav | 7575.1 | 3980.8 | 1107.5 | 1896.8 | 2300.2 | 1619.2 | 1572.1 | 882.2 | 368.8 | 760.5 | 760.5 | 96 | 155.9 | 78.2 | 25.2 | 25.7 | 1901.9 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2103.7 | -668.8 | 0 | 520.2 | 1639.8 | -496.8 | 711.7 | 217.9 | 87.1 | -208.7 | 491.9 | 514.4 | -35.5 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.1 | 1387.9 | 3264.6 | 52.8 | 20.5 | 21.8 | 9 | 10 | 10 | 0 | 0.97492 | 0.99582 | 0.99176 | 0.89215 | 0.98366 | 0.89929 | 0.9277 | 0.95369 | 0.94791 | 0.9581 | 0.91652 | 0.92239 | 0.93991 | 0.97926 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56.4 | 68.6 | 69.5 | 60.8 | 79.2 | 69.1 | 100.5 | 95.5 | 51.9 | 34.1 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1184.6 | 4832.8 | 28848.3 | 3273.9 | 225 | 125.3 | 3624.2 | 7635.3 | 303.2 | -1027.7 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 274.4 | 94.5 | 56.824 | 22.9 | 52.1 | 1.076 | 1.0671 | 1.0674 | 1.0275 | 0 | 0 | 129 | 0 | 1619.2 | 1991.7 | 354.9 | 268.3 | 86.6 | 0.99281 | 0.99356 | 0.97012 | 0.94984 | 0.97191 | 0.96905 | 0.98391 | 0.99748 | 1.0258 | 0.98737 | 0.98687 | 0.98903 | 0.99335 | 9 | 5
p18otc355b_angr1.sav | 7670.6 | 3896.2 | 1107.5 | 1896.8 | 2299.7 | 1708.8 | 1572.1 | 949.7 | 328.3 | 756 | 756 | 99.6 | 173.1 | 86.2 | 25.7 | 26.3 | 1922.9 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2109.1 | -821.7 | -243.7 | 396.4 | 1606.8 | -556.8 | 786.6 | 295.4 | 65.3 | -187 | 470.2 | 489.3 | -18.7 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 126.2 | 1392.9 | 3264.6 | 54.7 | 22 | 20 | 8.7 | 10 | 10 | 0 | 0.96745 | 0.97176 | 0.96789 | 0.91294 | 1.0277 | 0.92899 | 0.96156 | 0.97231 | 0.93017 | 0.91223 | 0.92575 | 0.93206 | 0.94972 | 0.98501 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 113.6 | 62.6 | 51.7 | 63.4 | 65.2 | 91.5 | 88.5 | 43.9 | 33.7 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1198.8 | 4818.7 | 28848.3 | 3273.9 | 204.7 | 145.6 | 3624.2 | 7635.3 | 298.1 | -1022.6 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 250.5 | 77.7 | 50.01 | 22.9 | 35.8 | 1.0758 | 1.0673 | 1.0681 | 1.0275 | 0 | 0 | 129 | 0 | 1708.8 | 2050.2 | 354.9 | 268.3 | 86.6 | 0.96882 | 0.96964 | 0.99272 | 0.99238 | 1.004 | 1.0044 | 1.0031 | 0.97882 | 0.97669 | 0.99732 | 0.99722 | 0.99936 | 0.99918 | 10 | 6
p18otc355b_angr2.sav | 7670.1 | 3898.8 | 1107.5 | 1896.8 | 2299.8 | 1707.9 | 1572.1 | 944.7 | 333.8 | 757.8 | 757.8 | 99.1 | 171.4 | 85.3 | 25.6 | 26.2 | 1923.1 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2109.3 | -818.1 | -241 | 400 | 1606.2 | -557.9 | 787.9 | 296.8 | 65.3 | -187 | 470.2 | 489 | -18.7 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 125.7 | 1393.4 | 3264.6 | 54.4 | 21.6 | 20.4 | 8.8 | 10 | 10 | 0 | 0.96998 | 0.98063 | 0.97621 | 0.91723 | 1.0328 | 0.93032 | 0.96307 | 0.97277 | 0.93649 | 0.91908 | 0.9276 | 0.934 | 0.95085 | 0.98575 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 87.7 | 0 | 63.1 | 52.2 | 64 | 65.2 | 91.4 | 88.5 | 43.8 | 33.7 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1194.8 | 4822.6 | 28848.3 | 3273.9 | 204.5 | 145.8 | 3624.2 | 7635.3 | 298.2 | -1022.8 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 254.3 | 79.5 | 50.304 | 22.9 | 37.5 | 1.0757 | 1.0673 | 1.0681 | 1.0275 | 0 | 0 | 129 | 0 | 1707.9 | 2049 | 354.9 | 268.3 | 86.6 | 0.97767 | 0.97798 | 0.99739 | 0.99727 | 1.0054 | 1.006 | 1.0036 | 0.98547 | 0.98403 | 0.99931 | 0.99929 | 1.0005 | 0.99993 | 11 | 7
p18otc355b_angr12.sav | 7733.9 | 3874.2 | 1107.5 | 1896.8 | 2299.3 | 1790.3 | 1572.1 | 1042.6 | 178.2 | 696.8 | 696.8 | 114.2 | 229.1 | 113.4 | 28.2 | 28.9 | 1907.5 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2102.9 | -923.5 | -316.5 | 297.5 | 1625 | -530.6 | 754.1 | 261.6 | 74.5 | -195.7 | 478.8 | 500.3 | -24.4 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.5 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 174.9 | 1345.1 | 3264.6 | 64.3 | 34.5 | 8.2 | 9.5 | 10 | 10 | 0 | 0.88273 | 0.78718 | 0.77885 | 0.84787 | 0.95084 | 0.91961 | 0.95088 | 0.97075 | 0.77944 | 0.74663 | 0.88379 | 0.88806 | 0.92467 | 0.96751 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 47 | 31.7 | 62.3 | 67 | 95 | 90.7 | 46.2 | 33.8 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1208 | 4809.4 | 28848.3 | 3273.9 | 209.9 | 140.3 | 3624.2 | 7635.3 | 297.6 | -1022.2 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 149 | 29.2 | 35.624 | 22.9 | -12.8 | 1.0738 | 1.0649 | 1.0663 | 1.0263 | 0 | 0 | 129 | 0 | 1790.3 | 2143.4 | 354.9 | 268.3 | 86.6 | 0.7848 | 0.78026 | 0.92197 | 0.91814 | 0.99387 | 0.99326 | 1.0015 | 0.8202 | 0.79939 | 0.95211 | 0.95014 | 0.973 | 0.98143 | 12 | 8
p18otc355b_grgr.sav | 7698.1 | 3888 | 1107.5 | 1896.8 | 2299.9 | 1745.6 | 1572.1 | 988.9 | 263.4 | 682.7 | 682.7 | 153.5 | 219.2 | 107.6 | 33.6 | 34.3 | 1913.6 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2103.5 | -863.8 | -273.7 | 355.5 | 1615.6 | -546 | 773.7 | 281.9 | 71.5 | -192.9 | 476 | 495.1 | -22.8 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -26.7 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 145.9 | 1373.6 | 3264.6 | 70.2 | 53 | 4.8 | 12.1 | 10 | 10 | 0 | 0.90216 | 0.91484 | 0.90845 | 0.9101 | 1.0244 | 0.94354 | 0.97809 | 0.98167 | 0.8894 | 0.86795 | 0.9227 | 0.92886 | 0.9502 | 0.9838 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 29.7 | 36.2 | 54.2 | 39.3 | 50.3 | 66 | 93 | 89.4 | 44.8 | 33.7 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1203.1 | 4814.6 | 28848.3 | 3273.9 | 206.5 | 143.7 | 3624.2 | 7635.3 | 296.8 | -1021.4 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 208.3 | 55 | 42.286 | 22.9 | 13.4 | 1.0753 | 1.0664 | 1.0674 | 1.0277 | 0 | 0 | 129 | 0 | 1745.6 | 2092 | 354.9 | 268.3 | 86.6 | 0.91208 | 0.9101 | 0.98964 | 0.98916 | 1.0197 | 1.0217 | 1.0128 | 0.93592 | 0.92928 | 0.99403 | 0.99379 | 0.99986 | 0.99795 | 13 | 9
p18otc355b_anpf.sav | 7812.7 | 3918 | 1107.5 | 1896.8 | 2298.7 | 1887.8 | 1572.1 | 1154.9 | 96.8 | 767.4 | 767.4 | 89.5 | 136.1 | 68.4 | 24.2 | 24.7 | 1877.6 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2097.7 | -974 | -347.6 | 251.4 | 1643.7 | -516.3 | 751.2 | 258.3 | 112.1 | -233.4 | 516.6 | 522.6 | -54.7 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -28.1 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 105.4 | 1413.4 | 3264.6 | 47.7 | 13.4 | 29.6 | 10.6 | 10 | 10 | 0 | 0.99339 | 1.0404 | 1.0323 | 1.1248 | 1.0239 | 1.09 | 1.1428 | 1.0496 | 0.95332 | 0.93726 | 0.9116 | 0.91723 | 0.93931 | 0.98821 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.4 | 37.1 | 0 | 69.3 | 99.9 | 68.4 | 97.7 | 92.1 | 47.5 | 34.1 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1224.1 | 4793.4 | 28848.3 | 3273.9 | 215.6 | 134.7 | 3624.2 | 7635.3 | 301.1 | -1025.6 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | -13.3 | 110.1 | 73.367 | 22.9 | 66.9 | 1.076 | 1.0664 | 1.0667 | 1.0274 | 0 | 0 | 129 | 0 | 1887.8 | 2250.1 | 354.9 | 268.3 | 86.6 | 1.0372 | 1.0342 | 1.2231 | 0.9887 | 1.1781 | 1.1938 | 1.0829 | 1.0032 | 1.0035 | 0.98207 | 0.98135 | 0.9884 | 1.0024 | 14 | 10
p18otc355b_antbdy.sav | 7679.2 | 3899.6 | 1107.5 | 1896.8 | 2299.7 | 1719.5 | 1572.1 | 956.4 | 325 | 771.8 | 771.8 | 95.5 | 153.1 | 76.6 | 25 | 25.6 | 1919.4 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2109.1 | -828.8 | -248.3 | 390.2 | 1604.8 | -552.2 | 787 | 295.7 | 69.9 | -191.6 | 474.8 | 490.9 | -22.4 | 288 | 580 | 465.6 | 335 | 191.5 | 78 | 257 | -27.8 | 151 | 39 | 59 | 2531.6 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 118.1 | 1400.9 | 3264.6 | 51.5 | 18.7 | 23.7 | 9.2 | 10 | 10 | 0 | 0.98062 | 1.0093 | 1.0039 | 0.92977 | 1.0475 | 0.90575 | 0.93506 | 0.92146 | 0.95173 | 0.93554 | 0.92151 | 0.92761 | 0.9425 | 0.97724 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 50.9 | 62 | 57.4 | 56.7 | 69.9 | 65.4 | 91.8 | 88.7 | 44.1 | 33.8 | 560 | 560 | 250 | 300 | 1670 | 22788.6 | 1194.7 | 4822.8 | 28848.3 | 3273.9 | 205 | 145.3 | 3624.2 | 7635.3 | 305.5 | -1030.1 | 6914.8 | 900 | 3038.3 | 664.8 | 757.6 | 490 | 236.9 | 88 | 45.993 | 22.9 | 45.9 | 1.0763 | 1.0677 | 1.0682 | 1.0277 | 0 | 0 | 129 | 0 | 1719.5 | 2062 | 354.9 | 268.3 | 86.6 | 1.0063 | 1.0058 | 1.011 | 1.0115 | 0.97889 | 0.97674 | 0.95066 | 1.0015 | 1.0016 | 0.99275 | 0.99246 | 0.99176 | 0.9913 | 15 | 11
p18otc355b_brbo_brkp.sav | 7789 | 3692.8 | 1107.5 | 1896.8 | 2393.8 | 1695.6 | 1584.5 | 933 | 371.6 | 784.3 | 784.3 | 99.3 | 161 | 81.6 | 25.5 | 26.1 | 1962.2 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2122.4 | -1234.8 | -558.1 | -49.1 | 789.7 | -262.5 | 907.2 | 225.1 | 27.5 | -149.6 | 432.7 | 433.9 | 10.5 | 288 | 585.5 | 467.4 | 338.2 | 193.4 | 78 | 260.2 | -30.5 | 151 | 39 | 59 | 2531.6 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 142.5 | 1381.4 | 3269.6 | 53.7 | 20.6 | 22.2 | 9.6 | 10 | 10 | 0 | 0.96066 | 0.97303 | 0.9682 | 0.84246 | 0.92604 | 0.85544 | 0.87735 | 0.92734 | 0.90153 | 0.88116 | 0.88557 | 0.88992 | 0.91734 | 0.96761 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58.2 | 70.9 | 73.9 | 64.7 | 93.4 | 70.3 | 102.7 | 97.5 | 52.9 | 38.1 | 0 | 560 | 250 | 300 | 1110 | 22788.6 | 1247.5 | 4960.8 | 29038.7 | 3283.2 | 206.3 | -409.4 | 3079.9 | 7635.3 | 323.2 | -1035.7 | 6926.7 | 909 | 3068.2 | 671.4 | 757.7 | 490 | 274.3 | 97.3 | 62.824 | 22.9 | 54.4 | 1.0694 | 1.0597 | 1.0604 | 1.0216 | 0 | 0 | 129 | 0 | 1695.6 | 2072.2 | 354.9 | 268.3 | 86.6 | 0.97009 | 0.96996 | 0.91609 | 0.8942 | 0.92452 | 0.91646 | 0.95672 | 0.94868 | 0.94343 | 0.95403 | 0.95213 | 0.96529 | 0.98153 | 16 | 12
p18otc355b_brbo_brkp_s.sav | 7781 | 3692 | 1107.5 | 1896.8 | 2392.5 | 1686.9 | 1584.5 | 922.4 | 385.3 | 784.8 | 784.8 | 99.1 | 162.7 | 82.1 | 25.5 | 26.1 | 1965.1 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2123.1 | -1225.7 | -551.7 | -40.4 | 788.5 | -266.5 | 906.2 | 227.8 | 24.6 | -146.7 | 429.9 | 431.9 | 12.8 | 288 | 585.5 | 467.4 | 338.2 | 193.4 | 78 | 260.2 | -30.5 | 151 | 39 | 59 | 2531.6 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.4 | 42.4 | 38.4 | 6.1 | 276.7 | 1745.2 | 142 | 1381.7 | 3269.4 | 53.8 | 20.6 | 22 | 9.5 | 10 | 10 | 0 | 0.96565 | 0.98253 | 0.97804 | 0.87704 | 0.96616 | 0.87668 | 0.9018 | 0.93809 | 0.92454 | 0.93218 | 0.89759 | 0.90254 | 0.92613 | 0.97321 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 58.4 | 71.1 | 74 | 64.6 | 91.3 | 70.1 | 102.3 | 97.2 | 52.7 | 38.1 | 0 | 560 | 250 | 300 | 1110 | 22788.6 | 1244.3 | 4962.4 | 29037.1 | 3283.2 | 205.2 | -408.5 | 3079.8 | 7635.3 | 322 | -1034.5 | 6926.7 | 909 | 3067.7 | 671.3 | 757.7 | 490 | 285.6 | 99.7 | 61.934 | 22.9 | 56.9 | 1.0706 | 1.0611 | 1.0614 | 1.0226 | 0 | 0 | 129 | 0 | 1686.9 | 2062.6 | 354.9 | 268.3 | 86.6 | 0.97956 | 0.97981 | 0.95369 | 0.93294 | 0.94747 | 0.942 | 0.96781 | 0.97289 | 0.99805 | 0.96698 | 0.96564 | 0.97454 | 0.98721 | 17 | 12
p18otc355b_brgo_brkp.sav | 7782.7 | 3680.5 | 1107.5 | 1896.8 | 2399 | 1680 | 1585.4 | 915.7 | 377.6 | 783.4 | 783.4 | 100.8 | 162.4 | 83 | 25.7 | 26.3 | 1964.8 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2123.2 | -1241.8 | -564 | -44.1 | 777.6 | -252.1 | 914.6 | 222.4 | 24.6 | -146.7 | 429.8 | 432.1 | 12.7 | 288 | 586 | 467.4 | 338.5 | 193.5 | 78 | 260.5 | -30.8 | 151 | 39 | 59 | 2531.6 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 156.9 | 1367.1 | 3269.6 | 54.3 | 21.5 | 21.4 | 9.5 | 10 | 10 | 0 | 0.95123 | 0.95613 | 0.94984 | 0.80837 | 0.88635 | 0.82659 | 0.84395 | 0.91094 | 0.85467 | 0.82996 | 0.83865 | 0.84058 | 0.88191 | 0.94906 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 61.2 | 74.5 | 76.4 | 74.4 | 119 | 70.3 | 102.8 | 97.7 | 53.1 | 38.2 | 0 | 560 | 250 | 300 | 1110 | 22788.6 | 1249.3 | 4967.6 | 29047.3 | 3283.2 | 216.9 | -419.4 | 3080.7 | 7635.3 | 331.7 | -1043.5 | 6927.4 | 909 | 3069.8 | 671.6 | 757.7 | 490 | 271.5 | 106.1 | 66.781 | 22.9 | 62.1 | 1.0677 | 1.0583 | 1.0593 | 1.0204 | 0 | 0 | 129 | 0 | 1680 | 2056.4 | 354.9 | 268.3 | 86.6 | 0.95324 | 0.95156 | 0.87902 | 0.85587 | 0.89334 | 0.88157 | 0.9398 | 0.89937 | 0.88861 | 0.90348 | 0.89934 | 0.928 | 0.96271 | 18 | 13
p18otc355b_brgo_brkp_s.sav | 7773.7 | 3680.4 | 1107.5 | 1896.8 | 2397.7 | 1671 | 1585.4 | 904.5 | 392.5 | 783.8 | 783.8 | 100.5 | 164.2 | 83.6 | 25.7 | 26.2 | 1967.9 | 330 | 330 | 807.6 | 815 | 2282.6 | 141 | 2121.2 | 2124 | -1231.3 | -556.8 | -34.2 | 776.8 | -256.9 | 913.9 | 225.4 | 21.6 | -143.7 | 426.8 | 430.1 | 15.1 | 288 | 586 | 467.4 | 338.5 | 193.5 | 78 | 260.5 | -30.8 | 151 | 39 | 59 | 2531.6 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 156.2 | 1367.8 | 3269.6 | 54.5 | 21.5 | 21.2 | 9.4 | 10 | 10 | 0 | 0.95643 | 0.96589 | 0.96003 | 0.84305 | 0.92672 | 0.84832 | 0.86913 | 0.9222 | 0.87838 | 0.88069 | 0.85161 | 0.85422 | 0.89145 | 0.95541 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 61.2 | 74.6 | 76.5 | 74 | 117.1 | 70.1 | 102.3 | 97.4 | 52.8 | 38.2 | 0 | 560 | 250 | 300 | 1110 | 22788.6 | 1245.7 | 4969.3 | 29045.4 | 3283.2 | 215.5 | -418 | 3080.7 | 7635.3 | 330.2 | -1042 | 6927.4 | 909 | 3069.2 | 671.6 | 757.7 | 490 | 283.3 | 109.3 | 65.775 | 22.9 | 65.3 | 1.069 | 1.0596 | 1.0605 | 1.0214 | 0 | 0 | 129 | 0 | 1671 | 2046.3 | 354.9 | 268.3 | 86.6 | 0.96297 | 0.96177 | 0.91673 | 0.89485 | 0.91683 | 0.90787 | 0.95142 | 0.92432 | 0.94292 | 0.91745 | 0.91394 | 0.93804 | 0.96915 | 19 | 13
p18otc358b.sav | 7760.2 | 3937.9 | 1107.5 | 1896.8 | 2300 | 1695 | 1617.1 | 899 | 358.9 | 763.2 | 763.2 | 95.4 | 154.2 | 77.2 | 25.1 | 25.6 | 1903.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2105.9 | -888.5 | -289.7 | 339.4 | 1603.4 | -636.5 | 751.5 | 262.3 | 87.6 | -209.2 | 492.4 | 503 | -36 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 126.5 | 1394.8 | 3267 | 59 | 20.3 | 22.9 | 9.4 | 10 | 10 | 0 | 0.97482 | 0.998 | 0.99337 | 0.90363 | 1.0337 | 0.91097 | 0.94103 | 0.96137 | 0.94527 | 0.92857 | 0.9244 | 0.93065 | 0.94714 | 0.98346 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 55 | 67 | 68.1 | 56.6 | 70.4 | 66.4 | 93.9 | 90.1 | 45.6 | 34.3 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1216 | 4976.7 | 29023.6 | 3273.9 | 209.3 | 196.2 | 3679.4 | 7635.3 | 305.2 | -1224.2 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 272.1 | 86.7 | 55.108 | 25 | 44.6 | 1.0753 | 1.0666 | 1.0674 | 1.0269 | 0 | 0 | 129 | 0 | 1695 | 2044.5 | 358.9 | 272.1 | 86.7 | 0.998 | 0.99337 | 0.90363 | 1.0337 | 0.91097 | 0.94103 | 0.96137 | 0.94527 | 0.92857 | 0.9244 | 0.93065 | 0.94714 | 0.98346 | 0 | 0
p18otc358b_amps.sav | 7926.4 | 4006.3 | 1107.5 | 1896.8 | 2298.7 | 1902.2 | 1617.1 | 1138.9 | 109.1 | 760.7 | 760.7 | 88.3 | 134.2 | 67.4 | 24 | 24.5 | 1859.9 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2094.1 | -1018.7 | -373.9 | 217.9 | 1633.9 | -605 | 727.3 | 237 | 132.1 | -253.2 | 536.4 | 531.9 | -69.6 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.6 | 1429.5 | 3267 | 54.3 | 13.9 | 30.1 | 11.1 | 10 | 10 | 0 | 0.99217 | 1.0396 | 1.0315 | 0.90363 | 1.0337 | 0.91097 | 0.94103 | 1.0123 | 0.95246 | 0.93633 | 0.90822 | 0.91369 | 0.93517 | 0.983 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 0 | 30.4 | 37 | 0 | 69 | 98.4 | 69.6 | 100 | 93.5 | 48.9 | 34.7 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1252.3 | 4940.5 | 29023.6 | 3273.9 | 218.8 | 186.7 | 3679.4 | 7581.2 | 305.3 | -1170.2 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 0 | 109.1 | 73 | 25 | 66 | 1.0753 | 1.0653 | 1.0657 | 1.0267 | 0 | 0 | 129 | 0 | 1902.2 | 2272.2 | 358.9 | 272.1 | 86.7 | 1.0417 | 1.0384 | 1 | 1 | 1 | 1 | 1.053 | 1.0076 | 1.0084 | 0.9825 | 0.98178 | 0.98736 | 0.99953 | 1 | 1
p18otc358b_amps_s.sav | 7925.3 | 4006.4 | 1107.5 | 1896.8 | 2298.7 | 1900.9 | 1617.1 | 1137.2 | 111.2 | 760.7 | 760.7 | 88.3 | 134.7 | 67.5 | 24 | 24.5 | 1860.4 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2094.3 | -1017.3 | -372.9 | 219.3 | 1633.6 | -605.4 | 727.7 | 237.4 | 131.6 | -252.7 | 535.9 | 531.6 | -69.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 104.7 | 1429.4 | 3267 | 54.3 | 13.9 | 30.1 | 11.1 | 10 | 10 | 0 | 0.9935 | 1.0421 | 1.0347 | 0.90363 | 1.0337 | 0.91097 | 0.94103 | 1.0126 | 0.96842 | 0.98079 | 0.9152 | 0.92101 | 0.93983 | 0.98552 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 0 | 30.5 | 37.2 | 0 | 69.3 | 97.6 | 69.6 | 99.9 | 93.5 | 48.9 | 34.7 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1251.9 | 4940.9 | 29023.6 | 3273.9 | 218.7 | 186.8 | 3679.4 | 7581.2 | 305.1 | -1170 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 0 | 111.2 | 72.895 | 25 | 68.2 | 1.0755 | 1.0655 | 1.0659 | 1.0268 | 0 | 0 | 129 | 0 | 1900.9 | 2270.7 | 358.9 | 272.1 | 86.7 | 1.0442 | 1.0416 | 1 | 1 | 1 | 1 | 1.0532 | 1.0245 | 1.0562 | 0.99005 | 0.98964 | 0.99228 | 1.0021 | 2 | 1
p18otc358b_dsbg.sav | 7813.3 | 3950.1 | 1107.5 | 1896.8 | 2299.5 | 1761.5 | 1617.1 | 977.2 | 280.9 | 766.4 | 766.4 | 92.7 | 141.2 | 69.6 | 24.7 | 25.2 | 1886.1 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2101.4 | -940.7 | -324.9 | 289.5 | 1619.8 | -623.9 | 739 | 249.2 | 105.8 | -227.2 | 510.4 | 516.2 | -49.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.4 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 108 | 1413.3 | 3267 | 57.2 | 18.1 | 25.5 | 10 | 10 | 10 | 0 | 0.97746 | 1.0025 | 0.99943 | 0.88883 | 0.9798 | 0.8955 | 0.92337 | 0.95376 | 0.9884 | 0.97504 | 0.95839 | 0.96621 | 0.97634 | 0.98773 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 48.9 | 59.5 | 71.4 | 17.5 | 44.9 | 67.5 | 96.1 | 91.4 | 46.8 | 34.5 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1227.7 | 4965.1 | 29023.6 | 3273.9 | 213.1 | 192.4 | 3679.4 | 7635.3 | 310.1 | -1229 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 280.9 | 0 | 58.479 | 25 | -41.6 | 1.0747 | 1.0657 | 1.0666 | 1.0264 | 0 | 0 | 129 | 0 | 1761.5 | 2118.3 | 358.9 | 272.1 | 86.7 | 1.0045 | 1.0061 | 0.98362 | 0.94783 | 0.98302 | 0.98123 | 0.99208 | 1.0456 | 1.05 | 1.0368 | 1.0382 | 1.0308 | 1.0043 | 3 | 2
p18otc358b_bloxhcb.sav | 7865.1 | 3950.7 | 1107.5 | 1896.8 | 2299.8 | 1561.9 | 1617.1 | 861.5 | 367.7 | 752.4 | 752.4 | 95 | 153.2 | 77 | 25 | 25.6 | 1880.7 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2099.1 | -783.7 | -458.4 | 398.1 | 1625.7 | -603.8 | 714.6 | 224.1 | 110.5 | -231.8 | 515 | 521.8 | -53.3 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 132.2 | 1389.2 | 3267 | 59.5 | 21.1 | 21.8 | 9.4 | 10 | 10 | 0 | 0.97074 | 0.98925 | 0.98461 | 0.87856 | 0.96791 | 0.88893 | 0.91584 | 0.94936 | 0.9293 | 0.91129 | 0.90935 | 0.91487 | 0.93532 | 0.97693 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 57 | 69.4 | 71.1 | 60.3 | 79.7 | 68.8 | 123.1 | 0 | 71.1 | 34.6 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1264 | 4928.9 | 29023.6 | 3273.9 | 187.1 | 218.4 | 3679.4 | 7635.3 | 309.4 | -1228.4 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 276 | 91.7 | 58.695 | 25 | 49.2 | 1.0747 | 1.0653 | 1.0655 | 1.0263 | 0 | 0 | 129 | 0 | 1561.9 | 2008.1 | 358.9 | 272.1 | 86.7 | 0.99123 | 0.99118 | 0.97226 | 0.93633 | 0.97581 | 0.97323 | 0.98751 | 0.98311 | 0.98139 | 0.98372 | 0.98304 | 0.98752 | 0.99336 | 4 | 3
p18otc358b_bloxhcb_s.sav | 7863.7 | 3950.9 | 1107.5 | 1896.8 | 2299.9 | 1560.3 | 1617.1 | 859.4 | 370.4 | 752.4 | 752.4 | 94.9 | 153.9 | 77.2 | 25 | 25.6 | 1881.3 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2099.2 | -781.9 | -457.1 | 399.9 | 1625.2 | -604.4 | 715.1 | 224.6 | 109.9 | -231.2 | 514.4 | 521.4 | -52.9 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 132.2 | 1389.1 | 3267 | 59.5 | 21.1 | 21.8 | 9.4 | 10 | 10 | 0 | 0.97226 | 0.99205 | 0.98816 | 0.88109 | 0.97085 | 0.89055 | 0.91769 | 0.95026 | 0.94562 | 0.95557 | 0.91659 | 0.92246 | 0.94024 | 0.9796 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 56.9 | 69.3 | 71.1 | 60.8 | 78.5 | 68.8 | 123.1 | 0 | 71 | 34.6 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1263.5 | 4929.4 | 29023.6 | 3273.9 | 186.9 | 218.5 | 3679.4 | 7635.3 | 309.1 | -1228.1 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 276.8 | 93.5 | 58.566 | 25 | 51.1 | 1.0749 | 1.0655 | 1.0656 | 1.0265 | 0 | 0 | 129 | 0 | 1560.3 | 2006.4 | 358.9 | 272.1 | 86.7 | 0.99404 | 0.99475 | 0.97506 | 0.93917 | 0.97758 | 0.9752 | 0.98844 | 1.0004 | 1.0291 | 0.99155 | 0.9912 | 0.99272 | 0.99608 | 5 | 3
p18otc358b_blhcoxll.sav | 8152.7 | 3966.8 | 1107.5 | 1896.8 | 2298.9 | 1948.4 | 1617.1 | 800.6 | 378.2 | 734.3 | 734.3 | 94 | 151.1 | 76.2 | 24.9 | 25.5 | 1840.2 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2087.3 | -650.3 | -672 | 475.8 | 1657 | -559.5 | 667.2 | 175.2 | 150.6 | -271.4 | 554.5 | 550.3 | -82.8 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 142.5 | 1378.9 | 3267 | 59.9 | 22.3 | 20.2 | 8.2 | 10 | 10 | 0 | 0.96559 | 0.97585 | 0.97097 | 0.83415 | 0.91637 | 0.849 | 0.86991 | 0.92736 | 0.9011 | 0.88068 | 0.88163 | 0.88578 | 0.91361 | 0.96465 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 60.3 | 73.4 | 76 | 66.5 | 95.4 | 23.7 | 0 | 0 | 101 | 35.1 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1313 | 4880.2 | 29023.6 | 3273.9 | 163.5 | 242 | 3679.4 | 7635.3 | 318.3 | -1237.3 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 279.4 | 98.9 | 64.958 | 25 | 55.8 | 1.0759 | 1.0712 | 1.0729 | 1.028 | 0 | 0 | 129 | 0 | 1948.4 | 1948.4 | 358.9 | 272.1 | 86.7 | 0.97781 | 0.97745 | 0.92311 | 0.88647 | 0.93197 | 0.92442 | 0.96462 | 0.95327 | 0.94843 | 0.95373 | 0.95179 | 0.9646 | 0.98087 | 6 | 4
p18otc358b_blhcoxll_s.sav | 8151.1 | 3967.1 | 1107.5 | 1896.8 | 2298.9 | 1946.4 | 1617.1 | 798.4 | 381.2 | 734.2 | 734.2 | 93.9 | 151.7 | 76.4 | 24.9 | 25.4 | 1840.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2087.5 | -648.4 | -670.4 | 477.7 | 1656.5 | -560.1 | 667.8 | 175.9 | 149.9 | -270.7 | 553.9 | 549.9 | -82.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 142.4 | 1379 | 3267 | 59.9 | 22.3 | 20.2 | 8.1 | 10 | 10 | 0 | 0.96708 | 0.97862 | 0.97449 | 0.83678 | 0.91944 | 0.85069 | 0.87187 | 0.92829 | 0.91715 | 0.92396 | 0.88874 | 0.89325 | 0.9184 | 0.96728 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 60.2 | 73.3 | 76 | 66.8 | 94.3 | 23.7 | 0 | 0 | 101 | 35.1 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1312.3 | 4880.8 | 29023.6 | 3273.9 | 163.4 | 242.1 | 3679.4 | 7635.3 | 318 | -1237 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 280.3 | 100.9 | 64.807 | 25 | 57.9 | 1.0762 | 1.0714 | 1.073 | 1.0281 | 0 | 0 | 129 | 0 | 1946.4 | 1946.4 | 358.9 | 272.1 | 86.7 | 0.98058 | 0.98099 | 0.92602 | 0.88944 | 0.93383 | 0.92651 | 0.96559 | 0.97025 | 0.99504 | 0.96142 | 0.95981 | 0.96966 | 0.98355 | 7 | 4
p18otc358b_mpsl.sav | 7657.4 | 4041.2 | 1107.5 | 1896.8 | 2300.3 | 1604.6 | 1617.1 | 848.3 | 370.9 | 749.1 | 749.1 | 95 | 153.1 | 77 | 25 | 25.6 | 1873.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2097.1 | -721.3 | 0 | 472 | 1650.5 | -553.6 | 646.7 | 154.4 | 117.3 | -238.5 | 521.7 | 537.3 | -58.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.5 | 1385.8 | 3267 | 59.9 | 21.4 | 21.6 | 9.5 | 10 | 10 | 0 | 0.9684 | 0.98405 | 0.97937 | 0.86303 | 0.94992 | 0.87424 | 0.899 | 0.94011 | 0.91938 | 0.90054 | 0.89926 | 0.90429 | 0.92705 | 0.97157 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 58 | 70.6 | 72.6 | 62.2 | 84.7 | 71.8 | 106.4 | 99.5 | 56.5 | 34.9 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1209.2 | 4983.6 | 29023.6 | 3273.9 | 237 | 168.5 | 3679.4 | 7635.3 | 311.2 | -1230.2 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 276.8 | 94.1 | 60.732 | 25 | 51.4 | 1.0746 | 1.0652 | 1.0659 | 1.0262 | 0 | 0 | 129 | 0 | 1604.6 | 1996.3 | 358.9 | 272.1 | 86.7 | 0.98602 | 0.98591 | 0.95507 | 0.91892 | 0.95968 | 0.95534 | 0.97789 | 0.97261 | 0.96981 | 0.9728 | 0.97168 | 0.97879 | 0.98791 | 8 | 5
p18otc358b_mpsl_s.sav | 7656.5 | 4041 | 1107.5 | 1896.8 | 2300.3 | 1603.3 | 1617.1 | 846.3 | 373.5 | 749 | 749 | 94.9 | 153.7 | 77.2 | 25 | 25.6 | 1874.5 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2097.3 | -720.2 | 0 | 473.3 | 1649.8 | -554.7 | 647.8 | 155.5 | 116.5 | -237.7 | 520.9 | 536.7 | -57.7 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.4 | 1385.8 | 3267 | 59.9 | 21.4 | 21.6 | 9.5 | 10 | 10 | 0 | 0.96995 | 0.98691 | 0.98298 | 0.86579 | 0.95312 | 0.87606 | 0.90109 | 0.94111 | 0.93574 | 0.94461 | 0.90658 | 0.91197 | 0.93202 | 0.97429 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 31.7 | 57.9 | 70.5 | 72.6 | 62.6 | 83.5 | 71.7 | 106.2 | 99.5 | 56.4 | 34.9 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1208.7 | 4984 | 29023.6 | 3273.9 | 236.7 | 168.9 | 3679.4 | 7635.3 | 310.9 | -1229.8 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 277.6 | 95.9 | 60.568 | 25 | 53.4 | 1.0748 | 1.0655 | 1.066 | 1.0264 | 0 | 0 | 129 | 0 | 1603.3 | 1994.7 | 358.9 | 272.1 | 86.7 | 0.98889 | 0.98954 | 0.95812 | 0.92202 | 0.96168 | 0.95756 | 0.97893 | 0.98992 | 1.0173 | 0.98072 | 0.97993 | 0.98404 | 0.99068 | 9 | 5
p18otc358b_angr1.sav | 7772.5 | 3935.1 | 1107.5 | 1896.8 | 2299.8 | 1710.7 | 1617.1 | 923.7 | 331.6 | 747.4 | 747.4 | 98.6 | 171.4 | 85.5 | 25.6 | 26.2 | 1902 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2104.6 | -906.7 | -302.6 | 321.8 | 1606.5 | -632.1 | 745.7 | 256.2 | 88.4 | -209.9 | 493.1 | 504.6 | -36.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 128.4 | 1393.1 | 3267 | 61.6 | 22.8 | 20 | 9.1 | 10 | 10 | 0 | 0.96343 | 0.96428 | 0.96066 | 0.89619 | 1.0248 | 0.91489 | 0.94551 | 0.96459 | 0.92293 | 0.9044 | 0.92123 | 0.92733 | 0.94611 | 0.98242 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 115.6 | 64.7 | 52.2 | 64.4 | 66.7 | 94.5 | 90.5 | 46 | 34.3 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1224.5 | 4968.2 | 29023.6 | 3273.9 | 210 | 195.4 | 3679.4 | 7635.3 | 304.2 | -1223.2 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 254.1 | 77.5 | 52.392 | 25 | 35.5 | 1.0749 | 1.0661 | 1.0671 | 1.0266 | 0 | 0 | 129 | 0 | 1710.7 | 2062.4 | 358.9 | 272.1 | 86.7 | 0.96621 | 0.96707 | 0.99177 | 0.99135 | 1.0043 | 1.0048 | 1.0033 | 0.97637 | 0.97397 | 0.99657 | 0.99643 | 0.99891 | 0.99894 | 10 | 6
p18otc358b_angr2.sav | 7772 | 3937.9 | 1107.5 | 1896.8 | 2299.8 | 1709.9 | 1617.1 | 918.5 | 337.3 | 749.1 | 749.1 | 98.2 | 169.7 | 84.5 | 25.5 | 26.1 | 1902.2 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2104.7 | -903 | -299.8 | 325.4 | 1605.9 | -633.2 | 747.1 | 257.7 | 88.4 | -209.9 | 493.1 | 504.3 | -36.4 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 127.9 | 1393.6 | 3267 | 61.3 | 22.4 | 20.4 | 9.2 | 10 | 10 | 0 | 0.96615 | 0.97365 | 0.96947 | 0.90071 | 1.0302 | 0.91626 | 0.94706 | 0.96505 | 0.9297 | 0.91173 | 0.92325 | 0.92943 | 0.94734 | 0.98321 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 89.2 | 0 | 65.2 | 52.7 | 65 | 66.6 | 94.4 | 90.5 | 45.9 | 34.3 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1220.4 | 4972.3 | 29023.6 | 3273.9 | 209.9 | 195.6 | 3679.4 | 7635.3 | 304.3 | -1223.3 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 258 | 79.3 | 52.683 | 25 | 37.3 | 1.0748 | 1.0661 | 1.0671 | 1.0266 | 0 | 0 | 129 | 0 | 1709.9 | 2061.2 | 358.9 | 272.1 | 86.7 | 0.9756 | 0.97594 | 0.99677 | 0.9966 | 1.0058 | 1.0064 | 1.0038 | 0.98353 | 0.98186 | 0.99876 | 0.99869 | 1.0002 | 0.99975 | 11 | 7
p18otc358b_angr12.sav | 7838.2 | 3907.5 | 1107.5 | 1896.8 | 2299.4 | 1795.7 | 1617.1 | 1021.6 | 169.9 | 689.4 | 689.4 | 114 | 224.4 | 111.5 | 28.3 | 28.9 | 1885.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2098.9 | -1016.9 | -381.6 | 214.9 | 1625.7 | -603.5 | 709.6 | 218.9 | 97.6 | -218.5 | 501.5 | 515.5 | -41.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.1 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.1 | 184 | 1338.5 | 3267 | 70.5 | 36.2 | 7.9 | 9.9 | 10 | 10 | 0 | 0.86377 | 0.75251 | 0.7442 | 0.81848 | 0.93127 | 0.90143 | 0.93014 | 0.96128 | 0.74716 | 0.7103 | 0.86972 | 0.87328 | 0.91464 | 0.96105 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 0 | 0 | 48.3 | 31.7 | 68.3 | 68.6 | 98.3 | 92.9 | 48.5 | 34.5 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1235.6 | 4957.2 | 29023.6 | 3273.9 | 216.3 | 189.2 | 3679.4 | 7635.3 | 304.1 | -1223.1 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 145.1 | 24.8 | 37.307 | 25 | -17.4 | 1.0723 | 1.063 | 1.0648 | 1.025 | 0 | 0 | 129 | 0 | 1795.7 | 2159.9 | 358.9 | 272.1 | 86.7 | 0.75402 | 0.74917 | 0.90577 | 0.90088 | 0.98953 | 0.98843 | 0.99991 | 0.79042 | 0.76494 | 0.94085 | 0.93836 | 0.96569 | 0.97721 | 12 | 8
p18otc358b_grgr.sav | 7800.3 | 3926 | 1107.5 | 1896.8 | 2299.9 | 1748 | 1617.1 | 963.8 | 265.2 | 674.4 | 674.4 | 152.8 | 216.7 | 106.6 | 33.5 | 34.3 | 1892.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2099.1 | -949.9 | -333.4 | 279.9 | 1615.3 | -621 | 732.2 | 242.3 | 94.3 | -215.5 | 498.6 | 510.1 | -40.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -70.2 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 149 | 1372.9 | 3267 | 76.5 | 54.2 | 4.3 | 12.3 | 10 | 10 | 0 | 0.88981 | 0.90073 | 0.89452 | 0.891 | 1.0186 | 0.92937 | 0.96199 | 0.97407 | 0.8768 | 0.85419 | 0.91633 | 0.92218 | 0.94539 | 0.98052 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.7 | 37.4 | 56 | 39.7 | 52.1 | 67.4 | 96 | 91.5 | 46.9 | 34.4 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1229.4 | 4963.6 | 29023.6 | 3273.9 | 212.1 | 193.3 | 3679.4 | 7635.3 | 302.8 | -1221.8 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 211.3 | 53.9 | 44.576 | 25 | 12.2 | 1.0744 | 1.0651 | 1.0664 | 1.0268 | 0 | 0 | 129 | 0 | 1748 | 2104.8 | 358.9 | 272.1 | 86.7 | 0.90253 | 0.90049 | 0.98602 | 0.98533 | 1.0202 | 1.0223 | 1.0132 | 0.92757 | 0.9199 | 0.99127 | 0.9909 | 0.99815 | 0.99701 | 13 | 9
p18otc358b_anpf.sav | 7917.2 | 3957.2 | 1107.5 | 1896.8 | 2298.8 | 1893.4 | 1617.1 | 1132.6 | 97.6 | 759 | 759 | 88.2 | 134.2 | 67.4 | 24 | 24.5 | 1856.3 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2093.1 | -1061 | -407.5 | 175.5 | 1643.3 | -591.2 | 709.5 | 218.6 | 135.6 | -256.7 | 539.9 | 537.6 | -72.2 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.6 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 106 | 1415.2 | 3267 | 54.4 | 14 | 30 | 11.1 | 10 | 10 | 0 | 0.99198 | 1.0393 | 1.031 | 1.1229 | 1.0221 | 1.0881 | 1.1407 | 1.0479 | 0.95018 | 0.93387 | 0.90775 | 0.91319 | 0.93607 | 0.98599 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 30.6 | 37.3 | 0 | 70.2 | 101.5 | 70 | 100.8 | 94.2 | 49.7 | 34.8 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1251.2 | 4941.6 | 29023.6 | 3273.9 | 221.8 | 183.7 | 3679.4 | 7635.3 | 306.9 | -1226 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | -13.2 | 110.8 | 76.254 | 25 | 67.6 | 1.0754 | 1.0653 | 1.0657 | 1.0267 | 0 | 0 | 129 | 0 | 1893.4 | 2266.3 | 358.9 | 272.1 | 86.7 | 1.0413 | 1.0379 | 1.2426 | 0.98875 | 1.1945 | 1.2122 | 1.09 | 1.0052 | 1.0057 | 0.98199 | 0.98124 | 0.98831 | 1.0026 | 14 | 10
p18otc358b_antbdy.sav | 7782 | 3938.5 | 1107.5 | 1896.8 | 2299.7 | 1722.5 | 1617.1 | 931.4 | 327.5 | 763.1 | 763.1 | 94.4 | 151.3 | 75.8 | 24.9 | 25.5 | 1898.1 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2104.4 | -914.9 | -308 | 314.6 | 1604.6 | -627.1 | 745.8 | 256.4 | 93.4 | -214.9 | 498.1 | 506.4 | -40.5 | 288 | 580 | 465.6 | 380 | 191.5 | 78 | 302 | -71.3 | 151 | 39 | 59 | 2534 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 119.7 | 1401.7 | 3267 | 58.3 | 19.4 | 23.9 | 9.6 | 10 | 10 | 0 | 0.97759 | 1.0044 | 0.99924 | 0.91261 | 1.0445 | 0.88569 | 0.91212 | 0.90459 | 0.9463 | 0.92968 | 0.91645 | 0.92231 | 0.93801 | 0.97356 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 51.6 | 62.8 | 59 | 57.3 | 71 | 66.9 | 94.9 | 90.7 | 46.2 | 34.4 | 560 | 560 | 300 | 300 | 1720 | 22788.6 | 1220.3 | 4972.4 | 29023.6 | 3273.9 | 210.4 | 195.1 | 3679.4 | 7635.3 | 312.5 | -1231.6 | 6720.3 | 900 | 3168.5 | 670 | 563.1 | 490 | 239.2 | 88.3 | 48.098 | 25 | 46.1 | 1.0754 | 1.0665 | 1.0672 | 1.0269 | 0 | 0 | 129 | 0 | 1722.5 | 2075.5 | 358.9 | 272.1 | 86.7 | 1.0064 | 1.0059 | 1.0099 | 1.0104 | 0.97225 | 0.96928 | 0.94094 | 1.0011 | 1.0012 | 0.9914 | 0.99104 | 0.99036 | 0.98993 | 15 | 11
p18otc358b_brbo_brkp.sav | 7891.2 | 3730.5 | 1107.5 | 1896.8 | 2394.7 | 1698.5 | 1629.9 | 908.3 | 371.6 | 775.3 | 775.3 | 98.3 | 158.9 | 80.7 | 25.4 | 25.9 | 1939.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.5 | 2117.3 | -1320.1 | -615.6 | -120.1 | 791.5 | -334.1 | 867.1 | 186.2 | 52.2 | -174 | 457.2 | 450.1 | -8.9 | 288 | 585.5 | 467.4 | 383.6 | 193.4 | 78 | 305.6 | -74.4 | 151 | 39 | 59 | 2534 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 145.2 | 1381.1 | 3272 | 60.7 | 21.3 | 22.4 | 10.1 | 10 | 10 | 0 | 0.95613 | 0.96588 | 0.96116 | 0.82136 | 0.90149 | 0.83661 | 0.85559 | 0.91687 | 0.89312 | 0.872 | 0.87911 | 0.88314 | 0.91207 | 0.96376 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 59.2 | 72 | 75.9 | 65.5 | 95 | 72 | 106.1 | 99.8 | 55.3 | 38.8 | 0 | 560 | 300 | 300 | 1160 | 22788.6 | 1278.6 | 5106.8 | 29215.7 | 3283.2 | 214.1 | -364.8 | 3132.4 | 7635.3 | 328.6 | -1230 | 6737.7 | 909 | 3199.7 | 673.9 | 568.7 | 490 | 274.5 | 97.1 | 65.661 | 25 | 54.2 | 1.0677 | 1.0575 | 1.0583 | 1.0201 | 0 | 0 | 129 | 0 | 1698.5 | 2085.8 | 358.9 | 272.1 | 86.7 | 0.96782 | 0.96757 | 0.90896 | 0.87208 | 0.91837 | 0.90921 | 0.95371 | 0.94483 | 0.93908 | 0.95101 | 0.94895 | 0.96297 | 0.97997 | 16 | 12
p18otc358b_brbo_brkp_s.sav | 7881.6 | 3728.2 | 1107.5 | 1896.8 | 2392.1 | 1689.6 | 1629.9 | 897.7 | 385.7 | 775.8 | 775.8 | 98.1 | 160.6 | 81.2 | 25.4 | 25.9 | 1942.8 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.5 | 2118 | -1310.8 | -609.3 | -111.4 | 790.2 | -338.5 | 864.9 | 188.8 | 49.1 | -171 | 454.2 | 447.9 | -6.5 | 288 | 585.5 | 467.4 | 383.6 | 193.4 | 78 | 305.6 | -74.4 | 151 | 39 | 59 | 2534 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.4 | 42.4 | 38.4 | 6.1 | 276.7 | 1745.2 | 144.6 | 1381.5 | 3271.8 | 60.8 | 21.3 | 22.2 | 10 | 10 | 10 | 0 | 0.96131 | 0.97559 | 0.97127 | 0.85593 | 0.94168 | 0.85795 | 0.88026 | 0.92767 | 0.91649 | 0.92322 | 0.89141 | 0.89606 | 0.92107 | 0.9695 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 59.3 | 72.2 | 76 | 65.3 | 92.8 | 71.7 | 105.7 | 99.5 | 55 | 38.8 | 0 | 560 | 300 | 300 | 1160 | 22788.6 | 1274.4 | 5108.2 | 29213 | 3283.2 | 212.8 | -363.5 | 3132.4 | 7635.3 | 327.2 | -1228.8 | 6737.5 | 909 | 3199.1 | 673.9 | 568.5 | 490 | 286.1 | 99.6 | 64.701 | 25 | 56.7 | 1.0691 | 1.0591 | 1.0596 | 1.0212 | 0 | 0 | 129 | 0 | 1689.6 | 2075.9 | 358.9 | 272.1 | 86.7 | 0.97754 | 0.97775 | 0.94721 | 0.91095 | 0.9418 | 0.93542 | 0.96495 | 0.96955 | 0.99424 | 0.96431 | 0.96283 | 0.97247 | 0.98581 | 17 | 12
p18otc358b_brgo_brkp.sav | 7885.4 | 3718.3 | 1107.5 | 1896.8 | 2399.3 | 1684 | 1630.9 | 892.7 | 375.3 | 774.3 | 774.3 | 99.8 | 160.1 | 82 | 25.6 | 26.1 | 1942.1 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2118 | -1328.4 | -622.3 | -116.3 | 778.4 | -321.6 | 873.6 | 182.7 | 49.6 | -171.5 | 454.7 | 448.2 | -6.9 | 288 | 586 | 467.4 | 384 | 193.5 | 78 | 306 | -74.7 | 151 | 39 | 59 | 2534 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 159.9 | 1366.7 | 3272 | 61.3 | 22.2 | 21.6 | 10 | 10 | 10 | 0 | 0.94619 | 0.94818 | 0.94194 | 0.78487 | 0.85892 | 0.80542 | 0.81927 | 0.89893 | 0.84426 | 0.81852 | 0.83001 | 0.83147 | 0.87483 | 0.94371 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 12 | 31.7 | 62.1 | 75.6 | 78.5 | 75.3 | 120.8 | 72 | 106.3 | 100.1 | 55.6 | 39 | 0 | 560 | 300 | 300 | 1160 | 22788.6 | 1281.1 | 5114.2 | 29225.7 | 3283.2 | 224.8 | -375 | 3133.1 | 7635.3 | 337.1 | -1237.7 | 6738.7 | 909 | 3201.4 | 674 | 569 | 490 | 269.9 | 105.4 | 69.833 | 25 | 61.3 | 1.0659 | 1.0558 | 1.057 | 1.0187 | 0 | 0 | 129 | 0 | 1684 | 2071.3 | 358.9 | 272.1 | 86.7 | 0.95008 | 0.94823 | 0.86857 | 0.83089 | 0.88413 | 0.87061 | 0.93505 | 0.89314 | 0.88148 | 0.89789 | 0.89343 | 0.92365 | 0.95958 | 18 | 13
p18otc358b_brgo_brkp_s.sav | 7876.9 | 3718 | 1107.5 | 1896.8 | 2398.2 | 1675 | 1630.9 | 881.3 | 390.7 | 774.8 | 774.8 | 99.6 | 162 | 82.6 | 25.5 | 26.1 | 1945.4 | 330 | 330 | 810 | 815 | 2285 | 141 | 2123.6 | 2118.9 | -1317.6 | -614.9 | -106.2 | 777.6 | -326.7 | 873.1 | 186 | 46.4 | -168.3 | 451.5 | 446.2 | -4.5 | 288 | 586 | 467.4 | 384 | 193.5 | 78 | 306 | -74.7 | 151 | 39 | 59 | 2534 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 159 | 1367.5 | 3272 | 61.4 | 22.2 | 21.4 | 9.9 | 10 | 10 | 0 | 0.95145 | 0.95796 | 0.95218 | 0.81948 | 0.89929 | 0.8274 | 0.84488 | 0.91049 | 0.86826 | 0.86934 | 0.84373 | 0.84593 | 0.88514 | 0.95086 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | -186 | 24 | 63.4 | 62.2 | 75.7 | 78.5 | 74.9 | 118.9 | 71.7 | 105.8 | 99.7 | 55.3 | 38.9 | 0 | 560 | 300 | 300 | 1160 | 22788.6 | 1277 | 5115.4 | 29222.8 | 3283.2 | 223.2 | -373.4 | 3133.1 | 7635.3 | 335.5 | -1236.2 | 6738.6 | 909 | 3200.9 | 674 | 568.9 | 490 | 282.1 | 108.6 | 68.761 | 25 | 64.5 | 1.0673 | 1.0573 | 1.0583 | 1.0198 | 0 | 0 | 129 | 0 | 1675 | 2061.2 | 358.9 | 272.1 | 86.7 | 0.95988 | 0.95854 | 0.90688 | 0.86995 | 0.90826 | 0.89782 | 0.94708 | 0.91853 | 0.93621 | 0.91273 | 0.90897 | 0.93454 | 0.96685 | 19 | 13
p18otc364b.sav | 7884.3 | 3982.1 | 1107.5 | 1896.8 | 2300 | 1832.5 | 1840 | 867.1 | 364.4 | 754.6 | 754.6 | 93.2 | 151.5 | 75.9 | 24.8 | 25.3 | 1879.9 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2101.3 | -1011 | -362 | 270.3 | 1603.4 | -707.6 | 707.5 | 219.5 | 114.8 | -236 | 519.2 | 521.5 | -56.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.4 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 129.4 | 1395.3 | 3270.4 | 66.8 | 22.2 | 20 | 8.6 | 10 | 10 | 0 | 0.97447 | 0.99569 | 0.9911 | 0.88537 | 1.0201 | 0.89359 | 0.92118 | 0.95187 | 0.94267 | 0.92576 | 0.9218 | 0.92792 | 0.94478 | 0.98144 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 55.9 | 68 | 70.9 | 57.1 | 70.9 | 69.4 | 99.9 | 93.7 | 49 | 35 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1258.9 | 5175.8 | 29265.5 | 3273.9 | 213 | 195.9 | 3682.9 | 7635.3 | 315.7 | -1424.3 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 277.5 | 86.9 | 58.208 | 28.2 | 44.7 | 1.0754 | 1.0674 | 1.0661 | 1.0281 | 0 | 0 | 129 | 0 | 1832.5 | 2204.7 | 364.4 | 277.5 | 86.9 | 0.99569 | 0.9911 | 0.88537 | 1.0201 | 0.89359 | 0.92118 | 0.95187 | 0.94267 | 0.92576 | 0.9218 | 0.92792 | 0.94478 | 0.98144 | 0 | 0
p18otc364b_amps.sav | 8054.5 | 4051 | 1107.5 | 1896.8 | 2298.6 | 2045.3 | 1840 | 1113.1 | 110.3 | 752.5 | 752.5 | 85.8 | 131.1 | 65.7 | 23.7 | 24.2 | 1835.5 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2089.5 | -1144.2 | -448.3 | 146.5 | 1634.2 | -675.9 | 682.3 | 193.3 | 159.7 | -280.5 | 563.7 | 550.2 | -90.1 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.4 | 1432.2 | 3270.4 | 62 | 15.6 | 27.3 | 10 | 10 | 10 | 0 | 0.99417 | 1.0427 | 1.0341 | 0.88537 | 1.0201 | 0.89359 | 0.92118 | 1.0117 | 0.95303 | 0.93695 | 0.90675 | 0.91214 | 0.93381 | 0.98217 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 0 | 30.3 | 36.9 | 0 | 69.9 | 99.7 | 72.7 | 106.2 | 97.2 | 52.5 | 35.4 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1297.6 | 5137.2 | 29265.5 | 3273.9 | 223 | 185.9 | 3682.9 | 7581.2 | 315.3 | -1369.7 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 0 | 110.3 | 76.637 | 28.2 | 67.1 | 1.0755 | 1.0658 | 1.0639 | 1.0279 | 0 | 0 | 129 | 0 | 2045.3 | 2438.1 | 364.4 | 277.5 | 86.9 | 1.0472 | 1.0434 | 1 | 1 | 1 | 1 | 1.0629 | 1.011 | 1.0121 | 0.98367 | 0.98299 | 0.98839 | 1.0007 | 1 | 1
p18otc364b_amps_s.sav | 8053.4 | 4051.1 | 1107.5 | 1896.8 | 2298.7 | 2043.9 | 1840 | 1111.4 | 112.4 | 752.5 | 752.5 | 85.7 | 131.5 | 65.8 | 23.7 | 24.2 | 1835.9 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2089.7 | -1142.8 | -447.3 | 147.9 | 1633.8 | -676.3 | 682.7 | 193.7 | 159.2 | -280 | 563.2 | 549.9 | -89.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 105.5 | 1432.1 | 3270.4 | 62 | 15.6 | 27.3 | 10 | 10 | 10 | 0 | 0.99542 | 1.045 | 1.0372 | 0.88537 | 1.0201 | 0.89359 | 0.92118 | 1.012 | 0.96889 | 0.98131 | 0.9137 | 0.91943 | 0.93846 | 0.98467 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 0 | 30.4 | 37 | 0 | 70.1 | 99 | 72.7 | 106.1 | 97.2 | 52.4 | 35.4 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1297.2 | 5137.6 | 29265.5 | 3273.9 | 222.9 | 186 | 3682.9 | 7581.2 | 315.1 | -1369.5 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 0 | 112.4 | 76.532 | 28.2 | 69.2 | 1.0757 | 1.066 | 1.0641 | 1.028 | 0 | 0 | 129 | 0 | 2043.9 | 2436.6 | 364.4 | 277.5 | 86.9 | 1.0495 | 1.0465 | 1 | 1 | 1 | 1 | 1.0632 | 1.0278 | 1.06 | 0.99121 | 0.99085 | 0.99331 | 1.0033 | 2 | 1
p18otc364b_dsbg.sav | 7938.1 | 3993.7 | 1107.5 | 1896.8 | 2299.4 | 1900.1 | 1840 | 946.6 | 285.1 | 757.9 | 757.9 | 90.4 | 138.4 | 68.1 | 24.4 | 24.9 | 1862.1 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2096.8 | -1064.3 | -398.1 | 219.5 | 1619.8 | -694.9 | 694.4 | 205.9 | 133.1 | -254.2 | 537.4 | 534.6 | -70.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.5 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 110.7 | 1413.9 | 3270.4 | 65.1 | 20 | 22.6 | 9.1 | 10 | 10 | 0 | 0.97717 | 1.0001 | 0.99717 | 0.86926 | 0.95712 | 0.8768 | 0.90194 | 0.94359 | 0.98629 | 0.97278 | 0.9564 | 0.96414 | 0.97441 | 0.98584 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 49.6 | 60.5 | 74.2 | 17.8 | 45 | 70.5 | 102.1 | 95 | 50.3 | 35.2 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1271.3 | 5163.4 | 29265.5 | 3273.9 | 217.1 | 191.8 | 3682.9 | 7635.3 | 320.8 | -1429.2 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 285.1 | 0 | 61.677 | 28.2 | -41.6 | 1.0747 | 1.0662 | 1.0651 | 1.0276 | 0 | 0 | 129 | 0 | 1900.1 | 2279.7 | 364.4 | 277.5 | 86.9 | 1.0044 | 1.0061 | 0.9818 | 0.93824 | 0.98121 | 0.97911 | 0.9913 | 1.0463 | 1.0508 | 1.0375 | 1.039 | 1.0314 | 1.0045 | 3 | 2
p18otc364b_bloxhcb.sav | 7996.1 | 3993.9 | 1107.5 | 1896.8 | 2299.8 | 1696.3 | 1840 | 828.8 | 372 | 743.3 | 743.3 | 92.7 | 150.4 | 75.6 | 24.7 | 25.3 | 1855.4 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2094.1 | -901.7 | -540.5 | 331 | 1626.8 | -673 | 667.7 | 178.5 | 139 | -260 | 543.2 | 541 | -74.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.7 | 1389 | 3270.4 | 67.4 | 23 | 18.9 | 8.7 | 10 | 10 | 0 | 0.96974 | 0.98574 | 0.98112 | 0.85698 | 0.94289 | 0.86869 | 0.89262 | 0.93838 | 0.92474 | 0.90635 | 0.90519 | 0.91051 | 0.93175 | 0.9742 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 58 | 70.6 | 74 | 61 | 81 | 72 | 130.6 | 0 | 75.8 | 35.4 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1310.9 | 5123.9 | 29265.5 | 3273.9 | 189.8 | 219.2 | 3682.9 | 7635.3 | 320.5 | -1428.9 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 280 | 92 | 62.135 | 28.2 | 49.5 | 1.0745 | 1.0655 | 1.0634 | 1.0274 | 0 | 0 | 129 | 0 | 1696.3 | 2167.4 | 364.4 | 277.5 | 86.9 | 0.99001 | 0.98993 | 0.96793 | 0.92429 | 0.97213 | 0.969 | 0.98583 | 0.98098 | 0.97903 | 0.98198 | 0.98124 | 0.98621 | 0.99262 | 4 | 3
p18otc364b_bloxhcb_s.sav | 7994.7 | 3994.2 | 1107.5 | 1896.8 | 2299.8 | 1694.7 | 1840 | 826.7 | 374.8 | 743.3 | 743.3 | 92.6 | 151 | 75.8 | 24.7 | 25.3 | 1856 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2094.3 | -900 | -539 | 332.8 | 1626.4 | -673.6 | 668.3 | 179.1 | 138.4 | -259.4 | 542.6 | 540.6 | -74.2 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 135.7 | 1389 | 3270.4 | 67.4 | 23 | 18.9 | 8.7 | 10 | 10 | 0 | 0.97127 | 0.98856 | 0.98469 | 0.85956 | 0.94588 | 0.87033 | 0.8945 | 0.93928 | 0.94104 | 0.95049 | 0.91242 | 0.91809 | 0.93666 | 0.97688 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 57.9 | 70.5 | 74 | 61.5 | 79.8 | 72 | 130.5 | 0 | 75.7 | 35.4 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1310.4 | 5124.4 | 29265.5 | 3273.9 | 189.7 | 219.3 | 3682.9 | 7635.3 | 320.2 | -1428.7 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 280.9 | 93.9 | 61.999 | 28.2 | 51.4 | 1.0748 | 1.0657 | 1.0636 | 1.0276 | 0 | 0 | 129 | 0 | 1694.7 | 2165.6 | 364.4 | 277.5 | 86.9 | 0.99284 | 0.99353 | 0.97085 | 0.92722 | 0.97397 | 0.97104 | 0.98677 | 0.99827 | 1.0267 | 0.98982 | 0.98941 | 0.9914 | 0.99535 | 5 | 3
p18otc364b_blhcoxll.sav | 8301.9 | 4008.6 | 1107.5 | 1896.8 | 2298.8 | 2107.2 | 1840 | 767.1 | 380 | 724.3 | 724.3 | 91.7 | 147.9 | 74.7 | 24.6 | 25.2 | 1812.5 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2081.9 | -762.1 | -769.4 | 411.6 | 1660.2 | -624.6 | 614.7 | 124.3 | 181.3 | -301.7 | 584.8 | 570.7 | -105 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 147.2 | 1377.5 | 3270.4 | 67.7 | 24.3 | 17.6 | 7.3 | 10 | 10 | 0 | 0.96404 | 0.97085 | 0.96596 | 0.8065 | 0.88418 | 0.8232 | 0.84001 | 0.9135 | 0.89333 | 0.87223 | 0.8744 | 0.87819 | 0.90767 | 0.96053 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 61.5 | 74.8 | 79.2 | 67.8 | 98 | 24.1 | 0 | 0 | 107.5 | 35.9 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1365.8 | 5069.3 | 29265.5 | 3273.9 | 165.8 | 243.2 | 3682.9 | 7635.3 | 330.8 | -1439.2 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 280.5 | 99.5 | 69.076 | 28.2 | 56.4 | 1.0759 | 1.0725 | 1.0723 | 1.0292 | 0 | 0 | 129 | 0 | 2107.2 | 2107.2 | 364.4 | 277.5 | 86.9 | 0.97505 | 0.97463 | 0.91092 | 0.86674 | 0.92123 | 0.91188 | 0.95969 | 0.94766 | 0.94218 | 0.94858 | 0.94641 | 0.96072 | 0.97869 | 6 | 4
p18otc364b_blhcoxll_s.sav | 8300.2 | 4009 | 1107.5 | 1896.8 | 2298.8 | 2105.1 | 1840 | 764.7 | 383 | 724.2 | 724.2 | 91.6 | 148.6 | 74.9 | 24.6 | 25.1 | 1813.1 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2082 | -760.2 | -767.6 | 413.6 | 1659.7 | -625.4 | 615.5 | 125 | 180.7 | -301.1 | 584.2 | 570.3 | -104.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 147.1 | 1377.6 | 3270.4 | 67.7 | 24.2 | 17.5 | 7.3 | 10 | 10 | 0 | 0.96557 | 0.97368 | 0.96953 | 0.80924 | 0.88736 | 0.82495 | 0.84204 | 0.91445 | 0.90939 | 0.91531 | 0.88151 | 0.88566 | 0.91246 | 0.96316 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 61.3 | 74.7 | 79.1 | 68.1 | 96.9 | 24.1 | 0 | 0 | 107.4 | 35.9 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1365.1 | 5070 | 29265.5 | 3273.9 | 165.7 | 243.3 | 3682.9 | 7635.3 | 330.4 | -1438.9 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 281.5 | 101.5 | 68.913 | 28.2 | 58.5 | 1.0762 | 1.0727 | 1.0725 | 1.0293 | 0 | 0 | 129 | 0 | 2105.1 | 2105.1 | 364.4 | 277.5 | 86.9 | 0.97789 | 0.97824 | 0.91401 | 0.86986 | 0.92319 | 0.91409 | 0.96069 | 0.9647 | 0.98871 | 0.95629 | 0.95446 | 0.96579 | 0.98137 | 7 | 4
p18otc364b_mpsl.sav | 7757.1 | 4111.3 | 1107.5 | 1896.8 | 2300.4 | 1721.7 | 1840 | 806.1 | 375.7 | 736.9 | 736.9 | 92.6 | 149.9 | 75.5 | 24.7 | 25.3 | 1841.8 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2090.2 | -803.2 | 0 | 436 | 1663.3 | -602.5 | 572.4 | 81.3 | 152.4 | -273.1 | 556.3 | 564.4 | -84.1 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 141.4 | 1383.3 | 3270.4 | 68 | 23.6 | 18.4 | 8.8 | 10 | 10 | 0 | 0.96565 | 0.97681 | 0.97212 | 0.83026 | 0.91185 | 0.84415 | 0.86432 | 0.92391 | 0.90782 | 0.888 | 0.88859 | 0.89309 | 0.91843 | 0.96599 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 59.6 | 72.6 | 76.5 | 64.3 | 89.4 | 76.3 | 115.8 | 105.7 | 63 | 35.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1251.1 | 5183.6 | 29265.5 | 3273.9 | 248.9 | 160.1 | 3682.9 | 7635.3 | 324.3 | -1432.7 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 280 | 95.8 | 65.634 | 28.2 | 53 | 1.0742 | 1.0651 | 1.0635 | 1.0272 | 0 | 0 | 129 | 0 | 1721.7 | 2146.4 | 364.4 | 277.5 | 86.9 | 0.98104 | 0.98085 | 0.93776 | 0.89387 | 0.94467 | 0.93827 | 0.97063 | 0.96303 | 0.95921 | 0.96397 | 0.96246 | 0.97211 | 0.98426 | 8 | 5
p18otc364b_mpsl_s.sav | 7756.1 | 4111 | 1107.5 | 1896.8 | 2300.4 | 1720.4 | 1840 | 804 | 378.6 | 736.9 | 736.9 | 92.6 | 150.5 | 75.7 | 24.7 | 25.3 | 1842.6 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2090.4 | -802 | 0 | 437.2 | 1662.6 | -603.6 | 573.6 | 82.5 | 151.6 | -272.4 | 555.6 | 563.9 | -83.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 141.3 | 1383.3 | 3270.4 | 68 | 23.6 | 18.4 | 8.8 | 10 | 10 | 0 | 0.9672 | 0.97968 | 0.97573 | 0.83309 | 0.91514 | 0.846 | 0.86645 | 0.92492 | 0.92408 | 0.93167 | 0.89587 | 0.90073 | 0.92336 | 0.96869 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 59.5 | 72.5 | 76.5 | 64.7 | 88.2 | 76.2 | 115.7 | 105.6 | 62.9 | 35.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1250.6 | 5184.1 | 29265.5 | 3273.9 | 248.5 | 160.4 | 3682.9 | 7635.3 | 324 | -1432.4 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 280.9 | 97.7 | 65.46 | 28.2 | 55 | 1.0745 | 1.0653 | 1.0637 | 1.0273 | 0 | 0 | 129 | 0 | 1720.4 | 2144.7 | 364.4 | 277.5 | 86.9 | 0.98392 | 0.98449 | 0.94095 | 0.89709 | 0.94674 | 0.94059 | 0.97169 | 0.98028 | 1.0064 | 0.97187 | 0.9707 | 0.97733 | 0.98701 | 9 | 5
p18otc364b_angr1.sav | 7896.8 | 3979 | 1107.5 | 1896.8 | 2299.8 | 1848.6 | 1840 | 892.4 | 336.5 | 738.8 | 738.8 | 96.5 | 168.8 | 84.2 | 25.3 | 25.9 | 1878.2 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2100 | -1029.6 | -375.3 | 252.4 | 1606.5 | -703.2 | 701.4 | 213.2 | 115.5 | -236.7 | 519.9 | 523 | -57 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.4 | 1393.5 | 3270.4 | 69.5 | 24.7 | 17.1 | 8.5 | 10 | 10 | 0 | 0.96219 | 0.95919 | 0.95575 | 0.87708 | 1.0101 | 0.89786 | 0.92606 | 0.95537 | 0.91815 | 0.89921 | 0.91791 | 0.92384 | 0.9433 | 0.98015 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 117.6 | 67.3 | 52.6 | 65 | 69.7 | 100.6 | 94.1 | 49.4 | 35.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1267.8 | 5166.9 | 29265.5 | 3273.9 | 213.9 | 195.1 | 3682.9 | 7635.3 | 314.6 | -1423.1 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 259.3 | 77.2 | 55.479 | 28.2 | 35.2 | 1.075 | 1.0668 | 1.0658 | 1.0279 | 0 | 0 | 129 | 0 | 1848.6 | 2222.9 | 364.4 | 277.5 | 86.9 | 0.96334 | 0.96433 | 0.99064 | 0.99016 | 1.0048 | 1.0053 | 1.0037 | 0.97399 | 0.97132 | 0.99578 | 0.9956 | 0.99843 | 0.99869 | 10 | 6
p18otc364b_angr2.sav | 7896.3 | 3981.9 | 1107.5 | 1896.8 | 2299.8 | 1847.7 | 1840 | 887.1 | 342.4 | 740.5 | 740.5 | 96 | 167.1 | 83.2 | 25.2 | 25.8 | 1878.4 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2100.1 | -1025.8 | -372.4 | 256.1 | 1605.8 | -704.3 | 702.9 | 214.8 | 115.4 | -236.6 | 519.8 | 522.7 | -57 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 130.9 | 1394 | 3270.4 | 69.2 | 24.4 | 17.5 | 8.5 | 10 | 10 | 0 | 0.96504 | 0.969 | 0.96498 | 0.88179 | 1.0158 | 0.8992 | 0.92759 | 0.9558 | 0.92527 | 0.90693 | 0.92005 | 0.92609 | 0.94461 | 0.98099 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 90.8 | 0 | 67.9 | 53.2 | 65.5 | 69.7 | 100.5 | 94.1 | 49.4 | 35.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1263.5 | 5171.2 | 29265.5 | 3273.9 | 213.7 | 195.3 | 3682.9 | 7635.3 | 314.7 | -1423.3 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 263.3 | 79.1 | 55.762 | 28.2 | 37 | 1.0749 | 1.0668 | 1.0658 | 1.0278 | 0 | 0 | 129 | 0 | 1847.7 | 2221.7 | 364.4 | 277.5 | 86.9 | 0.97319 | 0.97364 | 0.99596 | 0.99575 | 1.0063 | 1.007 | 1.0041 | 0.98154 | 0.97966 | 0.9981 | 0.99803 | 0.99982 | 0.99954 | 11 | 7
p18otc364b_angr12.sav | 7969.3 | 3944.8 | 1107.5 | 1896.8 | 2299.2 | 1942.3 | 1840 | 1002.2 | 156.7 | 684.1 | 684.1 | 112.3 | 216 | 107.9 | 28.2 | 28.8 | 1861.4 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2095.9 | -1153.8 | -464.8 | 132.2 | 1626.6 | -671.1 | 659.7 | 170.3 | 123.9 | -244.4 | 527.4 | 533.1 | -60 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1741.6 | 197.5 | 1332.1 | 3270.4 | 77.2 | 39.4 | 6.7 | 10.2 | 10 | 10 | 0 | 0.83945 | 0.70313 | 0.69482 | 0.77711 | 0.88843 | 0.87629 | 0.90135 | 0.94843 | 0.70123 | 0.65852 | 0.84992 | 0.85244 | 0.90061 | 0.95213 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 0 | 49.8 | 31.6 | 77.3 | 71.8 | 104.8 | 96.8 | 52.3 | 35.2 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1282.8 | 5152 | 29265.5 | 3273.9 | 221.4 | 187.6 | 3682.9 | 7635.3 | 315.5 | -1424 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 138.3 | 18.4 | 39.644 | 28.2 | -24 | 1.0711 | 1.0621 | 1.0622 | 1.0254 | 0 | 0 | 129 | 0 | 1942.3 | 2330.3 | 364.4 | 277.5 | 86.9 | 0.70617 | 0.70106 | 0.87772 | 0.87091 | 0.98064 | 0.97847 | 0.99639 | 0.74388 | 0.71133 | 0.92202 | 0.91866 | 0.95325 | 0.97014 | 12 | 8
p18otc364b_grgr.sav | 7924.9 | 3969.2 | 1107.5 | 1896.8 | 2299.9 | 1886.4 | 1840 | 933.4 | 269.2 | 668.2 | 668.2 | 149.5 | 212 | 104.6 | 33.2 | 33.9 | 1869.5 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2094.8 | -1073.8 | -406.8 | 209.7 | 1615.1 | -692 | 687.4 | 198.8 | 120.9 | -241.7 | 524.9 | 528.2 | -60.2 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.3 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 152.6 | 1372.7 | 3270.4 | 83.2 | 56.1 | 7 | 12.6 | 10 | 10 | 0 | 0.87802 | 0.88635 | 0.88047 | 0.8672 | 0.9981 | 0.91103 | 0.94111 | 0.9644 | 0.86442 | 0.84065 | 0.90985 | 0.9154 | 0.94043 | 0.97707 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 32.1 | 39.1 | 58.7 | 40.4 | 54 | 70.5 | 102.1 | 95.1 | 50.4 | 35.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1273.3 | 5161.7 | 29265.5 | 3273.9 | 216.1 | 192.9 | 3682.9 | 7635.3 | 313.2 | -1421.7 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 216.2 | 53 | 47.857 | 28.2 | 11.2 | 1.0746 | 1.0658 | 1.065 | 1.0281 | 0 | 0 | 129 | 0 | 1886.4 | 2265.9 | 364.4 | 277.5 | 86.9 | 0.89019 | 0.88838 | 0.97948 | 0.97841 | 1.0195 | 1.0216 | 1.0132 | 0.91699 | 0.90807 | 0.98704 | 0.98651 | 0.9954 | 0.99555 | 13 | 9
p18otc364b_anpf.sav | 8045.3 | 4001.4 | 1107.5 | 1896.8 | 2298.7 | 2036.5 | 1840 | 1106.8 | 98.6 | 750.8 | 750.8 | 85.7 | 131.1 | 65.7 | 23.7 | 24.2 | 1832 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2088.5 | -1186.7 | -482.1 | 104 | 1643.4 | -662.1 | 664.3 | 174.8 | 163.2 | -283.9 | 567.1 | 555.7 | -92.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 106.8 | 1417.7 | 3270.4 | 62.1 | 15.7 | 27.1 | 10 | 10 | 10 | 0 | 0.99397 | 1.0422 | 1.0336 | 1.1217 | 1.021 | 1.0871 | 1.1395 | 1.0469 | 0.95062 | 0.93435 | 0.90596 | 0.91132 | 0.9344 | 0.98483 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 30.5 | 37.2 | 0 | 71 | 102.9 | 73.1 | 107.1 | 97.9 | 53.3 | 35.5 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1296.8 | 5138 | 29265.5 | 3273.9 | 226.3 | 182.7 | 3682.9 | 7635.3 | 317 | -1425.5 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | -13.3 | 111.9 | 79.906 | 28.2 | 68.6 | 1.0755 | 1.0658 | 1.0638 | 1.0279 | 0 | 0 | 129 | 0 | 2036.5 | 2432.3 | 364.4 | 277.5 | 86.9 | 1.0467 | 1.0429 | 1.267 | 1.0009 | 1.2165 | 1.237 | 1.0999 | 1.0084 | 1.0093 | 0.98282 | 0.98211 | 0.98901 | 1.0035 | 14 | 10
p18otc364b_antbdy.sav | 7907.5 | 3982.2 | 1107.5 | 1896.8 | 2299.7 | 1862 | 1840 | 901.8 | 331.1 | 754.5 | 754.5 | 92.1 | 148.5 | 74.4 | 24.6 | 25.2 | 1873.8 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2099.7 | -1039.5 | -381.9 | 243.6 | 1604.8 | -697.8 | 701.2 | 213 | 121 | -242.2 | 525.4 | 525.1 | -61.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.4 | 151 | 39 | 59 | 2537.4 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 121.9 | 1402.9 | 3270.4 | 66.1 | 21.3 | 21 | 8.7 | 10 | 10 | 0 | 0.97745 | 1.0025 | 0.99735 | 0.89381 | 1.0303 | 0.86197 | 0.88486 | 0.88448 | 0.94345 | 0.9266 | 0.91245 | 0.91812 | 0.93413 | 0.96995 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 52.1 | 63.5 | 61.1 | 57.9 | 71.6 | 69.9 | 101 | 94.4 | 49.7 | 35.2 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1263.7 | 5171 | 29265.5 | 3273.9 | 214.2 | 194.7 | 3682.9 | 7635.3 | 324.2 | -1432.8 | 6530.8 | 900 | 3187.6 | 628.5 | 373.6 | 490 | 242.5 | 88.6 | 50.75 | 28.2 | 46.4 | 1.0755 | 1.0672 | 1.0659 | 1.0281 | 0 | 0 | 129 | 0 | 1862 | 2237.8 | 364.4 | 277.5 | 86.9 | 1.0069 | 1.0063 | 1.0095 | 1.01 | 0.96462 | 0.96057 | 0.9292 | 1.0008 | 1.0009 | 0.98986 | 0.98944 | 0.98873 | 0.98829 | 15 | 11
p18otc364b_brbo_brkp.sav | 8014.2 | 3771.4 | 1107.5 | 1896.8 | 2396.6 | 1831 | 1840 | 880.8 | 372.5 | 766.8 | 766.8 | 96.1 | 156.1 | 79.3 | 25.1 | 25.7 | 1915.9 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2112.6 | -1441.8 | -689.1 | -190.2 | 793.4 | -405.1 | 824.9 | 141.2 | 79.4 | -201 | 484.2 | 469.3 | -30.2 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537.4 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 148.2 | 1381.6 | 3275.4 | 67.6 | 23.1 | 19.5 | 9.3 | 10 | 10 | 0 | 0.9554 | 0.9626 | 0.95794 | 0.79881 | 0.8752 | 0.81504 | 0.83051 | 0.905 | 0.88881 | 0.8673 | 0.87476 | 0.87857 | 0.9082 | 0.96053 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 60 | 73 | 78.5 | 66.1 | 95.8 | 75 | 112.1 | 103.4 | 58.8 | 39.6 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1324 | 5295.9 | 29450.2 | 3283.2 | 220.1 | -364.3 | 3138.9 | 7635.3 | 338.4 | -1430.6 | 6547 | 909 | 3219.6 | 634.9 | 377.4 | 490 | 275.4 | 97.1 | 69.088 | 28.2 | 54.1 | 1.0676 | 1.0575 | 1.0559 | 1.0213 | 0 | 0 | 129 | 0 | 1831 | 2239.7 | 364.4 | 277.5 | 86.9 | 0.96677 | 0.96654 | 0.90223 | 0.85794 | 0.9121 | 0.90157 | 0.95076 | 0.94286 | 0.93685 | 0.94897 | 0.94682 | 0.96128 | 0.97869 | 16 | 12
p18otc364b_brbo_brkp_s.sav | 8004.9 | 3767.6 | 1107.5 | 1896.8 | 2394.8 | 1822.2 | 1840 | 869.9 | 387.1 | 767.3 | 767.3 | 95.9 | 157.8 | 79.8 | 25.1 | 25.7 | 1919 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2127 | 2113.4 | -1433 | -683.1 | -181.3 | 792 | -409.6 | 823.6 | 143.4 | 76.4 | -198.1 | 481.3 | 467.1 | -27.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2537.4 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 147.6 | 1382.2 | 3275.4 | 67.7 | 23.1 | 19.3 | 9.2 | 10 | 10 | 0 | 0.96061 | 0.97228 | 0.96803 | 0.83302 | 0.91506 | 0.83618 | 0.85508 | 0.91566 | 0.91221 | 0.91846 | 0.88712 | 0.89155 | 0.91724 | 0.96629 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 60 | 73.1 | 78.5 | 65.9 | 93.6 | 74.7 | 111.7 | 103.1 | 58.5 | 39.5 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1319.5 | 5295.7 | 29445.6 | 3283.2 | 218.7 | -363.6 | 3138.2 | 7635.3 | 337 | -1429.8 | 6546.4 | 909 | 3219.5 | 634.7 | 377.4 | 490 | 287.5 | 99.6 | 68.085 | 28.2 | 56.6 | 1.0691 | 1.0591 | 1.0573 | 1.0224 | 0 | 0 | 129 | 0 | 1822.2 | 2230 | 364.4 | 277.5 | 86.9 | 0.97649 | 0.97672 | 0.94087 | 0.89701 | 0.93575 | 0.92824 | 0.96196 | 0.96769 | 0.99211 | 0.96238 | 0.96081 | 0.97085 | 0.98456 | 17 | 12
p18otc364b_brgo_brkp.sav | 8010.4 | 3759 | 1107.5 | 1896.8 | 2401.8 | 1817.2 | 1840 | 866.8 | 373.8 | 765.7 | 765.7 | 97.6 | 157.1 | 80.5 | 25.3 | 25.8 | 1917.6 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2126.9 | 2113.1 | -1451.4 | -696.6 | -187.8 | 779.4 | -391.1 | 831.3 | 136 | 77.4 | -199 | 482.1 | 467 | -28.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2537.4 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 163.1 | 1366.6 | 3275.4 | 68.1 | 23.9 | 18.8 | 9.3 | 10 | 10 | 0 | 0.94505 | 0.94423 | 0.93799 | 0.7598 | 0.82957 | 0.7813 | 0.79097 | 0.88544 | 0.83827 | 0.81193 | 0.82365 | 0.82477 | 0.86925 | 0.9391 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 63 | 76.7 | 81 | 76.1 | 122 | 75 | 112.4 | 103.8 | 59.2 | 39.8 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1327.3 | 5302.3 | 29459.9 | 3283.2 | 231 | -374.5 | 3139.5 | 7635.3 | 347 | -1438.4 | 6547.6 | 909.9 | 3221.5 | 635.3 | 377.6 | 490 | 268.7 | 105.1 | 73.489 | 28.2 | 60.9 | 1.0656 | 1.0555 | 1.0544 | 1.0198 | 0 | 0 | 129 | 0 | 1817.2 | 2226 | 364.4 | 277.5 | 86.9 | 0.94832 | 0.94641 | 0.85817 | 0.81321 | 0.87434 | 0.85865 | 0.93021 | 0.88925 | 0.87704 | 0.89352 | 0.88884 | 0.92005 | 0.95686 | 18 | 13
p18otc364b_brgo_brkp_s.sav | 8002.1 | 3760.1 | 1107.5 | 1896.8 | 2400.9 | 1807.9 | 1840 | 854.9 | 389.7 | 766.2 | 766.2 | 97.4 | 159 | 81.2 | 25.3 | 25.8 | 1921 | 330 | 330 | 813.4 | 815 | 2288.4 | 141 | 2126.9 | 2114 | -1440.2 | -688.8 | -177.2 | 778.7 | -396.3 | 833.4 | 139.6 | 74 | -195.7 | 478.8 | 465.3 | -25.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2537.4 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 162.3 | 1367.4 | 3275.4 | 68.2 | 24 | 18.6 | 9.2 | 10 | 10 | 0 | 0.95034 | 0.95399 | 0.94824 | 0.79423 | 0.86986 | 0.80344 | 0.81697 | 0.89722 | 0.86251 | 0.86291 | 0.83806 | 0.83996 | 0.88027 | 0.94697 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 63 | 76.6 | 81 | 75.6 | 120 | 74.8 | 111.9 | 103.4 | 58.8 | 39.7 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1323 | 5304.6 | 29457.9 | 3283.2 | 229.3 | -372.8 | 3139.5 | 7635.3 | 345.3 | -1437.1 | 6547.2 | 909.9 | 3221.1 | 635.3 | 377.5 | 490 | 281.5 | 108.3 | 72.352 | 28.2 | 64.3 | 1.0671 | 1.0572 | 1.0558 | 1.0209 | 0 | 0 | 129 | 0 | 1807.9 | 2215.6 | 364.4 | 277.5 | 86.9 | 0.95812 | 0.95676 | 0.89706 | 0.8527 | 0.89911 | 0.88687 | 0.94259 | 0.91497 | 0.93211 | 0.90916 | 0.90521 | 0.93172 | 0.96488 | 19 | 13
p18otc368b.sav | 8016.1 | 4053.8 | 1107.5 | 1896.8 | 2300 | 1782.4 | 1840 | 829.3 | 367.6 | 740.8 | 740.8 | 91.8 | 149 | 74.6 | 24.6 | 25.1 | 1846.8 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2092.8 | -1102.7 | -423.2 | 193.6 | 1568.3 | -753.8 | 637 | 153.8 | 149.5 | -270.4 | 553.6 | 520.8 | -82.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 131.6 | 1395.1 | 3272.3 | 67.4 | 22.9 | 19.1 | 8.6 | 10 | 10 | 0 | 0.97225 | 0.99082 | 0.98643 | 0.86839 | 0.99955 | 0.87842 | 0.90379 | 0.94376 | 0.93672 | 0.91933 | 0.91731 | 0.92322 | 0.94128 | 0.97936 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 57 | 69.5 | 72.9 | 58.1 | 73.1 | 71 | 103.4 | 96.2 | 51.5 | 30.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1290 | 5377.1 | 29497.8 | 3273.9 | 216.9 | 195.8 | 3686.6 | 7635.3 | 313.4 | -1624.8 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 279.9 | 87.7 | 60.709 | 30 | 45.4 | 1.0753 | 1.0667 | 1.0654 | 1.0279 | 0 | 0 | 129 | 0 | 1782.4 | 2166.3 | 367.6 | 279.9 | 87.7 | 0.99082 | 0.98643 | 0.86839 | 0.99955 | 0.87842 | 0.90379 | 0.94376 | 0.93672 | 0.91933 | 0.91731 | 0.92322 | 0.94128 | 0.97936 | 0 | 0
p18otc368b_amps.sav | 8188.5 | 4122.9 | 1107.5 | 1896.8 | 2298.7 | 1998.4 | 1840 | 1078.4 | 111.7 | 738.9 | 738.9 | 84.3 | 128.4 | 64.3 | 23.5 | 24 | 1802.1 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2081.2 | -1237.1 | -510 | 69.3 | 1599.1 | -721.9 | 611.1 | 127.1 | 194.7 | -315.1 | 598.2 | 549.2 | -115.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 106.2 | 1433.4 | 3272.3 | 62.4 | 16.1 | 26.6 | 9.9 | 10 | 10 | 0 | 0.99405 | 1.0425 | 1.0338 | 0.86839 | 0.99955 | 0.87842 | 0.90379 | 1.0113 | 0.95001 | 0.93369 | 0.90306 | 0.90827 | 0.93107 | 0.98103 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 0 | 30.8 | 37.5 | 0 | 71.1 | 102.5 | 74.4 | 109.8 | 99.7 | 55.1 | 31.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1330.3 | 5336.8 | 29497.8 | 3273.9 | 227.4 | 185.3 | 3686.6 | 7581.2 | 312.4 | -1569.7 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 0 | 111.7 | 79.493 | 30 | 68.4 | 1.0758 | 1.0653 | 1.0632 | 1.0279 | 0 | 0 | 129 | 0 | 1998.4 | 2403.1 | 367.6 | 279.9 | 87.7 | 1.0521 | 1.048 | 1 | 1 | 1 | 1 | 1.0716 | 1.0142 | 1.0156 | 0.98447 | 0.98381 | 0.98915 | 1.0017 | 1 | 1
p18otc368b_amps_s.sav | 8187.4 | 4123.1 | 1107.5 | 1896.8 | 2298.7 | 1997.1 | 1840 | 1076.6 | 113.8 | 738.9 | 738.9 | 84.2 | 128.9 | 64.4 | 23.5 | 24 | 1802.6 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2081.3 | -1235.6 | -509 | 70.7 | 1598.8 | -722.3 | 611.5 | 127.5 | 194.2 | -314.6 | 597.7 | 548.9 | -115.3 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.7 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 106.2 | 1433.3 | 3272.3 | 62.4 | 16.1 | 26.5 | 9.9 | 10 | 10 | 0 | 0.99529 | 1.0448 | 1.0368 | 0.86839 | 0.99955 | 0.87842 | 0.90379 | 1.0116 | 0.96583 | 0.97793 | 0.90998 | 0.91554 | 0.9357 | 0.98352 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 0 | 30.9 | 37.6 | 0 | 71.4 | 101.8 | 74.4 | 109.7 | 99.7 | 55.1 | 31.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1329.9 | 5337.2 | 29497.8 | 3273.9 | 227.3 | 185.4 | 3686.6 | 7581.2 | 312.2 | -1569.5 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 0 | 113.8 | 79.386 | 30 | 70.6 | 1.076 | 1.0655 | 1.0633 | 1.0281 | 0 | 0 | 129 | 0 | 1997.1 | 2401.6 | 367.6 | 279.9 | 87.7 | 1.0545 | 1.0511 | 1 | 1 | 1 | 1 | 1.0719 | 1.0311 | 1.0637 | 0.99201 | 0.99168 | 0.99407 | 1.0042 | 2 | 1
p18otc368b_dsbg.sav | 8071.2 | 4065.3 | 1107.5 | 1896.8 | 2299.5 | 1851.7 | 1840 | 910.6 | 286.9 | 744.1 | 744.1 | 89 | 135.8 | 66.8 | 24.2 | 24.7 | 1828.6 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2088.3 | -1157.1 | -459.9 | 141.9 | 1585 | -740.7 | 623.4 | 139.8 | 168.2 | -288.9 | 572 | 534 | -96.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.4 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 112.3 | 1414.4 | 3272.3 | 65.6 | 20.5 | 21.8 | 9.1 | 10 | 10 | 0 | 0.97531 | 0.99578 | 0.9932 | 0.85142 | 0.93643 | 0.86056 | 0.88325 | 0.93498 | 0.98244 | 0.96864 | 0.95544 | 0.96313 | 0.97347 | 0.98492 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 50.6 | 61.7 | 76.3 | 18.1 | 45.1 | 72.2 | 105.7 | 97.5 | 52.9 | 30.9 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1303.1 | 5364 | 29497.8 | 3273.9 | 221.3 | 191.4 | 3686.6 | 7635.3 | 318.6 | -1629.9 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 286.9 | 0 | 64.3 | 30 | -41.6 | 1.0747 | 1.0654 | 1.0642 | 1.0274 | 0 | 0 | 129 | 0 | 1851.7 | 2243.1 | 367.6 | 279.9 | 87.7 | 1.005 | 1.0069 | 0.98046 | 0.93685 | 0.97967 | 0.97727 | 0.9907 | 1.0488 | 1.0536 | 1.0416 | 1.0432 | 1.0342 | 1.0057 | 3 | 2
p18otc368b_bloxhcb.sav | 8132.5 | 4065.7 | 1107.5 | 1896.8 | 2299.8 | 1644.3 | 1840 | 790.6 | 374 | 729.1 | 729.1 | 91.4 | 147.7 | 74.2 | 24.5 | 25.1 | 1821.1 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2085.4 | -988.9 | -607.3 | 255.6 | 1592.7 | -717.5 | 594.9 | 110.7 | 174.8 | -295.4 | 578.5 | 540.9 | -101 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.5 | 1388.1 | 3272.3 | 68 | 23.7 | 17.9 | 8.8 | 10 | 10 | 0 | 0.96701 | 0.9799 | 0.97546 | 0.83719 | 0.9199 | 0.85111 | 0.87236 | 0.92905 | 0.91708 | 0.89805 | 0.89926 | 0.9043 | 0.92718 | 0.9715 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 59.2 | 72.1 | 76.2 | 62.3 | 83.7 | 73.7 | 135.1 | 0 | 79.2 | 31.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1345.9 | 5321.2 | 29497.8 | 3273.9 | 191.4 | 221.4 | 3686.6 | 7635.3 | 318.4 | -1629.7 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 281.1 | 92.9 | 64.934 | 30 | 50.3 | 1.0742 | 1.0644 | 1.0623 | 1.0271 | 0 | 0 | 129 | 0 | 1644.3 | 2128.4 | 367.6 | 279.9 | 87.7 | 0.98898 | 0.98888 | 0.96407 | 0.92031 | 0.96891 | 0.96522 | 0.98441 | 0.97903 | 0.97685 | 0.98032 | 0.97951 | 0.98502 | 0.99197 | 4 | 3
p18otc368b_bloxhcb_s.sav | 8131 | 4066 | 1107.5 | 1896.8 | 2299.8 | 1642.7 | 1840 | 788.4 | 376.8 | 729 | 729 | 91.3 | 148.3 | 74.4 | 24.5 | 25.1 | 1821.7 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2085.5 | -987 | -605.8 | 257.5 | 1592.3 | -718.1 | 595.5 | 111.4 | 174.3 | -294.8 | 577.9 | 540.5 | -100.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 138.5 | 1388.2 | 3272.3 | 68 | 23.7 | 17.9 | 8.8 | 10 | 10 | 0 | 0.96853 | 0.98271 | 0.97902 | 0.83979 | 0.92292 | 0.85276 | 0.87426 | 0.92996 | 0.93331 | 0.94191 | 0.90646 | 0.91184 | 0.93206 | 0.97417 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 59.1 | 72 | 76.2 | 62.8 | 82.5 | 73.7 | 135 | 0 | 79.2 | 31.1 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1345.3 | 5321.8 | 29497.8 | 3273.9 | 191.2 | 221.5 | 3686.6 | 7635.3 | 318.2 | -1629.4 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 282 | 94.8 | 64.793 | 30 | 52.2 | 1.0745 | 1.0647 | 1.0624 | 1.0272 | 0 | 0 | 129 | 0 | 1642.7 | 2126.5 | 367.6 | 279.9 | 87.7 | 0.99182 | 0.99249 | 0.96706 | 0.92334 | 0.97079 | 0.96733 | 0.98538 | 0.99636 | 1.0246 | 0.98817 | 0.98767 | 0.99021 | 0.9947 | 5 | 3
p18otc368b_blhcoxll.sav | 8443.3 | 4075 | 1107.5 | 1896.8 | 2298.7 | 2068.6 | 1840 | 729.4 | 378.5 | 709.8 | 709.8 | 90.3 | 144.6 | 73 | 24.4 | 24.9 | 1776.8 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2074.1 | -845.9 | -844.3 | 336.4 | 1627.1 | -666 | 536.6 | 51.5 | 218.3 | -338.2 | 621.2 | 570.2 | -130.3 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 151.8 | 1374.9 | 3272.3 | 68.3 | 25 | 16.6 | 7.4 | 10 | 10 | 0 | 0.95982 | 0.96186 | 0.95701 | 0.77806 | 0.85096 | 0.79816 | 0.81078 | 0.90035 | 0.87967 | 0.85733 | 0.86353 | 0.86676 | 0.89939 | 0.95567 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 63.1 | 76.8 | 81.7 | 69.9 | 102.5 | 24.3 | 0 | 0 | 112.5 | 31.6 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1410.8 | 5256.8 | 29497.8 | 3273.9 | 165.8 | 246.9 | 3686.6 | 7635.3 | 330.2 | -1641.4 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 278.2 | 100.3 | 72.831 | 30 | 57 | 1.0756 | 1.0718 | 1.0718 | 1.0288 | 0 | 0 | 129 | 0 | 2068.6 | 2068.6 | 367.6 | 279.9 | 87.7 | 0.97077 | 0.97018 | 0.89598 | 0.85134 | 0.90863 | 0.89709 | 0.954 | 0.9391 | 0.93256 | 0.94137 | 0.93884 | 0.9555 | 0.97581 | 6 | 4
p18otc368b_blhcoxll_s.sav | 8441.5 | 4075.4 | 1107.5 | 1896.8 | 2298.7 | 2066.3 | 1840 | 726.8 | 381.7 | 709.6 | 709.6 | 90.2 | 145.3 | 73.3 | 24.4 | 24.9 | 1777.3 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2074.1 | -843.8 | -842.4 | 338.5 | 1626.6 | -666.7 | 537.5 | 52.4 | 217.8 | -337.7 | 620.7 | 569.9 | -130.1 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 151.7 | 1375.1 | 3272.3 | 68.3 | 25 | 16.6 | 7.4 | 10 | 10 | 0 | 0.9614 | 0.96477 | 0.96067 | 0.78095 | 0.85434 | 0.8 | 0.81294 | 0.90134 | 0.89574 | 0.90009 | 0.87065 | 0.87425 | 0.90417 | 0.95831 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 62.9 | 76.6 | 81.7 | 70.1 | 101.5 | 24.2 | 0 | 0 | 112.4 | 31.6 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1409.9 | 5257.6 | 29497.8 | 3273.9 | 165.7 | 247 | 3686.6 | 7635.3 | 329.9 | -1641.1 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 279.3 | 102.4 | 72.649 | 30 | 59.2 | 1.0759 | 1.072 | 1.072 | 1.029 | 0 | 0 | 129 | 0 | 2066.3 | 2066.3 | 367.6 | 279.9 | 87.7 | 0.97371 | 0.97389 | 0.89931 | 0.85472 | 0.91073 | 0.89948 | 0.95505 | 0.95625 | 0.97907 | 0.94913 | 0.94696 | 0.96057 | 0.97851 | 7 | 4
p18otc368b_mpsl.sav | 7869.2 | 4205.9 | 1107.5 | 1896.8 | 2300.4 | 1655.8 | 1840 | 761.1 | 376.7 | 720.2 | 720.2 | 91.2 | 146.7 | 74.1 | 24.5 | 25.1 | 1802 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2080.2 | -861.1 | 0 | 387.4 | 1640 | -628.7 | 473.8 | -11.9 | 193.6 | -313.8 | 596.9 | 571 | -113.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 146.7 | 1380.1 | 3272.3 | 68.7 | 24.5 | 17.3 | 9 | 10 | 10 | 0 | 0.96097 | 0.96697 | 0.96238 | 0.79903 | 0.87545 | 0.81673 | 0.83248 | 0.90961 | 0.89271 | 0.87155 | 0.87608 | 0.87995 | 0.90884 | 0.96049 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 61.5 | 74.9 | 79.6 | 66.9 | 95.3 | 79.2 | 122.4 | 110.5 | 68.3 | 31.6 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1281.6 | 5385.4 | 29497.8 | 3273.9 | 260.4 | 152.3 | 3686.6 | 7635.3 | 323.8 | -1635.1 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 279.2 | 97.5 | 69.868 | 30 | 54.5 | 1.0736 | 1.0634 | 1.0617 | 1.0265 | 0 | 0 | 129 | 0 | 1655.8 | 2100.7 | 367.6 | 279.9 | 87.7 | 0.97593 | 0.97562 | 0.92013 | 0.87584 | 0.92977 | 0.9211 | 0.96381 | 0.95302 | 0.94803 | 0.95505 | 0.95313 | 0.96554 | 0.98073 | 8 | 5
p18otc368b_mpsl_s.sav | 7868.2 | 4205.7 | 1107.5 | 1896.8 | 2300.5 | 1654.2 | 1840 | 758.8 | 379.8 | 720.1 | 720.1 | 91.2 | 147.4 | 74.3 | 24.5 | 25.1 | 1802.6 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2080.3 | -859.8 | 0 | 388.8 | 1639.3 | -629.9 | 475.3 | -10.4 | 192.9 | -313.2 | 596.3 | 570.5 | -113.5 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 146.5 | 1380.2 | 3272.3 | 68.7 | 24.4 | 17.3 | 9 | 10 | 10 | 0 | 0.96261 | 0.96998 | 0.96615 | 0.80211 | 0.87905 | 0.81876 | 0.83484 | 0.91068 | 0.90906 | 0.91495 | 0.8834 | 0.88765 | 0.91379 | 0.96321 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 31.7 | 61.3 | 74.7 | 79.6 | 67.2 | 94.1 | 79.2 | 122.3 | 110.3 | 68.2 | 31.6 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1281 | 5386 | 29497.8 | 3273.9 | 260 | 152.7 | 3686.6 | 7635.3 | 323.4 | -1634.6 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 280.2 | 99.6 | 69.667 | 30 | 56.6 | 1.0738 | 1.0637 | 1.062 | 1.0267 | 0 | 0 | 129 | 0 | 1654.2 | 2098.7 | 367.6 | 279.9 | 87.7 | 0.97897 | 0.97944 | 0.92368 | 0.87945 | 0.93208 | 0.92371 | 0.96495 | 0.97047 | 0.99524 | 0.96303 | 0.96147 | 0.97079 | 0.98351 | 9 | 5
p18otc368b_angr1.sav | 8028.9 | 4050.6 | 1107.5 | 1896.8 | 2299.8 | 1798.8 | 1840 | 855.3 | 339.2 | 724.8 | 724.8 | 95.2 | 166.4 | 83.1 | 25.2 | 25.7 | 1845.2 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2091.5 | -1121.7 | -436.8 | 175.3 | 1571.4 | -749.2 | 630.7 | 147.3 | 150.1 | -270.9 | 554 | 522.3 | -82.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133.6 | 1393.2 | 3272.3 | 70.1 | 25.4 | 16.2 | 8.6 | 10 | 10 | 0 | 0.95923 | 0.95208 | 0.94895 | 0.85965 | 0.98896 | 0.8832 | 0.90928 | 0.94761 | 0.91064 | 0.89106 | 0.91311 | 0.91881 | 0.93966 | 0.978 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 120.2 | 69.3 | 53.6 | 67 | 71.3 | 104.1 | 96.6 | 52 | 30.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1299.3 | 5367.7 | 29497.8 | 3273.9 | 217.7 | 195 | 3686.6 | 7635.3 | 312.2 | -1623.5 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 261.5 | 77.7 | 57.925 | 30 | 35.6 | 1.0748 | 1.066 | 1.0649 | 1.0276 | 0 | 0 | 129 | 0 | 1798.8 | 2184.9 | 367.6 | 279.9 | 87.7 | 0.9609 | 0.962 | 0.98994 | 0.9894 | 1.0054 | 1.0061 | 1.0041 | 0.97216 | 0.96925 | 0.99542 | 0.99522 | 0.99828 | 0.99861 | 10 | 6
p18otc368b_angr2.sav | 8028.4 | 4053.6 | 1107.5 | 1896.8 | 2299.8 | 1798 | 1840 | 849.8 | 345.2 | 726.5 | 726.5 | 94.7 | 164.8 | 82.1 | 25.1 | 25.6 | 1845.4 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2091.6 | -1117.8 | -433.8 | 179.2 | 1570.7 | -750.4 | 632.3 | 149 | 150.1 | -270.9 | 554 | 522 | -83 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 133.1 | 1393.8 | 3272.3 | 69.7 | 25.1 | 16.6 | 8.6 | 10 | 10 | 0 | 0.9622 | 0.96228 | 0.95855 | 0.8645 | 0.99484 | 0.8845 | 0.91076 | 0.948 | 0.91805 | 0.8991 | 0.91533 | 0.92114 | 0.94101 | 0.97886 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 92.8 | 0 | 69.8 | 54.1 | 67.6 | 71.3 | 104 | 96.5 | 51.9 | 30.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1294.8 | 5372.2 | 29497.8 | 3273.9 | 217.6 | 195.1 | 3686.6 | 7635.3 | 312.3 | -1623.7 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 265.6 | 79.6 | 58.208 | 30 | 37.5 | 1.0748 | 1.066 | 1.0649 | 1.0276 | 0 | 0 | 129 | 0 | 1798 | 2183.7 | 367.6 | 279.9 | 87.7 | 0.9712 | 0.97174 | 0.99552 | 0.99529 | 1.0069 | 1.0077 | 1.0045 | 0.98007 | 0.97799 | 0.99784 | 0.99775 | 0.99971 | 0.99949 | 11 | 7
p18otc368b_angr12.sav | 8111.1 | 4016.9 | 1107.5 | 1896.8 | 2299.1 | 1904.9 | 1840 | 979.9 | 148.5 | 673.9 | 673.9 | 111 | 208.9 | 104.6 | 28.1 | 28.7 | 1829.2 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2089.5 | -1255.7 | -532.8 | 46.4 | 1591.3 | -715.1 | 584.8 | 100.4 | 156.6 | -276.6 | 559.6 | 530.6 | -82.8 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1732.2 | 207.1 | 1333.9 | 3272.3 | 77.3 | 40.9 | 6.3 | 10.5 | 10 | 10 | 0 | 0.8217 | 0.66755 | 0.65942 | 0.7467 | 0.85115 | 0.85781 | 0.88008 | 0.93902 | 0.66833 | 0.62211 | 0.83548 | 0.83724 | 0.89049 | 0.94614 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 0 | 0 | 51 | 32 | 84.1 | 73.7 | 108.8 | 99.5 | 55.1 | 30.9 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1318.3 | 5348.7 | 29497.8 | 3273.9 | 226.6 | 186.1 | 3686.6 | 7635.3 | 313.7 | -1625 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 133.2 | 15.3 | 41.553 | 30 | -27.4 | 1.0702 | 1.0603 | 1.0606 | 1.0245 | 0 | 0 | 129 | 0 | 1904.9 | 2305.6 | 367.6 | 279.9 | 87.7 | 0.67373 | 0.66849 | 0.85987 | 0.85153 | 0.97654 | 0.97377 | 0.99498 | 0.71348 | 0.6767 | 0.91079 | 0.90687 | 0.94604 | 0.96608 | 12 | 8
p18otc368b_grgr.sav | 8057.9 | 4039.9 | 1107.5 | 1896.8 | 2299.9 | 1837.8 | 1840 | 897.9 | 269.8 | 654 | 654 | 149 | 209.5 | 103.5 | 33.2 | 33.9 | 1837 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2086.7 | -1167.6 | -469.4 | 131.2 | 1579.9 | -737.7 | 615.7 | 132 | 154.8 | -275.2 | 558.3 | 527 | -85.3 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -97.2 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 156 | 1371.3 | 3272.3 | 83.6 | 57.6 | 7.9 | 13.2 | 10 | 10 | 0 | 0.86706 | 0.87234 | 0.86663 | 0.84786 | 0.97465 | 0.89693 | 0.925 | 0.9571 | 0.85135 | 0.82632 | 0.90348 | 0.90872 | 0.93584 | 0.97437 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 33.1 | 40.3 | 60.4 | 41.2 | 56.4 | 72.1 | 105.7 | 97.6 | 53 | 30.8 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1305.5 | 5361.8 | 29497.8 | 3273.9 | 220.2 | 192.5 | 3686.6 | 7635.3 | 310.6 | -1621.9 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 217.4 | 52.3 | 50.113 | 30 | 10.5 | 1.0744 | 1.0649 | 1.064 | 1.0277 | 0 | 0 | 129 | 0 | 1837.8 | 2229.3 | 367.6 | 279.9 | 87.7 | 0.88042 | 0.87855 | 0.97636 | 0.97509 | 1.0211 | 1.0235 | 1.0141 | 0.90886 | 0.89883 | 0.98492 | 0.98429 | 0.99422 | 0.99491 | 13 | 9
p18otc368b_anpf.sav | 8179.4 | 4073.3 | 1107.5 | 1896.8 | 2298.7 | 1989.8 | 1840 | 1072.1 | 100 | 737.2 | 737.2 | 84.2 | 128.4 | 64.3 | 23.5 | 24 | 1798.6 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2080.2 | -1279.5 | -543.8 | 27 | 1608.5 | -708 | 592.9 | 108.4 | 198.1 | -318.4 | 601.5 | 554.6 | -118 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.6 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 107.6 | 1418.9 | 3272.3 | 62.5 | 16.2 | 26.4 | 9.9 | 10 | 10 | 0 | 0.99382 | 1.042 | 1.0332 | 1.1212 | 1.0205 | 1.0865 | 1.1389 | 1.0464 | 0.94747 | 0.93095 | 0.90215 | 0.90733 | 0.93158 | 0.98364 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 31 | 37.8 | 0 | 72.3 | 105.6 | 74.8 | 110.7 | 100.4 | 55.9 | 31.2 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1329.7 | 5337.4 | 29497.8 | 3273.9 | 230.9 | 181.9 | 3686.6 | 7635.3 | 314 | -1625.3 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | -13.3 | 113.3 | 82.771 | 30 | 69.9 | 1.0758 | 1.0652 | 1.0631 | 1.028 | 0 | 0 | 129 | 0 | 1989.8 | 2397.3 | 367.6 | 279.9 | 87.7 | 1.0517 | 1.0474 | 1.2911 | 1.021 | 1.2369 | 1.2602 | 1.1088 | 1.0115 | 1.0126 | 0.98347 | 0.98279 | 0.98969 | 1.0044 | 14 | 10
p18otc368b_antbdy.sav | 8040.3 | 4053.5 | 1107.5 | 1896.8 | 2299.7 | 1813.3 | 1840 | 865.5 | 332.9 | 740.7 | 740.7 | 90.7 | 145.9 | 73.1 | 24.4 | 25 | 1840.4 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2091.1 | -1132.7 | -444.1 | 165.6 | 1570 | -743.5 | 630.3 | 146.8 | 156.1 | -276.9 | 560.1 | 524.7 | -87.6 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.3 | 151 | 39 | 59 | 2539.3 | 192 | 66 | 258 | 12 | 40 | 50 | 26 | 14 | 46 | 42 | 38 | 6 | 274 | 1745.2 | 123.6 | 1403.1 | 3272.3 | 66.6 | 21.9 | 20.2 | 8.8 | 10 | 10 | 0 | 0.97537 | 0.9979 | 0.99292 | 0.87512 | 1.0077 | 0.83959 | 0.85902 | 0.86579 | 0.93736 | 0.92002 | 0.90667 | 0.91206 | 0.92924 | 0.96643 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 53.1 | 64.7 | 62.8 | 59.1 | 73.9 | 71.6 | 104.6 | 96.8 | 52.2 | 30.9 | 560 | 560 | 345 | 300 | 1765 | 22788.6 | 1295.2 | 5371.8 | 29497.8 | 3273.9 | 218.1 | 194.6 | 3686.6 | 7635.3 | 322.8 | -1634.2 | 6328 | 1100 | 3219.9 | 632.3 | 370.8 | 290 | 243.3 | 89.5 | 53.035 | 30 | 47.3 | 1.0754 | 1.0665 | 1.0651 | 1.0279 | 0 | 0 | 129 | 0 | 1813.3 | 2201 | 367.6 | 279.9 | 87.7 | 1.0071 | 1.0066 | 1.0077 | 1.0082 | 0.9558 | 0.95046 | 0.91738 | 1.0007 | 1.0008 | 0.9884 | 0.98791 | 0.98721 | 0.9868 | 15 | 11
p18otc368b_brbo_brkp.sav | 8145.1 | 3845.3 | 1107.5 | 1896.8 | 2396.6 | 1780 | 1840 | 841.5 | 371.6 | 750.9 | 750.9 | 94.6 | 152.9 | 77.8 | 24.9 | 25.4 | 1877.5 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2102.3 | -1527.1 | -744.7 | -258.3 | 774 | -454.7 | 752 | 73 | 119.5 | -240.7 | 523.9 | 475.3 | -60.7 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2539.3 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 150.7 | 1380.9 | 3277.3 | 68.1 | 23.7 | 18.6 | 9.4 | 10 | 10 | 0 | 0.95235 | 0.95648 | 0.95196 | 0.77751 | 0.85031 | 0.79592 | 0.80815 | 0.8948 | 0.88057 | 0.85832 | 0.8688 | 0.8723 | 0.90385 | 0.9583 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 61.2 | 74.5 | 80.5 | 67.4 | 98.7 | 76.6 | 115.8 | 106.1 | 61.5 | 35.2 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1360.8 | 5494.1 | 29685.2 | 3283.2 | 226.7 | -367.1 | 3142.7 | 7635.3 | 333.5 | -1625.6 | 6347 | 1111 | 3252.5 | 638.6 | 374.5 | 292.9 | 274 | 97.7 | 71.974 | 30 | 54.5 | 1.067 | 1.0558 | 1.0538 | 1.0207 | 0 | 0 | 129 | 0 | 1780 | 2199.5 | 367.6 | 279.9 | 87.7 | 0.96534 | 0.96506 | 0.89535 | 0.85069 | 0.90608 | 0.89418 | 0.94812 | 0.94006 | 0.93364 | 0.94712 | 0.94485 | 0.96023 | 0.9785 | 16 | 12
p18otc368b_brbo_brkp_s.sav | 8135.6 | 3841.4 | 1107.5 | 1896.8 | 2394.7 | 1771.1 | 1840 | 830.4 | 386.5 | 751.5 | 751.5 | 94.4 | 154.6 | 78.3 | 24.9 | 25.4 | 1880.6 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2103.2 | -1518 | -738.6 | -249.4 | 772.6 | -459.4 | 750.7 | 75.4 | 116.5 | -237.7 | 520.9 | 473.1 | -58.3 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98.1 | 151 | 39 | 59 | 2539.3 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 150 | 1381.6 | 3277.3 | 68.2 | 23.8 | 18.4 | 9.3 | 10 | 10 | 0 | 0.95754 | 0.96608 | 0.96199 | 0.8114 | 0.88988 | 0.81692 | 0.8327 | 0.90536 | 0.90396 | 0.90927 | 0.8812 | 0.88534 | 0.91292 | 0.96407 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 61.2 | 74.5 | 80.4 | 67.2 | 96.4 | 76.4 | 115.3 | 105.7 | 61.2 | 35.1 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1356 | 5494 | 29680.2 | 3283.2 | 225.2 | -366.3 | 3142 | 7635.3 | 332.1 | -1624.8 | 6346.4 | 1111 | 3252.1 | 638.5 | 374.5 | 292.9 | 286.4 | 100.1 | 70.923 | 30 | 57.1 | 1.0685 | 1.0574 | 1.0553 | 1.0218 | 0 | 0 | 129 | 0 | 1771.1 | 2189.6 | 367.6 | 279.9 | 87.7 | 0.97503 | 0.97522 | 0.93437 | 0.89028 | 0.92999 | 0.92134 | 0.95931 | 0.96503 | 0.98906 | 0.96064 | 0.95897 | 0.96987 | 0.98439 | 17 | 12
p18otc368b_brgo_brkp.sav | 8144.1 | 3833.9 | 1107.5 | 1896.8 | 2402.3 | 1768.5 | 1840 | 830.1 | 369.9 | 749.7 | 749.7 | 96 | 153.8 | 78.9 | 25 | 25.6 | 1878.8 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2102.7 | -1538.3 | -753.4 | -257.7 | 758.5 | -437.9 | 758.4 | 67.1 | 117.9 | -239 | 522.2 | 472.9 | -59.4 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98 | 151 | 39 | 59 | 2539.3 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 165.6 | 1366.1 | 3277.3 | 68.6 | 24.5 | 17.9 | 9.4 | 10 | 10 | 0 | 0.94163 | 0.93751 | 0.93135 | 0.73625 | 0.8019 | 0.75964 | 0.76533 | 0.87334 | 0.82818 | 0.80081 | 0.81428 | 0.81488 | 0.86149 | 0.93325 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 12 | 31.7 | 64.1 | 78 | 82.9 | 77.2 | 124.1 | 76.8 | 116.1 | 106.5 | 61.9 | 35.4 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1365.5 | 5500.1 | 29695.8 | 3283.2 | 237.3 | -377.1 | 3143.3 | 7635.3 | 342.3 | -1633.6 | 6347.8 | 1112.1 | 3254.2 | 639.1 | 374.7 | 293.1 | 265.3 | 104.6 | 76.561 | 30 | 60.3 | 1.0649 | 1.0536 | 1.0521 | 1.0191 | 0 | 0 | 129 | 0 | 1768.5 | 2188.3 | 367.6 | 279.9 | 87.7 | 0.9462 | 0.94416 | 0.84783 | 0.80226 | 0.86478 | 0.8468 | 0.92538 | 0.88413 | 0.87108 | 0.88768 | 0.88265 | 0.91523 | 0.95292 | 18 | 13
p18otc368b_brgo_brkp_s.sav | 8135.5 | 3834.9 | 1107.5 | 1896.8 | 2401 | 1759.1 | 1840 | 818.1 | 386.3 | 750.3 | 750.3 | 95.8 | 155.6 | 79.5 | 25 | 25.6 | 1882.3 | 330 | 330 | 815.3 | 815 | 2290.3 | 141 | 2128.9 | 2103.7 | -1527.2 | -745.6 | -247.3 | 757.8 | -443.5 | 760.2 | 70.9 | 114.5 | -235.7 | 518.9 | 471.1 | -56.9 | 288 | 605 | 562 | 410 | 263 | 78 | 332 | -98 | 151 | 39 | 59 | 2539.3 | 192 | 66.7 | 258.7 | 12.1 | 40.4 | 50.5 | 26.3 | 14.1 | 46.5 | 42.4 | 38.4 | 6.1 | 276.8 | 1745.2 | 164.7 | 1367.2 | 3277.3 | 68.7 | 24.6 | 17.7 | 9.3 | 10 | 10 | 0 | 0.94689 | 0.94719 | 0.94152 | 0.77037 | 0.84195 | 0.78176 | 0.79149 | 0.88519 | 0.85248 | 0.85162 | 0.829 | 0.83041 | 0.87283 | 0.94145 | 37.7 | 20 | 0 | 44.3 | -372 | 0 | 0 | 24 | 63.4 | 64 | 78 | 82.8 | 76.7 | 122.1 | 76.5 | 115.6 | 106.1 | 61.6 | 35.3 | 0 | 560 | 345 | 300 | 1205 | 22788.6 | 1360.8 | 5502.8 | 29693.8 | 3283.2 | 235.4 | -375.3 | 3143.3 | 7635.3 | 340.5 | -1632.4 | 6347.5 | 1112.1 | 3253.8 | 639.1 | 374.7 | 293.1 | 278.4 | 107.9 | 75.373 | 30 | 63.6 | 1.0663 | 1.0553 | 1.0536 | 1.0202 | 0 | 0 | 129 | 0 | 1759.1 | 2177.8 | 367.6 | 279.9 | 87.7 | 0.95597 | 0.95447 | 0.88712 | 0.84233 | 0.88996 | 0.87574 | 0.93794 | 0.91007 | 0.92635 | 0.90373 | 0.89947 | 0.92728 | 0.96129 | 19 | 13