2016 RFP

Attachment 20: PacifiCorp High Level Cost Estimates Associated With Integration

Draft (1-31-2012)

Preliminary Assessment of Transmission Impacts Associated with

RFP Points of Delivery

- Overview of Points of Delivery

PacifiCorp is interested in resources that are capable of delivery into or in a portion of the Company’s network transmission system in the eastern balancing area.  Specifically, the point(s) of delivery of primary interest to PacifiCorp are:

East system Points of Delivery

- Borah/Kinport 345 kV

- Populus 345 kV

- Salt Lake Valley

  - Connected to a major 138 kV or 345 kV substation in the Wasatch Front load area south of the Ben Lomond substation and north of the Camp Williams substation.

- PacifiCorp Site

  - Currant Creek (POR is Mona 345 kV)

- Mona 345 kV

- Glen Canyon 230 kV

- Nevada/Utah Border:

  - Gonder-Pavant 230 kV line known as “Gonder 230 kV”

  - Red Butte – Harry Allen 345 line known as “NUB” or Red Butte 345 kV

- Crystal 500 kV

Although the Company will consider resources delivered to the following areas, these areas have been identified as having potential transmission constraint implications and as such, will need to be evaluated accordingly:

- Wyoming.  Resources in Wyoming may be useful in supporting the increased load and wind resources in Wyoming; however, such resources may be negatively affected by transmission constraints prior to the addition of Energy Gateway.

- All points of receipt that require new transmission line construction will require 4-7 years and in some scenarios even longer in order to allow time for environmental work, route selection, permitting, and construction.  Resources located at these POR’s may require cost adjustment for some period of time to accommodate re-dispatch of existing resources or other means of managing transmission congestion in the interim period between completion of plant construction and before new transmission is commissioned.

Cost estimates provided in the document are conceptual (plus or minus 50%) un-scoped, may vary considerably depending on location and are provided for informational purposes.  System impact studies completed for actual generation interconnection request may identify new constraints and impacts that significantly change the cost and schedule estimates provided here.  Cost estimates and schedules provided in this document do not represent any firm offer of service.

PacifiCorp is willing to consider purchasing capacity and associated energy that is sourced from Desert Southwest (Nevada, California, Arizona, New Mexico); provided, the selling entity is able to purchase firm transmission from the resource to either Gonder or Nevada Utah Border (NUB).

West System Points of Delivery

- Mid Columbia – Yakima Area

  - Midway 230 kV

  - Wanapum 230 kV

- California Oregon Border

- Portland

  - Troutdale 230 kV

- Willamette Valley

  - Alvey 500 kV

  - Alvey 230 kV

  - Fry 230 kV

- Southern Oregon

  - Chiloquin230 kV

  - Dixonville 230 kV

  - Meridian 230 kV

  - Reston 230 kV

- Central Oregon

  - Bend 69 kV

  - Pilot Butte 69/230 kV

  - Ponderosa 230 kV

  - Redmond 69 kV

- Oregon Coast

  - Astoria to Tillamook 115 kV – 75 MW

  - Boyer (Lincoln City) 115 kV – 75 MW

- Within the Western Control Area – The point of interconnection is the point between the resource, or the electrical system to which the resource is connected, and PacifiCorp’s transmission system.

- Scheduled to the point(s) of interconnection between PacifiCorp’s western control area and the Bonneville Power Administration or Portland General Electric such that transfer limitations are not exceeded.  If the resource is located within the Bonneville control area the Bidder must show they have control area service from the resource to the delivery point.

- All points of receipt that require transmission line construction will require 4-7 years and in some scenarios even longer in order to allow time for environmental work, route selection, permitting, and construction.  Resources located at one of these POR’s may require cost adjustment for some period of time to accommodate re-dispatch (if possible) of existing resources or other means of managing transmission congestion in the interim period between completion of plant construction and before new transmission is commissioned.

- Transmission Assumptions Associated with the Points of Delivery

PacifiCorp may need to increase transmission import capability and upgrade its network system capacity in order to integrate a resource delivered to the preferred points of delivery. The table below indicates the possible additions necessary and indicative proxy cost associated with the upgrade.  These proxy costs are based on very high-level assessments done by the PacifiCorp Transmission group for current and past Integrated Resource Plan, as well as extrapolation from System Impact Studies.

These cost estimates are indicative but will be used for evaluating bids and may be refined if better estimates are received prior to issuance of the RFP.

| East System |  |  |  |  |
| --- | --- | --- | --- | --- |
| Point of Delivery | Description of Possible Transmission Additions/Upgrades | Path(s) to Upgrade and Voltage Support | Estimated Cost of Upgrades1 | Transmission In Service (estimate)2 |
| Populus 345 kV, 600 MW | Substation connection. Delivery requires use of existing firm network allocation rights across Path C. | Requires additions at the Populus substation to connect the new resource | $30 M | 2014 |
| Kinport/Borah 345 kV, 600 MW | Delivery requires use of existing firm network allocation rights across Path C. | Requires additions at the Populus substation to connect the new resource | $30 M | 2014 |
| Salt Lake Valley 138 kV, 600 MW | Upgrades to existing lines. | Unknown locations | $108 M | 2016 |
| Mona/Currant Creek 345 kV, 600 MW3 | Substation upgrades | Clover to PACE4 | $67 M | 2013 |
| Gonder 345 kV, 600 MW | Series compensation or other improvement north of Sigurd/Huntington cut plane. Transmission line(s), substation | Gonder/Nevada Border to Sigurd, North of Sigurd/Huntington cut plane and Clover to PACE4. | $336 M | 2018 |

1The costs are shown in current year (2011) up-front dollars. Costs are conceptual +/- 50%.

2Dates reflect Dec. 31 of the stated in service year unless otherwise stated.

3Currant Creek is a resource location; POD is Mona.

4 Required completion of the Clover to Oquirrh transmission line currently under construction, not included in costs.

| East System |  |  |  |  |
| --- | --- | --- | --- | --- |
| Harry Allen 345 kV (NUB) 449 MW Summer, 524 MW Winter | Series compensation or other improvement north of Sigurd/Huntington cut plane. Requires delivery to NV Energy’s interconnection with PacifiCorp | Sigurd/Huntington north and Clover to PACE.4 | $76 M | 20155 |
| Crystal 500 kV, 600 MW | Transmission line(s), substation, transformer, phase shifter. | Crystal to RButte+RButte to Sigurd6+Clover to PACE4 | $549 M | 2020 |
| NUB Glen Canyon 345 kV, 600 MW | Series compensation or other improvement north of Sigurd/Huntington cut plane. Transmission line(s), substation, phase shifter | Glen Canyon to Sigurd, North of Sigurd/Huntington cut plane, and Clover to PACE4 | $382 M | 2019 |
| Four Comers 345 kV, 600 MW | Series compensation or other improvement north of Sigurd/Huntington cut plane. New line(s), substation, phase shifter | F.Corners to Clover + Clover to PACE4 | $798 M | 2019 |
| Eastern Wyoming 400 MW | Energy Gateway facilities7 |  | $20 to 173 M8 | 2018 |
| Southwest Wyoming 400 MW | Transmission line, substation connection | Evanston West Path; Southwest Wyoming to northern Utah | $70 M | 2018 |

5Installation of series compensation or other improvements completed three years after notification of need.

6Sigurd to Red Butte #2 required for load service and excluded from costs for this resource.

7 Gateway transmission projects required for load service and excluded from costs for this resource.

8 Cost will vary depending on location of resource.

| West System |  |  |  |  |
| --- | --- | --- | --- | --- |
| Description of Possible Transmission Additions/Upgrades | Path(s) to Upgrade and Voltage Support | Estimated Cost of Upgrades1 | Transmission In Service (estimate)2 | Description of Possible Transmission Additions/Upgrades |
| Mid Columbia, 600 MW | Delivered load to Yakima Pod, delivered through Vantage and Wanapum | A new resource requires new substation and substation upgrades for interconnection + Vantage to Pomona9. Any resource above needed area load will require contracts with other transmission providers. | $30 M | 2013 |
| California Oregon Border, 600 MW | Delivered to southern Oregon load via Malin 230 kV – 200 MW delivered to Southern Oregon and up to 400 MW delivered to the Willamette Valley through a new or double circuit 230 upgrade through Alvey | New 500/230 kV substion10, 230 kV line Alvey to Dixonville, additions at Alvey and Dixonville with possible connection to Fry. | $314 M | 2018 |
| Portland Troutdale, 400 MW | Transmission line, substation additions | 230 kV line Gresham to Bethel + Bethel to Fry11, substation additions at Troutdale, Gresham, Bethel and Fry | $216 M | 2018 |
| Willamette Valley at Alvey substation 400 MW | Substation additions | Interconnection upgrades at Alvey substation | $10 M | 2013 |

9Vantage to Pomona project required for reliability and load service, and excluded for the cost for this resource.

10  New substation planned near Klamath Falls and Grants Pass for load service and excluded from the cost for this resource.

11 Bethel to Fry required for load service and excluded from the cost for this resource.

| West System |  |  |  |  |
| --- | --- | --- | --- | --- |
| Willamette Valley-Alvey 230 kV south of Alvey substation, 400 MW | Transmission line, substation additions | 230 kV line Alvey to Dixonville substations, additions at Alvey and Dixonville. | $314 M | 2018 |
| Chiloquin southern Oregon 400 MW | Transmission line, substation additions | 230 kV line Chiloquin to Klamath substation, additions at Chiloquin and Klamath substations. 500/230 kV substation near Klamath Falls10 | $108 M | 2017 |
| Southern Oregon, 588 Mw | Integrate existing interconnected third party resource | N/A | N/A | N/A |
| Southern Oregon, 600 MW | Substations | New 500/230 kV substation between Meridian and Grants Pass or Klamath Falls. | $55 M | 2015 |