** DRAFT REVISION (R4) **

Gateway Project Development

Southern Utah Transfer Capability (r4)

Prepared for:

Prepared by:

Electrical Consultants, Inc.

June 2008

Table of Contents

1.0	Executive Summary	1

2.0	Background	3

3.0	Study Assumptions	6

4.0	Study Procedures	7

5.0	Study Case Development and Results	11

5.1	North to South (N-S) Transfer	11

5.2	South to North (S-N) Transfer	14

6.0	Results Summary	18

6.1	North to South (N-S) Cases	18

6.2	South to North (S-N) Cases	19

7.0	Gateway Project Elements	20

7.1	North to South (N-S) Cases	22

7.2	South to North (S-N) Cases	23

8.0	Conclusions	24

9.0	Appendix	26

# Executive Summary

This report summarizes the studies performed to determine the transfer capability of the Southern Utah transmission system, and the transmission reinforcements necessary to increase the transfer capability.  For the purpose of this analysis, the existing Southern Utah transfer paths are defined as TOT2B and TOT2C.  The definition and ratings of these paths are described later in this document.

The system was studied with the TOT2B paths operating at their maximum transfer capability.  Transmission system reinforcements were then added to increase the transfer capability of the TOT2C path.  The studies included powerflow and contingency analysis only; no dynamic stability analysis was performed for this analysis.

The reinforcements necessary to obtain increased N-S TOT2C path ratings are listed in Table 1.1, below.

| N-S Path Rating | Description of Reinforcements |
| --- | --- |
| 0 MW | Existing N-S Capability Confirmed (with 2009 loads) |
| 370 MW | Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR + 150 / - 50 MVAR Red Butte SVC + 150 / - 50 MVAR |
| 600 MW | Harry Allen #2 230/345 kV transformer Increase Three Peak DVAR to +250 / -100 MVAR Increase Red Butte SVC to +250 / -100 MVAR |
| 700 MW | Harry Allen 345 kV Phase Shifter #3 |
| 900 MW | Crystal 500 kV 750 MVA Phase Shifters (2) Red Butte - Crystal #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer |
| 2100 MW | Sigurd - Red Butte #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Mona - Sigurd #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| Table 1.1 - North to South (N-S) Reinforcements |

The N-S path rating could be increased beyond the 700 MW level, to an intermediate level of 1100 MW, by construction of a third 345 kV line from Mona to Sigurd to Red Butte.  This 235-mile transmission line is not required to obtain the ultimate 2100 N-S path rating shown in Table 1.1.

The reinforcements necessary to obtain increased S-N TOT2C path ratings are listed in Table 1.2, below.

| S-N Path Rating | Description of Reinforcements |
| --- | --- |
| 351 MW | Existing S-N Capability Confirmed |
| 600 MW | Harry Allen #2 230/345 kV transformer Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR +100 / - 50 MVAR Red Butte SVC +100 /- 100 MVAR |
| 1300 MW | Crystal 500 kV Phase Shifters (2) Crystal - Red Butte #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Huntington #2 Unit Generator Tripping RAS Increase Three Peak DVAR to +250 / - 100 MVAR Increase Red Butte SVC to +250 /- 100 MVAR |
| 1500 MW | Red Butte - Sigurd #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Sigurd -Mona #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| 1700 MW | Huntington #2 Unit Generator Tripping RAS |
| Table 1.2 - South to North (S-N) Reinforcements |

Detailed data for the reinforcements listed in the above tables can be found later in this report.

This analysis was limited to the area from Mona to the south.  Reinforcements north of Mona that would be necessary to support these transfer levels were not evaluated.

# Background

As part of the Gateway Project development, PacifiCorp desires to understand and quantify the transfer capability of the Southern Utah transmission system.  For the purpose of this analysis, the existing Southern Utah transfer paths are defined as TOT2B and TOT2C.  The existing definition and accepted ratings of these paths are as follows:

| Path | Description | Rating (see note) |
| --- | --- | --- |
|  |  | North-South | South-North |
| TOT2B | Southern Utah to Northern Arizona/West New Mexico |
| TOT2B1 | Pinto-Four Corners 345 kV line flow - measured at Four Corners | 560 MW | 600 MW |
| TOT2B2 | Sigurd-Glen Canyon 230 kV line flow - measured at Glen Canyon | 265 MW | 300 MW |
| TOT2C | Southwestern Utah to Southeast Nevada |
|  | Red Butte-Harry Allen 345 kV line flow - measured at Harry Allen 500 kV | 300 MW | 300 MW |
| Table 2.1 - Southern Utah Path Designations and Existing Ratings Note: non-simultaneous rating with simultaneous interaction defined by a nomogram |

If additional transmission components are added in Southern Utah, the ratings of the paths in Table 2.1 would change.  For example, the addition of new transmission from the Red Butte area to the Harry Allen area would add capacity to the TOT2C path.  Reinforcements that are considered for this study are listed in Section 7.

Figures 2.1 and 2.2, on the following page show geographically the existing transmission facilities that make up the TOT2B paths.

Figure 2.1 - TOT2B1 Transmission Diagram

Figure 2.2 - TOT2B2 Transmission Diagram

Figure 2.3, below shows geographically the existing transmission facilities that make up the TOTC path.

Figure 2.3 - TOT2C Transmission Diagram

# Study Assumptions

The following key assumptions were used in performing this study.

- The study was performed using a WECC 2015 Heavy Summer base case.

- All studies were performed using PSS/E™ version 30.3.2.

- Studies were performed with TOT2B (TOT2B1 and TOT2B2) path flows at their current maximum rated levels.

- Southern Utah path scheduling was performed by adjusting the levels of load in Utah and in Arizona and modifying the area interchange in area 14 and area 65.  Phase shifters at Pinto, Sigurd, Harry Allen, and Crystal (future) were adjusted to accommodate the desired flows.

- Elements of the Gateway Project were modeled according to existing plans.  It is possible that these elements might change during the planning process.

- Cases were screened with the PacifiCorp-developed contingency processor for steady-state (N-0) and contingency (N-1 and N-2) conditions, including bus voltages and branch and equipment loading.

- Results were developed for both North to South flows (N-S) and South to North flows (S-N).  The results were presented separately to facilitate the independent rating of the path for each flow direction.

# Study Procedures

All study cases were performed with the TOT2B paths at their maximum rated flow.  For N-S cases, this results in TOT2B1 (Pinto - Four Corners) flows of 560 MW and TOT2B2 (Sigurd - Glen Canyon) flows of 265 MW.  For S-N cases, the flows are -600 MW for TOT2B1 and -300 MW for TOT2B2.  The flows on these paths were achieved with a combination of area scheduling and phase shifter setting adjustment.  Incremental path flows on the TOT2C path were set by adjusting the Harry Allen phase shifters and area interchange.

The loading in the Red Butte / Cedar City area has a significant effect on the transfer capability on the TOT2C path.  For heavy N-S flows, the most restrictive case is when these loads are at their maximum.  This tends to result in higher flows on the lines south of Mona and Sigurd for a given TOT2C path flow.  The converse is true for heavy S-N flow conditions.  Lighter loads in Southwestern Utah result in higher flows on the Sigurd and Mona transmission lines.  Table 4.1 below shows the most recent projection for the loads in SW Utah.

| Location | Year |
| --- | --- |
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 |
| Cedar City | 103 | 120 | 124 | 129 | 135 | 140 | 146 | 151 | 157 | 164 | 170 | 177 | 184 | 191 |
| Red Butte | 415 | 441 | 459 | 477 | 496 | 516 | 537 | 558 | 581 | 604 | 629 | 654 | 680 | 708 |
| Table 4.1 - Southwestern Utah Peak Load Projection (in MW excluding generation) |

Although cases were developed and analyzed for the less restrictive cases for N-S and for S-N flows, the results are not presented here.  For N-S cases the peak 2015 projected loads were assumed (~750 MW) and for S-N cases the minimum 2015 off-peak loads were assumed (~250 MW).  Tables 4.2 and 4.3, on the following page, list the loads and generation resources used in the N-S cases analyzed.

| Location | Load in Case |
| --- | --- |
|  | N-S 0 | N-S 370 | N-S 600 | N-S 700 | N-S 1100 | N-S 1500 | N-S 2100 |
| Cedar City | 124 | 124 | 124 | 124 | 124 | 124 | 124 |
| St George | 630 | 630 | 630 | 630 | 630 | 630 | 630 |
| Table 4.2 - SW Utah Load in N-S Cases |

| Plant | Case Generation |
| --- | --- |
|  | N-S 0 | N-S 370 | N-S 600 | N-S 700 | N-S 1100 | N-S 1500 | N-S 2100 |
| Aeolus | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 |
| Bonanza | 495 | 495 | 495 | 495 | 495 | 495 | 495 |
| Bridger5-6 | 1560 | 1560 | 1560 | 1560 | 1560 | 1560 | 1560 |
| Carbon1-2 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |
| Current Ck1-3 | 490 | 490 | 490 | 490 | 490 | 490 | 490 |
| Dave Johnston1-6 | 2376 | 2376 | 2376 | 2376 | 2376 | 2376 | 2376 |
| Gadsby1-6 | 325 | 325 | 325 | 325 | 325 | 325 | 325 |
| Hinshaw | 120 | 120 | 120 | 120 | 120 | 120 | 120 |
| Hunter1-3 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 |
| Huntington1-2 | 940 | 940 | 940 | 940 | 940 | 940 | 940 |
| Lakeside1-3 | 535 | 535 | 535 | 535 | 535 | 535 | 535 |
| Naughton1-3 | 527 | 534 | 577 | 574 | 531 | 575 | 680 |
| Nebo1-2 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |
| Palisade1-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |
| Two Elk | 275 | 275 | 275 | 275 | 275 | 275 | 275 |
| UPP1-4 | 210 | 210 | 210 | 210 | 210 | 210 | 210 |
| Wyodak1 | 370 | 370 | 370 | 370 | 370 | 370 | 370 |
| Wind River1-3 | 550 | 550 | 550 | 550 | 550 | 550 | 550 |
| Windstar | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 |
| Table 4.5 - Significant Generation in N-S Cases |

Tables 4.4 and 4.5, below, list the loads and generation resources used in the S-N cases.

| Location | Load in Case |
| --- | --- |
|  | Base | S-N 357 | S-N 600 | S-N 700 | S-N 1100 | S-N 1500 | S-N 1700 |
| New SLC Load | 0 | 475 | 700 | 800 | 1150 | 1490 | 1600 |
| Cedar City | 123 | 55 | 55 | 55 | 55 | 55 | 55 |
| St George | 396 | 200 | 200 | 200 | 200 | 200 | 200 |
| Table 4.4 - Load Adjustments S-N Cases |

| Plant | Case Generation |
| --- | --- |
|  | Base | S-N 357 | S-N 600 | S-N 700 | S-N 1100 | S-N 1500 | S-N 1700 |
| Bonanza | 502 | 502 | 502 | 502 | 502 | 502 | 502 |
| Bridger5 | 562 | 562 | 562 | 562 | 562 | 562 | 562 |
| Carbon1-2 | 179 | 179 | 179 | 179 | 179 | 179 | 179 |
| Current Ck1-3 | 500 | 500 | 500 | 500 | 500 | 500 | 500 |
| Dave Johnston1-4 | 826 | 826 | 826 | 826 | 826 | 826 | 826 |
| Gadsby1-6 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |
| Hunter1-3 | 1415 | 1415 | 1415 | 1415 | 1415 | 1415 | 1415 |
| Huntington1-2 | 950 | 950 | 950 | 950 | 950 | 950 | 950 |
| Lakeside1-3 | 544 | 544 | 544 | 544 | 544 | 544 | 544 |
| Naughton1-3 | 711 | 386 | 388 | 387 | 388 | 388 | 388 |
| Nebo1-2 | 145 | 145 | 145 | 145 | 145 | 145 | 145 |
| Palisade1-4 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |
| UPP1-4 | 175 | 175 | 175 | 175 | 175 | 175 | 175 |
| Wyodak1 | 374 | 374 | 374 | 374 | 374 | 374 | 374 |
| West Valley1-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |
| Table 4.5 - Significant Generation in S-N Cases |

Most of the N-S study cases required significant addition of shunt capacitors at Three Peak and Red Butte.  The S-N study cases required significant addition of shunt capacitors in the Huntington Canyon area.  A large SVC device was modeled at the Red Butte 345 kV station and at the Three Peak 345 kV station.  The Three Peak device could likely be a DVAR switching capacitor banks rather than a full SVC.  The output of the devices were monitored during contingency evaluations to achieve an approximation of the size of device required for various flow conditions.

A series of single contingencies (N-1) and double contingencies (N-2) were evaluated for each of the study cases.  The list of contingencies studied included key 345 kV facilities and proposed 500 kV facilities in the Southern Utah area.  The standard WECC/NERC/PacifiCorp requirements for post-contingency voltage and facility loading were used to evaluate the results of the contingency analysis.

The steady-state and contingency requirements are as follows:

- Maximum allowable post-transient voltage deviation of five (5) percent for N-1 Contingencies (deviation from pre-disturbance voltage).

- Maximum allowable post-transient voltage deviation of ten (10) percent for N-2 contingencies (deviation from pre-disturbance voltage).

- Post-transient bus voltages must be at least 0.90 per unit.

- Pre and post-disturbance loading to remain within the emergency ratings of all equipment and line conductors.  The emergency ratings are determined by the owner/operator of each equipment item.

# Study Case Development and Results

## North to South (N-S) Transfer

With 2009 Southwestern Utah loads (583 MW), the TOT2C path could not accommodate any flow without contingency-related voltage violations.  For the Sigurd - Three Peak 345 kV transmission line outage, there are numerous low-voltage violations in the Three Peak area.  Table 5.1.1, shows the confirmed N-S path rating is zero (0) MW.

| TOT2C Path Rating | Description |
| --- | --- |
| 0 MW | Existing N-S Capability Confirmed (with 2009 loads) |
| Table 5.1.1 - Existing N-S Capacity with 2009 Loads |

When the loads in Southwestern Utah increase to 2015 levels (750 MW), the number of contingency-related voltage violations increase.  For the Three Peak - Red Butte 345 kV transmission line outage, there are numerous high-voltage violations at buses near Three Peak.  For the Sigurd - Three Peak 345 kV transmission line outage, there are numerous low-voltage violations in the Three Peak area.

The first set of transmission system reinforcements are required to return the TOT2C path rating to the accepted level of 300 MW with expected 2015 loads in Southwestern Utah.  These upgrades and the maximum available path C flow are listed in Table 5.1.2 below.

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 370 MW | Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR + 150 / - 50 MVAR Red Butte SVC + 150 / - 50 MVAR |
| Table 5.1.2 - Base Level Reinforcements to Support 2015 Loads |

With the upgrades listed in Table 5.1.2, the TOT2C path can be loaded to 370 MW.  This is the rating of the Harry Allen 230/345 kV transformer.  To increase the TOT2C path above 370 MW, a second Harry Allen transformer must be installed (see Table 5.1.3).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 600 MW | Harry Allen #2 230/345 kV transformer Increase Three Peak DVAR to +250 / -100 MVAR Increase Red Butte SVC to +250 / -100 MVAR |
| Table 5.1.3 - 600 MW N-S Reinforcement |

With the upgrade listed in Table 5.1.3, the TOT2C path can be loaded to 600 MW.  This is the combined rating of the two (2) Harry Allen phase shifters.  To increase the TOT2C path above 600 MW, additional phase shifter capability must be installed at Harry Allen (see Table 5.1.4).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 700 MW | Harry Allen 345 kV Phase Shifter #3 |
| Table 5.1.4 - 700 MW N-S Reinforcement |

Although it is technically feasible to add additional 345 kV phase shifter capability at Harry Allen, this additional capacity would be limited by the 345 kV line capacity north of Red Butte.  With the upgrade listed in Table 5.1.4, the TOT2C path could be loaded to 700 MW.  With flows above 700 MW on the TOT2C path, the outage of one of the parallel 345 kV transmission lines between Sigurd and Red Butte results in an overload on the remaining lines.  The next required reinforcement would be a 235-mile 345 kV line from Mona to Sigurd to Red Butte.

In place of the addition of the 345 kV phase shifting capacity and extensive 345 kV transmission reinforcements, the first phase of the Gateway Project would provide up to 900 MW N-S capacity (see Table 5.1.5).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 900 MW | Crystal 500 kV 750 MVA Phase Shifters (2) Red Butte - Crystal #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer |
| Table 5.1.5 - 900 MW N-S Reinforcements |

The construction of the next phase of the Gateway Project south of Mona provide the system reinforcement necessary to achieve a 2100 MW capacity N-S.  The 500 kV project would include two (2) Mona 500/345 kV transformers and a single Red Butte 500/345 kV transformer.  Phase shifters would be installed at Crystal (see Table 5.1.6).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 2100 MW | Sigurd - Red Butte #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Mona - Sigurd #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| Table 5.1.6 - 2100 MW N-S Reinforcements |

For N-S transfers, the 500 kV transmission line does not require an interconnection to the 345 kV transmission system at Sigurd.

## South to North (S-N) Transfer

With light loads in the Southwestern Utah area of approximately 250 MW, the TOT2C path demonstrated acceptable steady-state and contingency performance up to a flow of 357 MW.  This is the rating of the Harry Allen 230/345 kV transformer (see Table 5.2.1).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 351 MW | Existing S-N Path Capability (with light 2015 loads) (limited by rating of Harry Allen 230/345 kV transformer) |
| Table 5.2.1 - Existing S-N Path Capability |

To increase the TOT2C path above 351 MW, a second Harry Allen transformer must be installed.  Additional reinforcements that are required to increase the TOT2C path rating to 600 MW are listed in Table 5.2.2.  Series compensation is required on the Red Butte - Harry Allen 345 kV transmission line and on the Sigurd - Three Peak 345 kV line to increase flowability.  With S-N flows above 351 MW on the TOT2C path, the outage of one of the parallel 345 kV transmission lines between Sigurd and Red Butte results in bus low voltage violations on the 138 kV transmission system near Pinto.

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 600 MW | Harry Allen #2 230/345 kV transformer Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR +100 / - 50 MVAR Red Butte SVC +100 /- 100 MVAR |
| Table 5.2.2 - 600 MW S-N Reinforcements |

With the reinforcements listed in Table 5.2.2, the TOT2C path can be loaded to 600 MW.  This is the combined rating of the two (2) Harry Allen phase shifters.

To increase the TOT2C path above 600 MW, additional phase shifter capability must be installed at Harry Allen (see Table 5.2.3).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 700 MW | Additional 345 kV phase shifting capacity at Harry Allen Increase Three Peak DVAR to +250 / - 100 MVAR Increase Red Butte SVC to +250 /- 100 MVAR |
| Table 5.2.3 - 700 MW S-N Reinforcement |

With the upgrade listed in Table 5.2.3, the TOT2C path could be loaded to 700 MW.  With loads above 700 MW on the TOT2C path, the N-2 outage of the Spanish Fork - Huntington and the Camp Williams - Emery 345 kV transmission lines results in overloads on the Mona - Huntington 345 kV line.  In order to increase the TOT2C path capacity above the 700 MW level, a third Mona - Sigurd 345 kV transmission line must be constructed.  Also at these flow levels the Three Peak voltage violations occur again for 345 kV outages on either side of Three Peak.  This requires the construction of the Sigurd - Red Butte #2 345 kV transmission line.

In place of the addition of the 345 kV phase shifting capacity and extensive 345 kV transmission reinforcements listed above, the first phase of the Gateway Project would provide up to the 1300 MW S-N capacity (see Table 5.2.4).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 1300 MW | Crystal 500 kV Phase Shifters (2) Crystal - Red Butte #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Huntington #2 Unit Generator Tripping RAS Increase Three Peak DVAR to +250 / - 100 MVAR Increase Red Butte SVC to +250 /- 100 MVAR |
| Table 5.2.4 - 1300 MW S-N Reinforcements |

The only limitation for S-N flows above 700 MW is the overload of the Mona - Huntington 345 kV transmission line for the N-2 outage of the Camp Williams - Emery and the Spanish Fork - Huntington 345 kV transmission lines.  This can be reduced by tripping generation at Huntington.

The installation of a remedial action scheme to trip Huntington generation for the N-2 outage during periods of high S-N flows, will allow the TOT2C path to be loaded up to 1300 MW.

The construction of the next phase of the Gateway Project south of Mona provide the system reinforcement necessary to achieve a 1500 MW capacity S-N.  The 500 kV project would include two (2) Mona 500/345 kV transformers, a single Sigurd 500/345 kV transformer, and a single Red Butte 500/345 kV transformer.  Phase shifters would be installed at Crystal (see Table 5.2.6).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 1500 MW | Red Butte - Sigurd #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Sigurd -Mona #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| Table 5.2.6 - 1500 MW S-N Reinforcements |

For S-N transfers, the 500 kV transmission line requires an interconnection to the 345 kV transmission system at Sigurd to reduce contingency overloads on the Mona - Sigurd 345 kV transmission lines.

The installation of the remedial action scheme to trip Huntington generation for the N-2 outage during periods of high S-N flows, will allow the TOT2C path to be loaded up to 1700 MW (see Table 5.2.7).

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 1700 MW | Huntington #2 Unit Generator Tripping RAS |
| Table 5.2.7 - 1700 MW S-N Reinforcement |

# Results Summary

## North to South (N-S) Cases

Table 6.1 below summarizes the transmission system reinforcements required for the various N-S transfer levels.

| N-S Path Rating | Description of Reinforcements |
| --- | --- |
| 0 MW | Existing N-S Capability Confirmed (with 2009 loads) |
| 370 MW | Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR + 150 / - 50 MVAR Red Butte SVC + 150 / - 50 MVAR |
| 600 MW | Harry Allen #2 230/345 kV transformer Increase Three Peak DVAR to +250 / -100 MVAR Increase Red Butte SVC to +250 / -100 MVAR |
| 700 MW | Harry Allen 345 kV Phase Shifter #3 |
| 900 MW | Crystal 500 kV 750 MVA Phase Shifters (2) Red Butte - Crystal #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer |
| 2100 MW | Sigurd - Red Butte #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Mona - Sigurd #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| Table 6.1 - North to South (N-S) Reinforcements |

## South to North (S-N) Cases

Table 6.2 below summarizes the transmission system reinforcements required for the various S-N transfer levels.

| S-N Path Rating | Description of Reinforcements |
| --- | --- |
| 351 MW | Existing S-N Capability Confirmed |
| 600 MW | Harry Allen #2 230/345 kV transformer Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak DVAR +100 / - 50 MVAR Red Butte SVC +100 /- 100 MVAR |
| 1300 MW | Crystal 500 kV Phase Shifters (2) Crystal - Red Butte #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Huntington #2 Unit Generator Tripping RAS Increase Three Peak DVAR to +250 / - 100 MVAR Increase Red Butte SVC to +250 /- 100 MVAR |
| 1500 MW | Red Butte - Sigurd #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Sigurd -Mona #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| 1700 MW | Huntington #2 Unit Generator Tripping RAS |
| Table 6.2 - South to North (S-N) Reinforcements |

# Gateway Project Elements

Figure 7.1 shows the Gateway Project system south of Mona substation.  The individual elements of the Project are listed in Table 7.1, on the next page.

Figure 7.1 - Gateway Project South of Mona

| Reinforcement | Details |
| --- | --- |
| Harry Allen #2 230/345 kV Transformer | 230/345 kV, 357/465 MVA |
| Sigurd - Red Butte #2 345 kV Line | 156.6-mile, 2-954 ACSR, 1163/1432 MVA |
| Sigurd - Red Butte #2 Series Comp | 345 kV, 2000 Amp, 50% of Line Reactance |
| Red Butte - Harry Allen Series Comp | 345 kV, 2000 Amp, 75% of Line Reactance |
| Sigurd - Three Peak Series Comp | 345 kV, 2000 Amp, 50% of Line Reactance |
| Huntington - Pinto Series Comp | 345 kV, 2000 Amp, 60% of Line Reactance |
| Red Butte SVC | +150/-50 MVAR expandable to +300/-300 MVAR |
| Crystal Phase Shifters | 500 kV, 750/840 MVA, +25/-25 Degree |
| Red Butte - Crystal 500 kV | 95-mile, 3-1590 ACSR/TWD, 3681/4097 MVA |
| Red Butte 500/345 kV Transformer | 500/345 kV, 1500/1680 MVA |
| Huntington #2 Generator Tripping RAS | Trip Huntington #2 for N-2 with Heavy S-N flows |
| Sigurd - Red Butte 500 kV Line | 156.6-mile, 3-1590 ACSR/TWD, 3681/4097 MVA |
| Sigurd 500/345 kV Transformer | 500/345 kV, 1500/1680 MVA |
| Mona - Sigurd 500 kV Line | 78.4-mile, 3-1590 ACSR/TWD, 3681/4097 MVA |
| Mona 500/345 kV Transformer #1 | 500/345 kV, 1500/1680 MVA |
| Mona 500/345 kV Transformer #2 | 500/345 kV, 1500/1680 MVA |
| Table 7.1 - Reinforcement Details |

## North to South (N-S) Cases

Table 7.1.1 below lists the transmission system reinforcements south of Mona that are required for the various N-S transfer levels.

| Specific Reinforcement | Case |
| --- | --- |
|  | N-S 370 | N-S 600 | N-S 700 | N-S 900 | N-S 1500 | N-S 2100 |
| Harry Allen #2 230/345 kV Transformer |  | ■ | ■ | ■ | ■ | ■ |
| Sigurd - Red Butte #2 345 kV Line | ■ | ■ | ■ | ■ | ■ | ■ |
| Sigurd - Red Butte #2 Series Comp | ■ | ■ | ■ | ■ | ■ | ■ |
| Red Butte - Harry Allen Series Comp | ■ | ■ | ■ | ■ | ■ | ■ |
| Sigurd - Three Peak Series Comp | ■ | ■ | ■ | ■ | ■ | ■ |
| Huntington - Pinto Series Comp | ■ | ■ | ■ | ■ | ■ | ■ |
| Red Butte SVC | ■ | ■ | ■ | ■ | ■ | ■ |
| Harry Allen 345 kV Phase Shifter #3 |  |  | ■ |  |  |  |
| Crystal 500 kV Phase Shifters |  |  |  | ■ | ■ | ■ |
| Red Butte - Crystal 500 kV |  |  |  | ■ | ■ | ■ |
| Red Butte 500/345 kV Transformer |  |  |  | ■ | ■ | ■ |
| Huntington #2 Generator Tripping RAS |  |  |  |  |  |  |
| Sigurd - Red Butte 500 kV Line |  |  |  |  | ■ | ■ |
| Sigurd 500/345 kV Transformer |  |  |  |  |  |  |
| Mona - Sigurd 500 kV Line |  |  |  |  | ■ | ■ |
| Mona 500/345 kV Transformer #1 |  |  |  |  | ■ | ■ |
| Mona 500/345 kV Transformer #2 |  |  |  |  | ■ | ■ |
| Table 7.1.1 - List of Reinforcements in N-S Cases |

## South to North (S-N) Cases

Table 7.2.1 below lists the transmission system reinforcements south of Mona that are required for the various S-N transfer levels.

| Specific Reinforcement | Case |
| --- | --- |
|  | S-N 351 | S-N 600 | S-N 700 | S-N 1300 | S-N 1500 | S-N 1700 |
| Harry Allen #2 230/345 kV Transformer |  | ■ | ■ | ■ | ■ | ■ |
| Harry Allen - Red Butte Series Comp |  | ■ | ■ | ■ | ■ | ■ |
| Sigurd - Three Peak Series Comp |  | ■ | ■ | ■ | ■ | ■ |
| Huntington - Pinto Series Comp |  | ■ | ■ | ■ | ■ | ■ |
| Red Butte SVC |  | ■ | ■ | ■ | ■ | ■ |
| Crystal 500 kV Phase Shifters |  |  | ■ | ■ | ■ | ■ |
| Red Butte - Crystal 500 kV |  |  | ■ | ■ | ■ | ■ |
| Red Butte 500/345 kV Transformer |  |  | ■ | ■ | ■ | ■ |
| Sigurd - Red Butte #2 345 kV Line |  |  | ■ | ■ | ■ | ■ |
| Sigurd - Red Butte #2 Series Comp |  |  | ■ | ■ | ■ | ■ |
| Huntington #2 Generator Tripping RAS |  |  | ■ | ■ |  | ■ |
| Sigurd - Red Butte 500 kV Line |  |  |  |  | ■ | ■ |
| Sigurd 500/345 kV Transformer |  |  |  |  | ■ | ■ |
| Mona - Sigurd 500 kV Line |  |  |  |  | ■ | ■ |
| Mona 500/345 kV Transformer #1 |  |  |  |  | ■ | ■ |
| Mona 500/345 kV Transformer #2 |  |  |  |  | ■ | ■ |
| Table 7.2.1 - List of Reinforcements in S-N Cases |

# Conclusions

Based on this evaluation, the current accepted path ratings for TOT2B and TOT2C were validated for south to north transfers.  However with 2009 peak projected loads, the north to south TOT2C path rating is approximately zero (0) MW.  No additional transfers could be accommodated without transmission system reinforcements.

The reinforcements necessary to obtain increased 700 and 1500 MW bi-directional TOT2C path ratings are listed in Table 8.1, below.

| TOT2C Path Rating | Description of Reinforcements |
| --- | --- |
| 700 MW | Harry Allen #2 230/345 kV transformer Sigurd - Red Butte #2 345 kV Transmission Line w/ series comp Red Butte - Harry Allen #1 345 kV Series Comp Sigurd - Three Peak #1 345 kV Series Comp Huntington - Pinto # 345 kV Series Comp Three Peak SVC Red Butte SVC Crystal 500 kV 750 MVA Phase Shifters (2) Red Butte - Crystal #1 500 kV Transmission Line w/Series Comp Red Butte #1 500/345 kV Transformer |
| 1500 MW | Huntington #2 Unit Generator Tripping RAS Sigurd - Red Butte #1 500 kV Transmission Line Sigurd #1 500/345 kV Transformer Mona - Sigurd #1 500 kV Transmission Line Mona 500/345 kV Transformers (2) |
| Table 8.1 - Southern Utah Transmission Reinforcements |

The reinforcements listed in Table 8.1 will result in the maximum rating listed.  Any increase in flows above this level will trigger the reinforcements for the next rating level.

A phased approach to construction of the required transmission system reinforcements will not result in any unnecessary facilities up through the 700 MW TOT2C transfer capability level.  For flows above 700 MW, a series of 345 kV transmission reinforcements can extend the capacity to 1100 MW for N-S and 1500 MW for S-N.  However, these reinforcements are ALL unnecessary once the 500 kV system reinforcements are implemented to increase the capacity to 1500 MW.

# Appendix

WECC Path Descriptions

Powerflow Diagrams

Contingency Summaries