## Slide 1: Wyoming WEST Area Study December 2013
Seongtae Kim/Jeremy Viula

## Slide 2: Geographical Location – Wyoming West
Pinedale
Paradise
La Barge
Kemmerer
Naughton power plant
Evanston

## Slide 3: General Information – Wyoming West
Area: Total 9,000 square miles (Lincoln, Sublette, & Uinta counties in Wyoming)
Substation
  22 PacifiCorp-owned
  16 customer-owned
Transmission Voltage
  69 kV
  138 kV
  230 kV

## Slide 4: General Information – Wyoming West
Generator
  740 MW coal-fired steam plant at Naughton substation
  265 MW wind generation in the Evanston area
Load
  10 % of residential & commercial
  90 % of industrial
  Double peaks (Summer & Winter)
  77 % overall load factor

## Slide 5: Projected Load – Wyoming West
Base System Loads
  2012 Summer: 292 MW
  2011-12 Winter: 314 MW
Growth
  Summer: 3.6 %
  Winter: 3.3 %
Projected System Loads
  2017 Summer: 415 MW
  2016-17 Winter: 436 MW

## Slide 6: Reliability Issues – Wyoming West
Issues: Overdutied circuit switcher 133A & 131I at Evanston 138 kV substation during 3-phase fault
  133A & 131I rating: 7 kA
  3-phase fault: 7.31 kA
Recommended solution: Replace both circuit switchers with a higher rating
Estimated cost: $300,000

## Slide 7: N-0 System Improvements – Wyoming West
Issue: Low voltage
  Pinedale 69 kV bus
  Paradise 69 kV bus
  Paradise Tap 69 kV
First predicted (Assuming full contract utilization): 2013-14 heavy winter
Cause: Impedance of the 69 kV line between Chimney Butte & Paradise Tap (almost 10 % of voltage drop)

## Slide 8: N-0 System Improvements – Wyoming West
Recommended solution: Install 3 MVar switched capacitor at Paradise 25 kV
Advantage of switched capacitor on feeder side over sub-transmission side: less cost & less space
Estimated cost: $195,000

## Slide 9: N-1 System Improvements* – Wyoming West
Craven Creek – Monument 230 kV outage
Issue: Low voltage
  Pinedale 69 kV bus
  Paradise 69 kV bus
First predicted (Assuming full contract utilization): 2013-14 heavy winter

## Slide 10: N-1 System Improvements* – Wyoming West
Craven Creek – Naughton 230 kV outage
Issue: Low voltage
  Pinedale 69 kV bus
  Paradise 69 kV bus
  Paradise Tap 69 kV
First predicted (Assuming full contract utilization): 2013 heavy summer

## Slide 11: N-1 System Improvements* – Wyoming West
Chimney Butte 230/69 kV 75MVA transformer outage
- replaced by 230/69 kV 50MVA back-up transformer
Issue: Low voltage
  Paradise 25 kV bus
  Pinedale 69 kV bus
  Paradise 69 kV bus
  Paradise Tap 69 kV
First predicted (Assuming full contract utilization): 2013 heavy summer
Voltage collapsed below 0.8 pu during 2016-17 heavy winter

## Slide 12: N-1 System Improvements* – Wyoming West
Paradise 69/25 kV transformer outage
Issue: High Voltage
  Pinedale 25 kV bus
First predicted (Assuming full contract utilization): 2013 heavy summer
Cause: Instantaneous voltage rise

## Slide 13: N-1 System Improvements* – Wyoming West
Recommended short-term solution for both high & low voltage issues: Install 2-step (2.5 MVar/step) 5Mvar capacitor bank at
  Pinedale 69 kV bus
  Paradise 69 kV bus
Estimated cost: $2,367,000

## Slide 14: N-1 System Improvements* – Wyoming West
Construction Details
Paradise 69 kV substation
Pinedale 69 kV substation

## Slide 15: Construction Schedule – Wyoming West
Total Estimated Cost: $2,862,000

## Slide 16: Construction Schedule (cont’d) – Wyoming West
Total Estimated Cost: $2,862,000

## Slide 17: Long-term Solution – Wyoming West
Construction of 230kV line between Chimney Butte & Paradise
Resolved issues
  Voltage issues (High & Low) at Upper Green River area
  Load serving issue at Paradise
    Up to 24.5MVA (Current 69kV line)
    27MVA (Contracted load in 2017)
    24.1MVA (Anticipated load in 2017)
The project is budgeted & the anticipated in-service date is the end of 2017

## Slide 18
Any Questions or Comments?
Wyoming West Area Study